## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | GT4-ITP-012 - Concrete Structural Footings | itp |  |  |  | Yes | GT4-ITP-012 - Concrete Structural Footings
section | 1 - Preliminary Works
checkpoint | 1.1 - Check that current revision drawings are being used
label | Frequency: Prior to Commencing Work
label | Acceptance Criteria: Issued For Construction (IFC) and latest available revision used
label | Reference Documents: IFC Project Drawings/ Drawing Register
label | Inspection / Test Method: Document review
label | Record of conformity: Latest revision IFC drawings, ITP signed
label | HP*
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency: Prior to commencing any activity
label | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
label | Reference Documents: OHSMP, EMP, TMS, SWMS, WP
label | Inspection / Test Method: Visual Inspection
label | Record of conformity: This ITP Signed
label | HP*
label | Responsibility: Site Engineer
date | Date Completed:
section | 2 - Material Conformance
checkpoint | 2.1 - Materials & source Approval - Reinforcing
label | Frequency: Prior to works commencing 1 per delivery
label | Acceptance Criteria: Reinforcing supply quantities in accordance with the drawings and AS/NZS 4671.
label | Reference Documents: Work Procedure
label | Inspection / Test Method: Visual Inspection
label | Record of conformity: Receival inspection checklist
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 2.2 - Materials & source Approval - Cast-in Items
label | Frequency: Prior to works commencing 1 per delivery
label | Acceptance Criteria: Cast-In items to be in accordance with the drawings and manufacturer specifications. All surface exposed, cast-in components are to be hot dip galvanised and fire protected as required.
label | Reference Documents: EW-ST-DRW-10- 0005
label | Inspection / Test Method: Visual Inspection
label | Record of conformity: Receival inspection checklist
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 2.3 - Source In-situ Concrete Material
label | Frequency: Each Lot
label | Acceptance Criteria: Concrete shall be at minimum 28-day strength, F’c of 32 MPa and when placed shall be well rammed to ensure thorough consolidation. Concrete slump shall be 100mm +/- 20mm
label | Reference Documents: EW-ST-DRW-10- 0005 Table 5.1 of AS1379
label | Inspection / Test Method: Verify
label | Record of conformity: Mix Design
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
section | 3 - Construction \ Erection of Formwork
checkpoint | 3.1 - Set Out
label | Frequency: Each Lot
label | Acceptance Criteria: Provide 24 hr inspection notice for Superintendent confirmation of footings location.
label | Reference Documents: EW-ST-DRW-10- 0005
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP signed
label | HP
label | Responsibility: Site Engineer
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Excavation
label | Frequency: Each Lot
label | Acceptance Criteria: Excavation to be to the depth and size required for the concrete footing.
label | Reference Documents: EW-ST-DRW-10- 0020
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 3.3 - Blinding Concrete
label | Frequency: Each Lot
label | Acceptance Criteria: Min. 200mm of concrete blinding layer below the base of the pad footing.
label | ○ Where a footing does not extend to the level required within the acceptable founding material, the contractor is to provide a weak-mix blinding concrete (minimum N15) for the footprint of the footing to achieve the required depth
label | Reference Documents: EW-ST-DRW-10- 0020, EW-ST-DRW-10- 0005
label | Inspection / Test Method: Inspection
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 3.4 - Formwork
label | Frequency: Each Lot
label | Acceptance Criteria: Formwork shall conform to shapes, lines, levels and dimensions of the concrete shown or indicated on the Drawings.
label | Reference Documents: Work Procedure
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
section | 4 - Reinforcement
checkpoint | 4.1 - Steel Fixing
label | Frequency: Each Lot
label | Acceptance Criteria: Reinforcement type and design to be in accordance with DWG EW-ST-DRW-10-0020.
label | ○ Reinforcing steel shall be bent and placed in accordance with AS 4671 and sufficient bar chairs shall be installed to ensure reinforcement is in the correct position.
label | Reference Documents: EW-ST-DRW-10- 0020 Work Procedure
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 4.2 - Reinforcement Installation
label | Frequency: Each Lot
label | Acceptance Criteria: Pre-pour Checklist Completed:
label | – Position and spacing check and recorded
label | – Cover checked and recorded
label | – Reinforcing supports checked and recorded
label | – Laps at required length
label | Reference Documents: Work Procedure
label | Inspection / Test Method: Inspection
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 4.3 - Cast-In Items
label | Frequency: Each Lot
label | Acceptance Criteria: Installation of cast in items as per manufacturer specifications
label | Reference Documents: Work Procedure
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
section | 5 - Inspections
checkpoint | 5.1 - Pre-pour Inspection
label | Frequency: Each Lot
label | Acceptance Criteria: Concrete shall not be placed until:
label | (i) the evidence that the forms, reinforcement, any stressing materials and embedments conforming to the requirements of the specification and the drawings, has been reviewed by the Superintendent
label | (ii) all foreign material has been completely removed from the forms
label | – Superintendent requires 48 HR notice for inspection.
label | Reference Documents: Work Procedure
label | Inspection / Test Method: Inspection
label | Record of conformity: Pre Pour Inspection Checklist Completed
label | HP
label | Responsibility: Site Engineer/Superintendant
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 6 - Placing and Finishing Concrete
checkpoint | 6.1 - Pour Concrete Footings
label | Frequency: Each Lot
label | Acceptance Criteria: Footings shall be constructed in accordance with the detail shown on the drawings.
label | Reference Documents: EW-ST-DRW-10- 0020
label | Inspection / Test Method: Inspection
label | Record of conformity: Concrete pour record and delivery docket
label | HP*
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 6.2 - Finishing
label | Frequency: Each Lot
label | Acceptance Criteria: Concrete to be vibrated to ensure compaction and air voids removed. Screed finish required on exposed surfaces. Concrete surface finishes to meet Class 4 requirements as per table 3.2.3 and 3.3.5.1 of AS 3610. (Attached Below)
label | Reference Documents: Work Procedure
label | Inspection / Test Method: Verify
label | Record of conformity: Completion of prepour inspection checklist
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 6.3 - Concrete Testing
label | Frequency: Each Lot
label | Acceptance Criteria: Testing for conventionally reinforced elements: UNO in specifications or on drawings, the contractor is to arrange for project sampling for every 50m³ of concrete supplied (1000m³ in the case of shrinkage tests alone).
label | ○ Provide slump, 7- and 28-day compressive strength and shrinkage test results in accordance with AS 1379 and AS 1012.1 to the engineer, as a minimum.
label | ○ Concrete Testing to be carried out as per specifications in AS 1379
label | Reference Documents: Work Procedure
label | Inspection / Test Method: Verify
label | Record of conformity: Test Results
label | TP
label | Responsibility: Site Engineer
date | Date Completed:
section | 7 - Post Pour Details and Inspections
checkpoint | 7.1 - Concrete Curing
label | Frequency: Each Lot
label | Acceptance Criteria: Concrete to be cured as per project specifications.
label | ○ All concrete elements are to be actively cured for a minimum of 14 days following pouring by ponding or an approved proprietary system. The contractor shall submit the proposed curing methodology to the engineer for approval prior to pouring.
label | Reference Documents: EW-ST-DRW-10- 0005
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP Signed
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 7.2 - Removal of Formwork
label | Frequency: Each Lot
label | Acceptance Criteria: Stripping of vertical faces in accordance with C.1.8.13 of EW-ST-SPC-000001.
label | Reference Documents: EW-ST-SPC- 000001
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP Signed
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 7.3 - Allowable Tolerances Level & Alignment
label | Frequency: Each Lot
label | Acceptance Criteria: Surface Tolerances to be in accordance with Table 3.3.5.1 of AS 3610 As-built survey completed for lot
label | Reference Documents: AS 3610
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP Signed
label | SCP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 7.4 - Post-pour Checklist
label | Frequency: Each Lot
label | Acceptance Criteria: Completion of Pre Pour checklist quality checks.
label | Reference Documents: Work Procedure
label | Inspection / Test Method: Inspection
label | Record of conformity: Pre Pour Inspection Checklist Completed
label | HP*
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | 7.5 - Backfilling
label | Frequency: Each Lot
label | Acceptance Criteria: Backfilling to match pavement design and to occur min. 72 hours post concrete pour.
label | Reference Documents: Work Procedure
label | Inspection / Test Method: Inspection
label | Record of conformity: This ITP Signed
label | HP*
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | Print Name:
text | Position:
date | Date:
signoff | Sign ITP