## General
Modify template as required prior to use, e.g. to accommodate project or customer specific requirements, then delete this instructional text when complete.
SECTION 1 – GENERAL DETAILS
Project Name: | DCC9459 - Reid Avenue, Mosgiel - Stormwater Upgrade | [5 empty] | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561461 | [5 empty] | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council | [5 empty] | B | Report by Breach | ER | Engineers Representative | Will Heffernan Meng Hong Loh
Contract Number: | DCC9459 | [5 empty] | C | Check | CR | Cust. Representative | Todd Williams
Area/ Sub-System: | Reid Avenue, Mosgiel - Stormwater Upgrade |  |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel | Aaron Sutherland
[7 empty] | E | Examine | MC | Material Controller
ITP Number: | ITP-002 |  |  | Version: | V1 |  | H | Hold Point | OP | Operations Manager
ITP Description: | Installation of SW Manhole | [5 empty] | I | Inspection | PM | Project Manager | Philip Rowley
Discipline: | Utilities | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor | Matt Paterson
Specification: | Three Waters Infrastructure Renewals & Upgrade. Specification - Reid Avenue, Mosgiel | [5 empty] | O | Operation | QE | Quality Engineer | Matt Paterson
[7 empty] | R | Review | QM | QA Manager
Drawings: | WSP 6-CD109.96 Drawings C101, C102, C110 through C114, C120, C121, C200 through C204 & C210 | [5 empty] | S | Subcontractor | SP | Supervisor | Aaron Sutherland
[7 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Matt Paterson |  |  | Date: | 2025-06-18 |  | W | Witness Point | SV | Surveyor
Quality Specified: | [8 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: | Aaron Sutherland |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: | Matt Paterson / Phil Rowley |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: | Will Heffernan / Meng Hong Loh |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Manhole Delivery | Inspect for damage and wear, Confirm Manhole is correct type & dimensions correct as per drawings and Specifications | - Items are approved as per contract specification - DCC approved | Photos, delivery docket | On Delivery | Visual | C | SP QE
3.2 | Set out & Locations | Set out completed by an approved surveyor marked allignment | - Allignment set out matches drawing C111(rev1) or aggreed with the Engineer | Survey marks, photos | Prior to commencement of works | Survey | H | SV SP QE ER
3.3 | Backfill / Bedding Material | Approved Material, AP20 on site | As per Details on WSP drawing C121(rev1) | Delivery dockets, photos | On Delivery | Visual | C | SP QE
3.4 | Delivery of Corbel Reinforcing Bars | Insect for the correct quantity supplied, Correct Material & Dimensions | As detailed on Drawing C201 (Section 4 & Detail A) | Delivery dockets, photos | On Delivery | Visual | C | SP QE
3.5 | Delivery of HILTI RE-500 Chemical Anchor | Inspect Packaging and condition of product & application gun. Check if application gun is compatable with product | No damage and gun is correct for product | Nil | On Delivery | Visual | C | SP QE
3.6 | Manhole Lid & Sealant | Inspect for damage and wear, Confirm Manhole Lid & Sealant is correct type & dimensions/quantities correct as per drawings and Specifications | - Items are approved as per contract specification - DCC approved | Delivery docket | On Delivery | Visual | C | SP QE
3.7 | Manhole Adjstment rings | Inspect for damage and wear, Confirm Manhole is correct type & dimensions correct as per drawings and Specifications | - Items are approved as per contract specification - DCC approved | Delivery docket | On Delivery | Visual | C | SP QE
3.8 | Manhole Korum | Inspect for damage and wear, Confirm Manhole is correct type & dimensions correct as per drawings and Specifications | - Items are approved as per contract specification - DCC approved | Delivery docket | On Delivery | Visual | C | SP QE

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | Trench Excavation | - Excavate to required depth to invert as per C121(rev1) - Trench width 1300mm to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe - Floor of trench to be even across width and length | Depth is correct using measurements from RL's provided by surveyer | Photos, measurement checks | During Installation | Visual | V | SP QE
4.2 | Foundation | Scala test on base of trench | 100kPa Allowable Bearing Stress. 600mm maximum Foundation required. Ballast to be added if required subject to | Test results & Engineer approval if below 100kPa | At each Manhole Location | Visual, On site test | H | SP QE ER
4.3 | Bedding - Primary | Bedding minimum 200mm compacted AP40 | - Bedding to comply with WSP requirements | Photo | During installation | Visual, Measurement Check | C | SP QE
4.4 | Bedding - Secondary | Bedding minimum 75mm compacted AP150 | - Bedding to comply with WSP requirements | Photo | During installation | Visual, Measurement Check | C | SP QE
4.5 | MH Installation | MHs to be installed true to the design level includung riser, sealing strip/lid and neck rings and Manhole Korum Ductile Iron cover. | -Final levels are in accordance with the C4300 or within tolerance and agreed with the Engineer | Photos, As-built | During installation | Survey | H | SP QE ER
4.6 | Cutting of Manhole wall for pipe installation | Marking out of the Pipe entry & Exit positions | Pipe invert levels are correct as per long section drawings | Photos & Measurement checks | 2 per manhole (Inlet & Outlet) | Measurement check, Photos | C | SP QE
4.7 | Installation of HD12 L Bar (hook) | Marking out of Bar locations as per drawing as agreed with the Engineer | Bars installed as per drawings ensuring a minimum of 50mm cover to all reinforcing | Photos & Measurement checks | As each Manhole Penetration | Measurement check, Photos | C | SP QE
4.8 | Pipe starter install | Determine the correct required starter length. Confirm diameter is correct | Starter pipe is in correct position and is of suitable length so not to obstruct Corbel. Consider the length of the next pipe section (short) | Drawings & Measurement checks | 2 per manhole (Inlet & Outlet) | Measurement check, Photos | C | SP QE
4.9 | Epoxy Mortar Install | Epoxy Mortar is installed in accordance with Product Specifications & drawing C201 (Detail A) | Epoxy Mortar is cured and provides a waterproof seal and is visually free of imperfections | Product Data Sheet, Drawings | 2 per manhole (Inlet & Outlet) | Visual | C | SP QE
4.10 | Corbel Boxing | Construction of Boxing in preparation for casting | Boxing is constructed to the correct | Drawings & Measurement checks | 2 per manhole (Inlet & Outlet) | Measurement check, Photos | C | SP QE
4.11 | Corbel Casting | Determine concrete quantity and confirm delivery. Vibrate as required to remove entrained air | All entrained air removed | Supplier document certifying 30MPa | 2 per manhole (Inlet & Outlet) | Visual, Supplier Documentation | C | SP QE
4.12 | Benching | Benching concrete shall have a crushing strength of 10MPa at 28 days. Benching shape to have smooth transitions at bends and junctions | - Benching built up & shaped to the drawings & specifications | Photos | During benching contruction | Visual, Test Results | H | SP QE ER
4.13 | Backfill and Compact | - Backfill in 200mm layers of compacted AP65 - Compaction testing one test every two layers as required | - 95% MDD in roads, paths, and pavements | Photos, Compaction test results | During Installation | Visual, On Site test | H | SP QE ER
4.13 | Materials compaction | Each Layer (200mm) compaction using plate compactor/foot wacker 8No back and forward passes | Compacted layer is 200mm | Photos, visual, measurement | 16No passes (8no x 2) | Visual, Photograph | V | SP QE ER

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | Red pen markups | Complete mark up of any changes from project drawings | Installation complete | Original Drawings & Documentation | After installation of SWMH | Document | H | SP QE ER
5.2 | As-Built Survey | At project completion | Engineer approval | As-Built Drawings | Completion of Project | Submission of Documentation | R | ER
5.3
5.4
5.5
5.6
5.7
5.8
5.9
5.10
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: