## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
fd828da4-39dc-4ce3-85b3-ec3ef7efb398 | checklist | 561450-DOW-ITP-X001 Gravity Sewer | itp | 561450-DOW-ITP-X001 Gravity Sewer
1717eede-d860-4842-8c27-cf82e71aeee9 | section | SECTION 3 – RECEIVING INSPECTIONS
60387823-7ccb-45e8-8e5a-1931124dff29 | checkpoint | 3.1 - Material Delivery
13fa249c-4853-5892-a230-f2c42238b52e | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct size as per drawings and Specifications
68ef3256-67b4-56bd-983f-558a53bc8215 | note | Acceptance Criteria - Pipes shall be DN150 SN16 PVC-U rubber ring jointed
11b64ad0-7134-59e2-9c30-8e7c51e35810 | note | ○ Items are approved as per contract specification
aa31dae9-4ab4-520b-9c4f-0338e823c94a | note | ○ DCC approved
198f7523-10ae-5ca1-b737-91881887d232 | note | Verifying Document - Photos, delivery docket,
79bda257-7304-5157-a940-d49d2a6aa5f7 | note | Frequency - On Delivery
e615f043-6212-5f10-afb5-ff7c73447802 | note | Inspection Type (Visual, other) - Visual
825a2f03-516c-5baf-931b-79d1a026be29 | note | Inspection: Key - C
dc8d3efb-086b-5a26-b8b9-d37f4cac396c | note | Inspection: By - SP/QE
2da840bc-2ae8-4ef7-abf6-9efe20bd1c22 | checkpoint | 3.2 - Set out
8b9d43a6-4c33-5a0b-ac48-14ecfa53bc31 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
07b62d6d-1f3d-5599-bb3a-f0c46dab3870 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
7c1732eb-ebff-58b8-b602-c0f3e284e884 | note | Verifying Document - Survey marks, photos
f3ff83ff-5660-51f0-a2a8-eaf3b376a904 | note | Frequency - Prior to commencement of works
f7139f2e-8ede-5c12-a5b5-fdd9be8584bc | note | Inspection Type (Visual, other) - Survey
2a592127-5c71-5741-b8c0-973ab9add74b | note | Inspection: Key - H
40ce5f24-6c6c-540b-bd6f-57644e7c8366 | note | Inspection: By - SV/QE/PE/CR
9b16bf31-f684-4602-a872-07fc196f80bf | signoff | AUTHORITY HOLDPOINT
e14cd4f1-d699-4a97-b192-46ffa023a44d | section | SECTION 4 – IN-PROCESS INSPECTIONS
197d9920-990a-4aa1-b25a-98a5b63feb59 | checkpoint | 4.1 - Trench Excavation
f723b7ab-5f35-5da5-badd-e7f0f9990ee3 | note | Inspection Point: Quality Control Activity - excavate to achieve required depth to invert as per drawings
25d3bcc9-b965-5266-9365-9c8e74eaf0a6 | note | ○ Floor of trench to be even across width and length
f0547dc8-4045-5aca-8be4-c15232fcfcfb | note | Acceptance Criteria - Allow 100mm for bedding
8bb462d9-af52-5e39-be6b-76fba084100f | note | Verifying Document - Photos, measurement checks
de0cc256-3270-555c-8661-cda300c6b51c | note | Frequency - During Installation
35b5bfcd-105a-5c6d-ae6c-831974a6f2e4 | note | Inspection Type (Visual, other) - Visual
b12a7656-0311-5403-b45e-c2510b1c571f | note | Inspection: Key - C
314bb7e2-b596-5988-b7d8-e3eff66bf722 | note | Inspection: By - SP/QE/CM
83677bae-cf1c-48ff-a515-c50ba6af3635 | checkpoint | 4.2 - Foundation
d83822d9-0466-548c-80b3-84929b6b6872 | note | Inspection Point: Quality Control Activity - Trench Floor Foundation to be checked it is suitable to support loads
03357e67-cae2-5c6a-8101-527398e728c2 | note | Acceptance Criteria - Foundation should avoid very soft clay, saturated soil, or fragmented rock
0aa22ac3-e2ca-57f8-ae59-6b06e04fdb2a | note | Verifying Document - Photos
67d8755e-084e-50e3-b480-fc76077df1ce | note | Frequency - During Installation
a3224b55-f03a-5f4b-b125-d967bded5048 | note | Inspection Type (Visual, other) - Visual
72331b1c-ceaf-564b-993e-99456790f137 | note | Inspection: Key - H
7691bca3-eadb-5b1c-9353-75d44722e9fd | note | Inspection: By - SP/QE
4ee1a8cc-2629-4761-af98-d7eac12f6b46 | signoff | AUTHORITY HOLDPOINT
8fe7c4d8-a2c6-49c6-b80c-cdfaa470d9b3 | checkpoint | 4.3 - Install Pipe
ebb99398-aa0e-5928-9fe3-00a13d64480f | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per design drawings
41f72e9a-c9df-5828-b567-9c20355f53fc | note | Acceptance Criteria - Pipe not damaged during installation
ad212a17-baad-53c5-9bf3-ed94e582d223 | note | ○ Pipe installed to grade within tolerances
b5f3f83f-7184-5d95-ac56-129c97e67828 | note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
4297c85e-66fe-50ce-8bed-9241ea8a0e78 | note | Frequency - During installation
2f1c564a-b3a2-5947-bd19-d336dcdb24ec | note | Inspection Type (Visual, other) - Visual, Survey
cb9ec0b6-1a12-5067-9e0b-604dcde45571 | note | Inspection: Key - C
09f3e668-e339-580e-8a0e-cfa9da2752d5 | note | Inspection: By - SP/QE
5ee1ff65-9a62-4be1-a948-856861e50e0a | checkpoint | 4.4 - Laterals connections and installation
4776f539-ea3d-5e73-86f9-a4a3e56912bd | note | Inspection Point: Quality Control Activity - Lateral connection as per drawing
dfd94f2c-f0a4-5924-ae92-4ce25a90f3ba | note | Acceptance Criteria - Lateral connection as per drawing and DCC standard details
68e48312-d91c-54c0-87bc-39fd72da1685 | note | Verifying Document - Photos
7b660b0a-8c2e-53f9-8ba5-b8d3a378f6a6 | note | Frequency - Every Lateral
442e0dc2-910b-5aa0-8fdf-abe8c73287df | note | Inspection Type (Visual, other) - Visual, Survey
7c226bc5-091f-5e93-848f-3b06ba49b666 | note | Inspection: Key - C
fcd443f4-39b0-56ac-a467-6218c2b3af83 | note | Inspection: By - SP/QE
da075d86-1830-48df-8c0a-c4b545b73df6 | checkpoint | 4.5 - Embedment zone
91c54804-0fb9-5294-8dde-2a53928e4b3b | note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
35a9dee9-5a72-5065-9a0e-9dbbe5c2d439 | note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
360f94da-f75c-5603-bfb6-ad74f1042fe5 | note | Acceptance Criteria - min 100mm bedding
08e2952c-55f9-50da-93a6-398047ad4398 | note | ○ 100mm overlay
2ee46c6f-71be-54f1-a1e0-dccc52bb9253 | note | Verifying Document - Photos
57e78fc0-0ad6-5459-b037-36134667ed06 | note | Frequency - During Installation
9535d3ce-de85-5a24-9ee3-31ba84286fc0 | note | Inspection Type (Visual, other) - Visual
82969f38-22c2-5af4-ac41-f3415d12111d | note | Inspection: Key - C
708f48d0-d753-57bb-a2e1-cfed0ea8478d | note | Inspection: By - SP/QE
2fa848ad-110e-481a-944a-0cbf0e6af20a | checkpoint | 4.6 - Backfill and Compact
fe94dbc3-b40b-598f-81fd-8130b8da5143 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
6007de14-a277-5642-848f-d0861f54981d | note | ○ Compaction testing one test every two layers as required
0c7492df-6b33-5e5d-87b6-1f74d435ea0e | note | ○ Conductive signal strip to be laid at 300mm above pipe
f9ced9ea-5f4c-536b-b803-74d1e4450117 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
cc238824-3111-5de9-a38d-e1a7c9718d04 | note | Verifying Document - Photos, Compaction test results
834dea89-8728-532e-8de5-035ca4be29c4 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
022edbf2-3160-50db-b682-eac53360659f | note | Inspection Type (Visual, other) - Visual, On Site test
50a15cf0-72ed-59f2-831f-b92a73432c75 | note | Inspection: Key - H
9715ef8f-edc4-55da-a6aa-0ec4022832ae | note | Inspection: By - SP/QE/CM
20779dfc-7c43-42a3-99b5-c0efe8d5f12a | signoff | AUTHORITY HOLDPOINT
2a228ad4-430a-4539-a3f1-916b6d51b7b2 | checkpoint | 4.7 - Basecourse
560cde67-86af-5f38-a48f-675cefe0c02e | note | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
fea2d63c-a1c2-5f3c-93f2-4c4eac4a05f2 | note | Acceptance Criteria - 98% MDD in roads
c02a17d0-e1a0-58fc-952d-307e5ae83663 | note | Verifying Document - Photos, Compaction test results
795ceaba-4276-5f70-b69f-27f60b105966 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
f50c245a-6f2c-5b1c-84fe-02581c0c538a | note | Inspection Type (Visual, other) - Visual, On Site test
63dbc9cd-59b1-5f03-bda4-8ac1ead00e10 | note | Inspection: Key - H
9d9db31c-36bc-5a87-aaf9-a2bf82b11a9d | note | Inspection: By - SP/QE/CM
15680522-c441-4799-8b03-a8c873ef3c6a | signoff | AUTHORITY HOLDPOINT
da8d2c16-6f4a-4253-bd2e-8c2b7ab4c711 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
4db824c2-ca70-49bb-bd87-45663954693d | checkpoint | 5.1 - Leak Testing
61771cd4-54bd-5a24-bac9-649c4aa144de | note | Inspection Point: Quality Control Activity - Completed pipelines including laterals to be tested in the presence of the Engineer or their Representative in accordance with AS/NZS 2566.2 Section 6.4
837517f5-2fb1-532f-af05-dfc3ca849586 | note | Acceptance Criteria - Engineer Approval
e7bec4af-05e0-55d7-a18b-5bc168276d80 | note | Verifying Document - Test Records
1951db37-95ed-5976-81de-fbd93e5fc012 | note | Frequency - Every section of pipe completed
6b49c0bd-7166-5cde-a4f3-1ec738f09cec | note | Inspection Type (Visual, other) - On-Site Test
aeabb0da-a360-5acd-941e-0580a3b7b322 | note | Inspection: Key - H
7fde76d0-ea46-50c2-a3bb-f799bfa77527 | note | Inspection: By - SP/QE/CM/CR
e2459a1b-78a5-4d3a-a3dc-ee3018a98a21 | signoff | AUTHORITY HOLDPOINT
d08d2aeb-b711-4866-93e2-8de822f8e9e5 | checkpoint | 5.2 - CCTV
c51384c5-20d5-5665-843e-f7d39899c552 | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
f2fca48b-c018-5331-9d6f-6baa38a2b221 | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
66daaca9-9721-5c3e-955a-e98ce184bbec | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
55a9826f-a4fc-570e-a8e7-75b6508c2da9 | note | ○ Dips or ponding of water inside the pipe
39ac2eb6-cd93-5fd2-a1fd-8c96d2e696f4 | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
8c7b2cce-5242-5075-98d8-8a865a379b25 | note | Verifying Document - Test Records, CCTV footage
a8a4d4b3-ec20-5856-8ed8-863e20038c8b | note | Frequency - Every section of pipe completed
23e86508-9a24-51c1-9d7e-59a080273ade | note | Inspection Type (Visual, other) - On-Site Test
4e839d14-1624-5ec0-aa0d-a312c32e9af6 | note | Inspection: Key - H
e328ae5f-ac9b-5829-9ded-5d630ed3b6dc | note | Inspection: By - SP/QE/CM/CR
9e95830e-8cbb-41fc-9415-427549927941 | signoff | AUTHORITY HOLDPOINT
a4863d03-9e09-4046-9af3-e77573f02059 | checklist | 561450-DOW-ITP-X002 Installation of Manhole | itp | 561450-DOW-ITP-X002 Installation of Manhole
7e6f5f7d-4bb4-413a-a08a-fffe02973fea | section | SECTION 3 – RECEIVING INSPECTIONS
05f48cf8-b9fd-4786-82a2-bc7964cb3dd5 | checkpoint | 3.1 - Material Delivery
eaf02e44-cbb1-58cf-af1c-e393399ad743 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
8cad225b-166c-570f-bdb5-bb883711dd08 | note | Acceptance Criteria - Items are approved as per contract specification
091f7d2b-7633-5c38-9986-eb60d7852565 | note | ○ DCC approved
88111bd1-a6e6-58f0-b23d-dc3115237030 | note | Verifying Document - Photos, delivery docket
094ce441-1da0-52f6-bc73-fa92ebc0c26f | note | Frequency - On Delivery
0b388bcc-a60b-5073-9b29-1e8aa3040e42 | note | Inspection Type (Visual, other) - Visual
558b048c-414e-5b71-9e21-d252dd924faa | note | Inspection: Key - C
563f34ee-f0b0-593d-b762-80685e5471eb | note | Inspection: By - SP/QE
0500c46a-a9d4-4b6f-ba60-bfd52482a4bf | checkpoint | 3.2 - Set out
ab9f3525-dd17-55ff-b5ef-d9b0ccf4c735 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
197157ff-b923-56d4-9cdd-fd206b2318cd | note | Acceptance Criteria - - Allignment set out matches drawings or aggreed with the Engineer
b4b74ff4-3790-5f7f-be07-4e7b4fe56a91 | note | Verifying Document - Survey marks, photos
c2624b29-6554-5cf4-b2eb-5e0e558cce36 | note | Frequency - Prior to commencement of works
254ed5cc-a460-512a-b6ea-66eee86d54b8 | note | Inspection Type (Visual, other) - Survey
f229a8d6-92ea-560c-b136-1b5c5ed4f1f6 | note | Inspection: Key - H
08bba13a-fff5-57a2-a8e6-5384831ef0f8 | note | Inspection: By - SV/SP/QE
792abe26-115a-47d2-8edb-07cfabcb1a8e | signoff | AUTHORITY HOLDPOINT
1551629d-f665-4f0b-b54f-8f9a65d2cf9a | section | SECTION 4 – IN-PROCESS INSPECTIONS
7c508862-49d0-4728-a799-d3db91487ea6 | checkpoint | 4.1 - Trench Excavation
28af5014-44c6-5555-8df8-02f59367b9b2 | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per drawings
18b0a7fa-a219-5d0d-ba5a-471012bab3cb | note | ○ Floor of trench to be even across width and length
47db84de-6030-5d2d-bbf7-862da7a60096 | note | Acceptance Criteria - - Allow 100mm for bedding
52be0810-d46a-5372-a565-93fec25a0d10 | note | Verifying Document - Photos, measurement checks
4b714825-7038-5b1e-8403-d88f44134381 | note | Frequency - During Installation
d8478c00-6d0a-5006-9fde-c49b6d4bffa8 | note | Inspection Type (Visual, other) - Visual
171ae244-0ad9-5774-90d3-f4fb84e37de7 | note | Inspection: Key - C
75599966-f516-565d-86a6-2aea117452b5 | note | Inspection: By - SP/QE
34ea985c-88b3-4930-beb5-0be2a8310956 | checkpoint | 4.2 - Foundation
074bce11-2b38-561f-b803-4573531b767b | note | Inspection Point: Quality Control Activity - Trench Floor Foundation to be checked it is suitable to support loads
53864fc4-e80a-54e9-abfc-a148e1d1c3a0 | note | Acceptance Criteria - Foundation should avoid very soft clay, saturated soil, or fragmented rock
43f9deb7-dda4-598b-b59b-647859b325eb | note | Verifying Document - Photos
6027f639-56fe-5c64-b452-d1709fbcd36e | note | Frequency - During Installation
8ef78a30-855f-5a7c-930b-e7c5ac5f46ad | note | Inspection Type (Visual, other) - Visual
64719749-53f1-5d1c-9614-9230e178b51b | note | Inspection: Key - H
38587172-158b-554b-a46e-275602227ce8 | note | Inspection: By - SP/QE
c6ed8d0d-2e36-47ef-8c66-988634045425 | signoff | AUTHORITY HOLDPOINT
8fcd0958-9731-4b0a-9b89-3ea38edd385c | checkpoint | 4.3 - MH Installation
7a094cef-180f-5f8a-b288-4f0920587eb3 | note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
ceb22f4c-5d38-5a6d-862e-7a28d6a286cb | note | Acceptance Criteria - -Final levels are in accordance with the drawings or within tolerance and agreed with the Engineer
d0ce067e-315a-5785-9448-39e28647e3c3 | note | Verifying Document - Photos, As-built
c9ba904b-3420-5114-8025-d8580e08d1a9 | note | Frequency - During installation
0a1ce588-301d-5cc9-80bd-d7dc26cc1c73 | note | Inspection Type (Visual, other) - Survey
1afce87c-365d-503a-a439-10804b8f49df | note | Inspection: Key - H
4d787f75-56c9-5bce-bbef-0ba683eee87b | note | Inspection: By - SP/QE
7af1a344-2754-479a-92e9-0631dc0e197d | signoff | AUTHORITY HOLDPOINT
2cff0d4c-6a2d-4f55-b259-dfc03b735175 | checkpoint | 4.4 - Benching
1501727f-c5ee-5f6b-b184-710acc4f1b8b | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
834b1011-fafb-5942-98c1-fb8181070d1a | note | ○ Benching shape to have smooth transitions at bends and junctions
5b6d1aa3-c9ce-55c2-b1c9-f24444624305 | note | Acceptance Criteria - - Benching built up to the specifications
7524a4b7-a74b-5bf7-86f0-caeeb06fbcf7 | note | Verifying Document - Photos
dda97fa4-6fe1-5005-b0a9-7779a7dbaa1b | note | Frequency - During benching contruction
1e1ce97c-8fee-583a-be03-29f155b7b24e | note | Inspection Type (Visual, other) - Visual
b0b93f69-f83d-5d7a-8672-1a0471cf314f | note | Inspection: Key - H
ea5d0a4a-5ced-509c-9fcd-16478da50815 | note | Inspection: By - SP/QE
536d8905-e7a3-4d61-b0ed-403fd4f1867b | signoff | AUTHORITY HOLDPOINT
929c7545-8f15-4fb2-8f74-1db6857b8af7 | checkpoint | 4.5 - Backfill and Compact
a16c68ea-101c-5168-b873-1bbc6081b8df | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
e3e3e80a-bc28-5cfc-a707-6e823b019c1a | note | ○ Compaction testing one test every two layers as required
55173769-c3ba-528d-a075-6f83ea6a22f3 | note | Acceptance Criteria - - 95% MDD in roads, paths, and pavements
66dd2ab1-b916-5535-99ba-6f3bfdb88c8a | note | Verifying Document - Photos, Compaction test results
5fe8ba4c-0bfc-50d8-912d-460b0d5ccbb3 | note | Frequency - During Installation
71ad657f-3edb-5542-b382-9bb99dffe8bf | note | Inspection Type (Visual, other) - Visual, On Site test
8931e8f6-96d5-5ea6-9fab-05ac708dd937 | note | Inspection: Key - H
33784cc0-1f6b-55ff-886d-f21ec3e5821f | note | Inspection: By - SP/QE
fd19e0e3-5ba2-4443-b8c6-8211a19d65b0 | signoff | AUTHORITY HOLDPOINT
3112bd5a-9cd3-4438-86f1-7ae6598f00d2 | checkpoint | 4.6 - Basecourse
cc6b6b52-a889-56b2-8f2b-4e388458975f | note | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
d3c88e11-8c17-59c4-877e-d2623e91ee91 | note | Acceptance Criteria - 98% MDD in roads
9d31119e-b801-5884-bc9c-116276fd59e2 | note | Verifying Document - Photos, Compaction test results
62783151-bba5-5f37-8329-74d363a5569c | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
ce71c7cd-5e09-515d-af8a-74317be165c3 | note | Inspection Type (Visual, other) - Visual, On Site test
6041f129-11cc-57a2-b724-9c475019a2cb | note | Inspection: Key - H
ad1d2f03-f22c-5e46-a86d-e69ee5f12541 | note | Inspection: By - SP/QE/CM
15fb340e-affe-4e1d-9148-15dde16e8783 | signoff | AUTHORITY HOLDPOINT
75189e9f-f889-4518-82e8-222024e96501 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
cfe62015-827d-45aa-bfdc-fa724c0d0350 | checkpoint | 5.1 - Leak Testing
2016f9d0-c180-5723-982e-f986a39a911a | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
0e4b959f-3ae4-58cf-bc83-8b1a2c6bed5c | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
5f9f80f3-b68a-5de9-b1c3-fed8b2f938eb | note | Verifying Document - Photos, test records
bd5c3855-59a7-5b77-84e8-b5193265b89f | note | Frequency - For every manhole
e41b6032-8b6f-5927-854c-811b5069475b | note | Inspection Type (Visual, other) - Test, visual
293a5022-cd57-53f2-9dea-8eddc082753c | note | Inspection: Key - H
08a8083b-740a-5988-a06a-312f974ebfcb | note | Inspection: By - SP/QE/PE/CR
c5c34675-2af0-4c9a-8d30-852d37e4e972 | signoff | AUTHORITY HOLDPOINT
f202a5d5-e25b-4565-b458-ee99a446b2b3 | checklist | 561450-DOW-ITP-X003 Watermain (Trenched) | itp | 561450-DOW-ITP-X003 Watermain (Trenched)
69a1f80a-7c54-4bda-a2b1-699d059788ea | section | SECTION 3 – RECEIVING INSPECTIONS
f8dfa879-834a-4797-85f3-7dd99a0dd365 | checkpoint | 3.1 - Material Delivery
e02f77f9-0dcd-5e48-b883-7d58d7e45135 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and specifications
d29b0bd8-f0d0-5d1b-a559-e1d0b6506d9c | note | Acceptance Criteria - Pipes shall be DN180 PE100 PN16
92ce6735-519a-54ef-baae-fcd56f3cbdaa | note | ○ Material and fittings are approved as per contract specification
fcec1e49-3243-5be1-b35d-f9cbc6ce8ad8 | note | Verifying Document - Photos,delivery docket
dcd68ea9-dae5-573e-b6a2-479423fe4794 | note | Frequency - On delivery
94db2bd9-d6b1-5a5a-b214-6aaca851bff4 | note | Inspection Type (Visual, other) - Visual
2e2d88d6-dad8-5572-ab4c-7d4d1b0acda2 | note | Inspection: Key - C
ad78f71b-d2cb-5967-87db-040c882de3c8 | note | Inspection: By - CR/IP
12746e36-d54e-4755-a7dc-8aa6e449e42d | checkpoint | 3.2 - Set out
5d18a616-28ec-5479-8ff4-c4163fd40582 | note | Inspection Point: Quality Control Activity - Allignment set out as per design or as agreed with Engineer
84867664-a47c-5ca0-aa2f-bd251b8f5873 | note | Acceptance Criteria - Set out matches drawings or as agreed with the Engineer
f951395c-a7f8-55a8-9a57-be14e1c6c2f6 | note | Verifying Document - Photos
5ea37322-9115-5b9b-b652-425d9436b913 | note | Frequency - Prior to commencement of works
74be6dc0-b454-5790-a5ab-041d006b94c4 | note | Inspection Type (Visual, other) - Visual
acadd416-2df3-5116-b408-ae518d12ae1a | note | Inspection: Key - C
98b71267-c3dc-5829-9b15-3d51bc556044 | note | Inspection: By - CR/IP
09d51630-7f1e-4237-8f24-6ea8e1f3dc29 | section | SECTION 4 – IN-PROCESS INSPECTIONS
4b794a28-0324-489f-b1e8-e4779ce1cb35 | checkpoint | 4.1 - Trench Excavation
b077f41e-6ca4-5755-9c8c-630a42a6ec07 | note | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawings
31b4cf5c-6a59-5d18-ad14-afed53ae1363 | note | ○ Floor of trench to be even across width and length.
75307ab5-5dde-5088-b8fe-5d6a3b71779e | note | Acceptance Criteria - Allow 100mm for bedding
c33cdb9a-4918-5076-bc8b-33ed7694b970 | note | ○ Allow for minimum cover of 750mm.
16991585-a709-56cc-aa2c-6d715b6baf4f | note | ○ As shown on Drawings
475b2a71-5df8-5621-bd16-7dc3e24b576d | note | Verifying Document - Photos
1a861ce9-e469-5b3a-8dbe-7fe9641bcc30 | note | Frequency - During Installation
20986d45-6f13-59ce-b468-ba8028142534 | note | Inspection Type (Visual, other) - Visual
f0879830-a4a1-53f1-84d4-5ebd17f8cb1d | note | Inspection: Key - V
6de8b566-01d8-57de-addf-88ec7acb5715 | note | Inspection: By - SP/CR
86343a17-df58-4f8b-8d79-2e74c752911a | checkpoint | 4.2 - Foundation
7a91f584-8474-50d2-8946-80bd3b1b668e | note | Inspection Point: Quality Control Activity - Material trench floor is inspected to ensure suitable
290a5ebe-1abd-5b3d-98d5-db075e2a41c1 | note | Acceptance Criteria - Able to support loads
775571a3-5516-5c04-9630-544ee92b834f | note | ○ Free of very soft material or irregular or fragmented rock
79678b45-c448-56ed-918a-0e2014986b5f | note | Verifying Document - Photos
f04dbbd3-1a94-5c7e-baec-8dfda044a67a | note | Frequency - During installation
965d801d-d9f6-5dc9-a97b-cb8bcbb73588 | note | Inspection Type (Visual, other) - Visual
e0cf15c1-a6f5-563d-a5f2-6c0c2e0b8490 | note | Inspection: Key - V
d5b649e9-8ffd-5ce3-8ebf-6dc8a3bef8ec | note | Inspection: By - SP/CR
4db330d2-2458-443d-8b4b-e3c6309374f9 | checkpoint | 4.3 - Pipe Installation
6e97bfe7-0fb2-5fd5-9921-5bc98ba6f4f2 | note | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
cddf6db2-229d-5d63-835e-c18c34fbc428 | note | Acceptance Criteria - Pipe not damaged during installation
6cc09f2e-b6fc-585b-a08a-a849c08656d1 | note | ○ Pipe is centrally located within trench
26ae06c4-1eac-5660-a7f6-92e1372a5ec0 | note | ○ Pipe levels are within tolerance and according to the drawings
3013e2f9-5294-5eb5-bd06-0300ec9a03b2 | note | Verifying Document - Photos, weld records (if required), Survey of position for asbuilt
fa4e64bc-dbac-5a54-b93c-3ab93dbfa8e0 | note | Frequency - During installation
994cd95b-3ead-5a79-9601-6d306df1906c | note | Inspection Type (Visual, other) - Visual
a4d7ec1b-dc24-58ff-af9e-e977c3b503f5 | note | Inspection: Key - V
f26056cf-1385-5c85-ae23-fac46a29ba8f | note | Inspection: By - SP/CR
ab3ca1da-2c91-4d6b-a690-52beda6f57e5 | checkpoint | 4.4 - Embedment zone
acdb9b6f-5608-5105-9a83-8571225c1430 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
6ff23925-c002-54b9-9ed5-d6a5069ec54a | note | Acceptance Criteria - min 100mm bedding
0b5c5b53-43a4-5b7a-81a6-4fd10c2eee62 | note | ○ 150mm overlay
2b1e9d3e-915a-5286-a88f-b3bdc7522059 | note | Verifying Document - Photos
229aef6f-55e1-5845-9900-7dbbfda13926 | note | Frequency - During Installation
224e4f39-69b1-5bbc-9bcc-5774898a813c | note | Inspection Type (Visual, other) - Visual
8f42ceb7-76c0-5bbb-b196-fb02c85a9422 | note | Inspection: Key - V
2e73600c-4e9b-5ed4-b0a2-7d841c736fd7 | note | Inspection: By - SP/CR
2d495f8f-90d6-4d1d-9f6c-e49de671c741 | checkpoint | 4.5 - Backfill and Compact
e8729456-04c6-5809-9ce9-c699a588d31d | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
acef7be8-fe57-5e5d-b11a-1142e1bb8384 | note | ○ Compaction testing one test every two layers as required
026d5a5b-fe00-5637-af9f-93b6299b991b | note | ○ Conductive signal strip to be laid at 300mm above pipe
f4c234dd-a348-5f12-8485-4e43f8f52c1e | note | Acceptance Criteria - Passing compaction results - 95% MDD backfill - basecourse
77f37144-0da8-58bd-bbb6-3201304b5ccd | note | Verifying Document - Photos, compaction test results
30429be8-897b-55c5-9ecb-b1d742765838 | note | Frequency - During Installation, compaction testing per 50m of pipeline
eb25e315-4f7f-52ae-a2bb-1a09fa285bf2 | note | Inspection Type (Visual, other) - Visual, On site test
46b04a3a-4290-56fd-a941-b4d160fd2413 | note | Inspection: Key - H
82737e9f-2be7-5e5d-bd25-67352c278db2 | note | Inspection: By - SP/CR/IR
97467c1b-6e79-4617-b71a-651223f586dd | signoff | AUTHORITY HOLDPOINT
12069458-99ca-43e2-8f64-bc19d9e21f07 | checkpoint | 4.6 - Basecourse
e3ad4b65-902a-524e-a5c4-823994beb1de | note | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
57dfbac0-ee0f-5d6f-b71d-44967f26341d | note | Acceptance Criteria - 98% MDD in roads
4d633dd4-85d4-5d7d-9750-4024ccb96c93 | note | Verifying Document - Photos, Compaction test results
2151298b-18fd-5f6c-ad9a-9cc785fdec90 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
32112cbe-49af-5345-855e-3d4cc017c6a7 | note | Inspection Type (Visual, other) - Visual, On Site test
07282b73-de52-5f55-a803-9540d77e2fa1 | note | Inspection: Key - H
103990b2-f2a3-52b1-a7d3-5148e82b2220 | note | Inspection: By - SP/QE/CM
59be1519-b0b5-40fa-9782-ad488bd32e81 | signoff | AUTHORITY HOLDPOINT
19c9cd76-1956-4e24-9163-17c308bc536f | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
53dff629-005f-48ed-925b-b3622bc90aed | checkpoint | 5.1 - Pressure Testing (PE pipeline)
c1cb0eb1-20ea-58b1-a2d0-b1d501e73701 | note | Inspection Point: Quality Control Activity - PE pipelines to be tested in accordance with specifications
f2e52f54-6d94-5b66-b0a6-580101bfa773 | note | Acceptance Criteria - Specification Attachment C, clause 4.7.5
841e40ee-7776-531e-b5ab-065ea06885f3 | note | ○ No Thrust block failures, No visible leaks, Do not exceed make-up water limit
fa4f2894-91b9-5a93-be9e-cf3bd9b070ba | note | Verifying Document - Test Records
08ea1585-5179-5bc2-aeca-60a12fb136f5 | note | Frequency - Before commissioning
f4ee2994-2638-5e82-a4db-567f25778637 | note | Inspection Type (Visual, other) - On-Site Test
94362b4d-f210-54be-9b81-961ecaed0455 | note | Inspection: Key - H
01fbbde7-1716-54e6-afe6-475096a95855 | note | Inspection: By - CR/IP/DR
5401ee63-c9fb-4290-ac21-d91c3b640dbd | signoff | AUTHORITY HOLDPOINT
5b20c8f2-96a0-440c-b1ff-96de8c52cd55 | checkpoint | 5.2 - Disinfection
2fbf20a3-d7cb-54d5-90c9-20fdfd93a106 | note | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
0be34b8f-8e6a-5391-833b-8f443e82641e | note | Acceptance Criteria - Specification Attachment C, clause 4.12
11212408-9d93-5669-a9bf-8412d41c01fd | note | Verifying Document - Test Records
9d4bd7d3-297d-5f3a-bf7d-d7c6028d6105 | note | Frequency - Before commissioning
67c1bbee-c018-5c52-b3bf-a33f218b4754 | note | Inspection Type (Visual, other) - On-Site Test
d7c80519-f018-5907-9a83-edde94fa4803 | note | Inspection: Key - H
ae9866ec-e1c1-560e-9a02-60032628cea6 | note | Inspection: By - CR/IP/DR
4fac940b-b088-47e5-8477-59134b94cb78 | signoff | AUTHORITY HOLDPOINT
9f0e3b77-fdaa-49eb-a04b-573c9a9df8bf | checklist | 561450-DOW-ITP-X004 Watermain (Directional Drill) | itp | 561450-DOW-ITP-X004 Watermain (Directional Drill)
8d8cbfcb-dba0-45b1-9495-a5d12c838bb1 | section | SECTION 3 – RECEIVING INSPECTIONS
84180960-f1d6-4ea8-be75-d5767da0cc78 | checkpoint | 3.1 - Material Delivery
8e32e384-6407-5c5e-92a6-4efa32f5bfaf | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and specifications
1f9b7df3-dc01-517b-b691-d087d3425c17 | note | Acceptance Criteria - Pipes shall be DN180 PE100 PN16
3ed36cba-a0ff-5830-83cd-35fc160b1d2a | note | ○ Material and fittings are approved as per contract specification
b71879cc-9d80-5d68-ac86-efce8825862d | note | Verifying Document - Photos,delivery docket,
69404173-2f14-5b11-a0a9-eab916402d71 | note | Frequency - On delivery
4b681484-3a6c-51ba-b729-b72a391131a6 | note | Inspection Type (Visual, other) - Visual
9a364b70-37d9-5936-8a7b-f41997aa759a | note | Inspection: Key - C
f8193a9c-f8f9-56fd-b5bc-0c22597d2a59 | note | Inspection: By - CR/IP
fa0924d7-f1de-4ce9-9f8a-a5caddee0cd2 | checkpoint | 3.2 - Set out
d8c106d0-3050-57f3-ba26-4f38da412081 | note | Inspection Point: Quality Control Activity - Allignment set out as per design or as agreed with Engineer
367c1c76-c2b6-53b2-8f65-a62625f6dd1a | note | Acceptance Criteria - Set out matches drawings or as agreed with the Engineer
2519bf14-5958-5e62-8873-607945673cea | note | Verifying Document - Photos
20012353-1983-569a-ad86-83b164821202 | note | Frequency - Prior to commencement of works
d0477762-da11-5e0c-888e-a846cf6131cf | note | Inspection Type (Visual, other) - Visual
a8308691-e765-5b98-98dd-d73e3aeb0cb4 | note | Inspection: Key - C
0c24e418-1d47-513f-a613-b049deaa3d63 | note | Inspection: By - CR/IP
25839679-bc3c-414e-9b26-61fac41dc824 | checkpoint | 3.3 - Service Locate
50fa4f1a-f441-5fa8-bd19-cc0d1b59b4aa | note | Inspection Point: Quality Control Activity - Mark out known existing services from service plans along alignment
3f0a5efd-e970-58fe-a7b8-0fd3b1db4e55 | note | ○ Pothole sevices and confirm design alignment
19a17ea3-8f69-50e5-abd0-832633202aff | note | Acceptance Criteria - Positive locate of services close to planned alignment
7789bb03-b84d-5331-9cfd-8489800c8d8b | note | ○ Review and acceptance of any required changes due to services by Engineer
1afd0a05-a44e-5151-adb9-624a7cbddfdb | note | Verifying Document - Photos
2436017d-2a11-581a-9c4c-3d1b4d1a1957 | note | Frequency - Prior to commencement of works
3d99ca21-4832-5908-9f18-27fc68f6c7e6 | note | Inspection Type (Visual, other) - Hold Point
2fecec49-ec1d-5c31-bd4a-81a40ec55461 | note | Inspection: Key - H
fcbcc14a-4ea6-5d66-929f-3ea7897eb0bd | note | Inspection: By - CR/IP
bb8b746a-f9bc-4e77-9dec-8bca01ade180 | signoff | AUTHORITY HOLDPOINT
63e0f24f-e18e-465f-9c36-c7800fc954a8 | section | SECTION 4 – IN-PROCESS INSPECTIONS
f198bbd6-edf3-4b3b-9a04-5e36255f1dba | checkpoint | 4.1 - Excavate Launch Pits
82565523-3899-51dc-91d3-1ff51de6218b | note | Inspection Point: Quality Control Activity - Excavate to acheive required depth
02bf2ae6-951f-5128-b039-0d93f6b79c22 | note | ○ Floor of trench to be even across width and length.
0ca759cf-f5a3-517e-8c72-be3c9258626b | note | Acceptance Criteria - Cover of 750mm for directional drilled watermains in all areas
6e43815f-09f5-5393-bc34-988ea4a3302a | note | Verifying Document - Photos
3b5c13db-7cb0-5588-b85e-e6bd5b0e411f | note | Frequency - During Installation
1a068dfd-3ef2-5847-bda4-bae3ffea7391 | note | Inspection Type (Visual, other) - Visual
5958c213-8b6b-5838-b0c7-169b0c4d08f1 | note | Inspection: Key - V
ffef2edf-4cfa-5b8c-a278-9fbddd93da06 | note | Inspection: By - SP/CR
feb3b948-40a6-469f-a84c-a3ab235d0f50 | checkpoint | 4.2 - Trench Excavation
bfffc541-5a30-5e1e-be93-e94f65143884 | note | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawings.
9af2838e-7f1e-56c4-ab46-e80869d7fb01 | note | ○ Floor of trench to be even across width and length.
e5eb895c-3ec7-5a04-b6dd-9fa84d9dc99b | note | Acceptance Criteria - Allow 100mm for bedding
ca5e33ac-fa25-50b9-a9e8-a5339567e0fa | note | ○ Allow for minimum cover of 750mm for watermain
5b0e3e6d-f54f-5e8a-86e8-452b2e2c9208 | note | ○ As shown on Drawings
1adc5690-4c7b-500e-9861-0bffd26324dd | note | Verifying Document - Photos
9f2aeffc-471d-509d-b4fe-ce182bdba07b | note | Frequency - During Installation
0855106c-2292-5466-860d-404b7bdfc8a9 | note | Inspection Type (Visual, other) - Visual
4c2608f0-381e-5ca8-a7ce-eaf932c4c431 | note | Inspection: Key - V
fc5a7079-4e7a-50c1-be40-7207c74a7235 | note | Inspection: By - SP/CR
b147a98b-41ff-4b16-9f12-43f0cab04bec | checkpoint | 4.3 - Foundation
2f9bd091-4763-5e78-ab57-c59a4bc32690 | note | Inspection Point: Quality Control Activity - Material trench floor is inspected to ensure suitable
b3964605-52f5-5866-b050-e356f7fd950a | note | Acceptance Criteria - Able to support loads
d9bf9227-b251-5ee6-ad4f-9749348ea710 | note | ○ Free of very soft material or irregular or fragmented rock
72dd7804-6bbe-5058-945a-94e476002ed5 | note | Verifying Document - Photos
3d9cf012-7c2c-5b59-8a87-f4ef6ae58f6e | note | Frequency - During installation
61e6ed62-5934-50b3-9da5-a98ec6dccdba | note | Inspection Type (Visual, other) - Visual
657574ba-823c-58f0-913e-4531bf55163a | note | Inspection: Key - V
ae98f1bc-d9aa-53f1-bfa0-5d12a430a19a | note | Inspection: By - SP/CR
19e1fc22-aa39-4391-91ac-33f08446c8eb | checkpoint | 4.4 - Pipe Installation
d8566404-f9d9-5770-a801-c91a7bf2838f | note | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
6ee39207-d6f8-55f4-9991-70fb0f30cf5c | note | Acceptance Criteria - Pipe not damaged during installation
1f6350ac-b51e-5668-a0a6-3152cf68b13d | note | ○ Pipe is centrally located within trench
c20ec179-731b-5279-aa6d-9fb6159c86e5 | note | ○ Pipe levels are within tolerance and according to the drawings
32ff0d4a-93c3-5398-8d0a-dbb7b8b9b7cc | note | Verifying Document - Photos, weld records (if required), Survey of position for asbuilt
a50df230-33b1-56ea-a7f4-0c13352d50da | note | Frequency - During installation
d645440e-3ef1-55ea-a5fa-f19bc6cf60ec | note | Inspection Type (Visual, other) - Visual
078c5fa4-49d8-5a95-b4e5-2de8c5f057eb | note | Inspection: Key - V
3dd3b1cf-1b0b-54d1-be2c-91f802f268f1 | note | Inspection: By - SP/CR
88bd7545-b360-4910-b3d9-0a33dfebd648 | checkpoint | 4.5 - Embedment zone
559e5fac-25fb-51c6-ab62-a85bd54aceba | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
bfce11d8-78a1-5633-aa99-e3967c884d65 | note | Acceptance Criteria - min 100mm bedding
56a9eafb-a751-5583-81ca-4b44b692eab2 | note | ○ 150mm overlay
774a21e2-d030-56e8-9fd9-88f4a7b147a1 | note | Verifying Document - Photos
4987bc89-9816-55d9-95ce-40d049aa8e75 | note | Frequency - During Installation
4b681d26-9de9-51db-91f2-e2f0c308d7db | note | Inspection Type (Visual, other) - Visual
5e42ed3f-e806-510f-aad6-34a4feb25482 | note | Inspection: Key - V
0de03fc2-326c-59b0-a44e-c7ef70727d70 | note | Inspection: By - SP/CR
1ca77908-aa63-48d3-a3e3-73cd2c8d63f2 | checkpoint | 4.6 - Backfill and Compact
fa70ab24-0a28-518b-a650-79dc4b476bd8 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
277971df-c33d-5dc4-9bc6-d27579c4da6a | note | ○ Compaction testing one test every two layers as required
979b51f6-df63-5434-8b49-0cc62b7ae973 | note | ○ Conductive signal strip to be laid at 300mm above pipe
d5f9eb02-9897-5ea2-9e5b-63e30d1b2deb | note | Acceptance Criteria - Passing compaction results - 95% MDD backfill - basecourse
49382616-7a63-55dc-b688-f7382f79c546 | note | Verifying Document - Photos, compaction test results
9e9742a8-7d54-56a7-9c43-a5323f317898 | note | Frequency - During Installation, compaction testing per 50m of pipeline
f1d8e950-4f49-5bff-8107-d83d281a5455 | note | Inspection Type (Visual, other) - Visual, On site test
f9bdb16b-d51f-5540-9645-cf537974a2e1 | note | Inspection: Key - H
32722d8c-c76a-52b0-9d8e-0879276fdc6e | note | Inspection: By - SP/CR/IR
22c0e5c6-4120-4b6a-909e-f5656d023fb7 | signoff | AUTHORITY HOLDPOINT
7842c275-306e-44bf-b7a4-351e83f81c4a | checkpoint | 4.6 - Basecourse
63faeea4-11e7-506f-aa73-18f5bec69483 | note | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
f0765766-5ac6-5194-8cd5-047991155d58 | note | Acceptance Criteria - 98% MDD in roads
f41ef0f8-9977-53e5-8b58-3212a11693a4 | note | Verifying Document - Photos, Compaction test results
e0dad0fc-979e-54ac-990c-6736055deebe | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
a6261dcc-3882-5f3f-8a50-d85c2d445c7f | note | Inspection Type (Visual, other) - Visual, On Site test
bf8178c0-c582-50ce-81f9-7928a8512f32 | note | Inspection: Key - H
8533a7be-064b-5d00-a792-8707896af53c | note | Inspection: By - SP/QE/CM
6e08641d-76eb-45af-908d-96aa1bc5217c | signoff | AUTHORITY HOLDPOINT
ec78d542-6a9e-49e7-aeb9-0e3ddd96d46f | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
79e17b69-764c-42ad-9d88-cf14bf7ea5e0 | checkpoint | 5.1 - Pressure Testing (PE pipeline)
cd66e3c2-7666-51f1-8f7f-3cedf5385f1a | note | Inspection Point: Quality Control Activity - PE pipelines to be tested in accordance with specifications
addf5539-587b-517c-9433-08ee900fd180 | note | Acceptance Criteria - Specification Attachment C, clause 4.7.5
140667a9-3613-5f93-954c-8f5e65cd91c2 | note | ○ No Thrust block failures, No visible leaks, Do not exceed make-up water limit
f47139f1-13e9-54f4-8541-9ceef2312697 | note | Verifying Document - Test Records
52aec72d-0e24-5e89-8bb8-501b3684a120 | note | Frequency - Before commissioning
bcd93435-1d14-5019-8ed7-3eaaa0d211a7 | note | Inspection Type (Visual, other) - On-Site Test
ddb5f891-e8d5-5d0d-8487-8689003bb4ea | note | Inspection: Key - H
404c2e36-1189-5e95-9a5a-e85a1fedb305 | note | Inspection: By - CR/IP/DR
71252575-690e-4ad3-bb08-06bd2dada53d | signoff | AUTHORITY HOLDPOINT
6e9ad73b-a6a3-49bb-8dfd-0e3865a2848b | checkpoint | 5.2 - Disinfection
8e7d9fe4-2859-5fc5-a130-f209d9ab452b | note | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
34544fa0-cc97-574a-b1b7-27d257fea55d | note | Acceptance Criteria - Specification Attachment C, clause 4.12
7a2bc229-3536-5356-8949-27b7dc85a07e | note | Verifying Document - Test Records
f849c896-7d8a-53de-b525-159af3c3224b | note | Frequency - Before commissioning
21a815dd-f141-5c58-adfa-2f326234b0a6 | note | Inspection Type (Visual, other) - On-Site Test
99bb5799-30ed-5765-af65-a68bbb95577e | note | Inspection: Key - H
48f4d710-15b1-5b84-a1bc-e34331dcaafa | note | Inspection: By - CR/IP/DR
6901d490-0c77-4a48-8052-54d6a3f4cbde | signoff | AUTHORITY HOLDPOINT
2c9bb35f-3db2-4721-a06b-327e0b2abb56 | checklist | 561450-DOW-ITP-X005 Butt Welding | itp | 561450-DOW-ITP-X005 Butt Welding
524ebca2-d23a-4419-b844-2c189c3621f4 | section | SECTION 3 – RECEIVING INSPECTIONS
6373221d-6c0e-4e17-92b8-64eae09237e4 | checkpoint | 3.1 - Material delivery
9de41165-89b0-58c3-8ea0-5c8720be75b0 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and specifications
8372476d-c1f5-5b2a-bd19-f58e6b564305 | note | Acceptance Criteria - Pipes shall be DN180 PE100 PN16
34001854-5ea7-5c29-ba62-b08428744852 | note | ○ Material and fittings are approved as per contract specification
6fc673f6-e53f-517b-ab33-e460686f011b | note | Verifying Document - Photo of pipe bundle(s) showing pipe classification.
5e8daa32-974e-56d2-80e1-f760b3364335 | note | ○ Delivery docket/packing slip
4aa30a0a-3f2b-5279-b5cf-e7ca5d38c6b1 | note | Frequency - On delivery
b468f30d-8a97-5f1c-8fd8-fd7f8618548a | note | Inspection Type (Visual, other) - Visual
882a580e-4d2c-5199-9441-b5eda6d882d1 | note | Inspection: Key - V
e60e514b-ef0f-59c2-b5cf-1c0e0671e9d7 | note | Inspection: By - CR, IP
1455057b-1938-4195-8153-dcf0e851ebeb | checkpoint | 3.2 - Certification of welding equipment
d781c839-96ae-5b20-ae9e-3fc8cf4d498e | note | Inspection Point: Quality Control Activity - Confirming just one butt welding machine in use during life of project.
76746b1b-963c-5d16-bac6-b53b7b441136 | note | Acceptance Criteria - Accepted by Client as suitable for use
717c18ab-b3de-5672-ba66-ac8aba46fbe8 | note | Verifying Document - Current calibration certificate/service record
2e19e464-2e92-5592-8a96-1fba91484f4b | note | Frequency - Prior to commencement of works
59547939-a150-5f0b-b631-123e6f968f4b | note | Inspection Type (Visual, other) - Hold point
747f08c4-43fb-5cf8-a9b9-e891df722c9b | note | Inspection: Key - H
f459c69a-12f6-53f0-afd4-78199e57571a | note | Inspection: By - IP
a5878b78-17b4-42f7-a534-9a6676630ab0 | signoff | AUTHORITY HOLDPOINT
7147b971-ef20-4a90-958c-e22ec8771754 | section | SECTION 4 – IN-PROCESS INSPECTIONS
5a76cfb7-f4df-4e65-ba29-27520fcd6ee2 | checkpoint | 4.1 - PE Welding – Operator and Equipment
8334d2cb-e04f-58de-aec7-41f6a98d4cfd | note | Inspection Point: Quality Control Activity - Competency certificate of welder and certificate of fitness for welding equipment
f963b942-25e2-534b-aaf4-7018ad16237c | note | Acceptance Criteria - Testing of weld samples carried out by an IANZ accredited laboratory.
cee431f8-da3e-5030-9fad-c0d9378b7e32 | note | Verifying Document - Current welding certificates of operatives
283e7fd3-83d9-557e-8747-24e26f1f4490 | note | ○ Current calibration record of welding Equipment
dda6ae0a-535d-5079-8d86-4716d5547e1b | note | ○ Tensile test results
d9f8ed19-116c-5245-a9c5-748f62ae7e4d | note | Frequency - During Installation
bc586208-aa61-5853-bc9f-fd5ad24bc5c9 | note | Inspection Type (Visual, other) - Inspection, Examine
8dd878f2-2798-5849-9bbe-58608e4e5c1f | note | Inspection: Key - I, E
8aeef420-cd2e-5a5e-8d39-a099d38b6722 | note | Inspection: By - CR, IR
dcdb788c-a80d-4202-ab79-39e0465b2753 | checkpoint | 4.2 - Test Sampling
67a75bd0-f110-5adb-b452-5e7cb9085cca | note | Inspection Point: Quality Control Activity - one pre-qualification per operator, one pilot weld per machine/per DN.
67410916-4f5f-50f6-ae01-26c2099fdfcd | note | ○ Test failures will require the previous weld and the following weld to be tested and passed.
9880cbc0-7b5e-5047-a38d-aa26b6d084a9 | note | Acceptance Criteria - Pass/Fail
4a69790b-4973-51c0-a22d-7cdd019a1308 | note | ○ ISO 21307
93e3a6bf-b00e-56a9-bb81-3fcc30e05560 | note | ○ ISO 13953 (Testing)
3cd394a6-f97b-5497-aece-919fc87d4202 | note | Verifying Document - Tensile test results from Kiwi Mechanical Ltd
1eaa4b71-932b-529d-9220-587cc14c62b1 | note | Frequency - Every 50 welds per operator (or as requested by Client).
170b36f0-744e-5e76-ac99-abf35ad33177 | note | ○ Test frequency to be reduced in response to consistent pass results, with Engineers approval.
738a1183-9f0d-50c6-bc15-bac89056dd87 | note | Inspection Type (Visual, other) - Operation
467c560c-5715-5e3d-821f-ec8119778a08 | note | Inspection: Key - O, R
085e5e4b-4a05-548a-8ddb-926ff6f5c3fe | note | Inspection: By - WS/CR, IR
3f3d676f-62df-48b7-97dd-086340d99ffc | checkpoint | 4.3 - Weld Completion
089a53fd-4dd2-5569-aeda-461b4ecc207b | note | Inspection Point: Quality Control Activity - Weld completed to required standard and specification
9753b4c4-5ee2-5517-abdb-b0391ec97194 | note | Acceptance Criteria - Pass/Fail
1c733ee4-3bdb-5c65-88e3-e20bf100f76a | note | ○ ISO 21307
2904c17c-f64a-5235-94ee-5138fc9ffd31 | note | Verifying Document - Power App or manual records
689175c4-6f21-5a61-b8a9-abc865882119 | note | ○ Data log from welding equipment
7df972d1-ec8d-57e0-8376-bf2a58b42853 | note | ○ Photo Log
b36646cd-0270-546f-b5c7-48fb740e8d3d | note | Frequency - Each weld
13626414-8bf0-5a8d-bbaa-5c3526156898 | note | Inspection Type (Visual, other) - Check, Dimension Inspection
89273140-9cc1-50e3-9968-9fea3ebf0f73 | note | Inspection: Key - C, D, R
d69ea8e1-1092-5dbc-9edf-898f3f25dc27 | note | Inspection: By - WS, CR, IR
6843d6b4-e73e-41b1-90f1-863373123581 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
2cf15509-641f-4874-a857-5d7f7472a53f | checkpoint | 5.1 - Completion of QA
6d3177ee-71a3-5ccf-ba0f-a0f1450b1dff | note | Inspection Point: Quality Control Activity - Ensure QA package complete.
a2a6710c-1092-543a-b9eb-a40a1325add1 | note | Acceptance Criteria - all necessary documents including HDPE welding compiled and handed over to ER in completeness.
de0f4719-f185-532a-9ee2-ca00c0f4c934 | note | Verifying Document - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment.
d2fff832-42cd-5ad6-a074-954573d77c7b | note | ○ EF controller printout for all EF joints
d6af8c34-6b89-5701-8f30-9c117b3544da | note | Frequency - Before practical completion
d834ee1d-f561-5dd1-a37a-accd0380b731 | note | Inspection Type (Visual, other) - Inspection, Monitor on Random Basis
be5b09d7-c938-55cd-80f6-ed3353e4a0d5 | note | Inspection: Key - I, M
3349086b-6c35-5c94-9759-bfce57495f84 | note | Inspection: By - CR, IP
89876595-8ede-49b9-b899-8017947ed107 | checklist | 561450-DOW-ITP-X006 EF Welding | itp | 561450-DOW-ITP-X006 EF Welding
c1e30351-6b1f-45ec-8481-c8339bdfc3bf | section | SECTION 3 – RECEIVING INSPECTIONS
988da88b-faf5-4145-ba97-81d82ff16d9a | checkpoint | 3.1 - Material delivery
790bf116-eaaa-5eba-b908-f933f8fb168a | note | Inspection Point: Quality Control Activity - Each pipe welding location check pipes to be welded
5f8bcd0c-eb74-51ec-92f1-f63d32f8f1a5 | note | ○ Each EF fitting
d2ce81ad-3f2f-5534-aea3-f597558675bd | note | ○ Check bags undamaged and sealed
6dc51a14-d326-518d-a445-b6dca23f4e21 | note | Acceptance Criteria - Pipes shall be DN180 PE100 PN16
06bc52f0-ff0c-5755-afea-dc05f49e04f9 | note | ○ EF fittings correct size, SDR, PE100 and pressure rating.
31008a2e-bdb3-500c-a2d8-9006851303c5 | note | Verifying Document - Photo of markings and labels on pipe.
86df8768-a9d5-591a-ac4a-368d7cdfb472 | note | ○ Delivery docket/ packing slip
2ffeef06-a050-591a-b69a-530b24e9ba59 | note | ○ Scan bar code on fitting
8ebd2e55-b930-5ec0-888f-c2dbb77c1ca2 | note | Frequency - On delivery
9cb550b6-16a0-5899-b68b-b67b4d99ea7c | note | Inspection Type (Visual, other) - Visual
01d2e968-c310-58ae-b050-a83eff214715 | note | Inspection: Key - V
ce43b4c5-58da-5332-ae41-bcb64aac3659 | note | Inspection: By - CR, IP
626931a2-ce2e-4cd0-914c-cf45a678a40c | checkpoint | 3.2 - Certification of welding equipment
f2de90cd-3bfa-5846-8c55-54f17ee9f4c4 | note | Inspection Point: Quality Control Activity - Confirming just one EF welding machine in use during life of project.
da74ee92-4ce9-5bbc-83f9-7c7cc2d59abe | note | Acceptance Criteria - Accepted by Client as suitable for use
fa6d3d64-608b-5a91-8d4d-183a55585627 | note | Verifying Document - Current calibration certificate/service record
271446e8-bfc3-520a-9044-beb5e7af7714 | note | Frequency - Prior to commencement of works
031f3630-1122-5f8a-880c-e2f97bf69efc | note | Inspection Type (Visual, other) - Hold point
4371b285-885c-5ad7-9063-c6c38cefe0be | note | Inspection: Key - H
be32ca52-d0cd-55c0-a49e-a748bbdb82a6 | note | Inspection: By - IP
6189bc5e-2ec7-4c81-9969-427f017d032b | signoff | AUTHORITY HOLDPOINT
e971d1c7-b20a-4d56-b7b2-19c10b71f7bb | section | SECTION 4 – IN-PROCESS INSPECTIONS
396d9750-b6cb-4756-b39f-44eea7dfbfb6 | checkpoint | 4.1 - PE Welding – Operator and Equipment
4b7756c3-85f4-5f59-a4ae-5cd850d2b493 | note | Inspection Point: Quality Control Activity - Competency certificate of welder and certificate of fitness for welding equipment
e8c356dc-e91c-5f88-831e-d9f686e46b9c | note | ○ Generator capacity adequate for the EF fittings.
cf199ed1-54ef-5479-80f9-ac137fc955c3 | note | Acceptance Criteria - Have peel decohesion test of weld samples carried out by an IANZ accredited laboratory.
014f630c-35d3-5eae-868d-790dceb89fcd | note | Verifying Document - Current welding certificates of operatives
1b49e27b-b4e2-5e74-a330-e50ef9ab8437 | note | ○ Current calibration record of welding Equipment
f92e8b0c-e1e4-5b82-a6cf-466762ee8b60 | note | ○ Peel decohesion test results
9ccb1fa3-25d5-5b30-8bfe-4807dbd0d9cb | note | Frequency - During Installation
3b48a67e-72af-5962-9107-de64ff6d360a | note | Inspection Type (Visual, other) - Inspection, Examine
94c9eb18-472f-5a33-a5f6-a18c807322a6 | note | Inspection: Key - I, E
b82c6407-4232-52a3-b41b-f7dd3ca3db27 | note | Inspection: By - CR, IP
ea9cb44c-40ab-49c3-b024-4c0b9969038c | checkpoint | 4.2 - Test Sampling
cdc70a16-79de-5267-b2b2-3681248edf1f | note | Inspection Point: Quality Control Activity - one pre-qualification per operator, one pilot weld per machine/per DN.
9cdd8145-fec6-5b21-9b2f-d1e7c2d5ec32 | note | Acceptance Criteria - Pass/Fail
f9e7f615-5e0d-55c6-847d-2628dcaecd27 | note | ○ ISO 13953 (Testing)
9691a34c-49e2-560a-af89-d161cd5df70e | note | Verifying Document - Peel decohesion test results from Kiwi Mechanical Ltd
14829eb8-72cf-58dd-9978-3b64965861e7 | note | Frequency - Every 20 welds per operator (or as requested by Client).
355904ab-35b3-5059-9ce5-45b8ba3c6bba | note | ○ Test frequency to be reduced in response to consistent pass results, with Engineers approval.
19349b11-3f4a-5456-9d41-75d787343096 | note | Inspection Type (Visual, other) - Operation, Review
6a1ba33c-5b18-5e77-aea6-413ff578b72b | note | Inspection: Key - O, R
3ad715ca-16dd-5256-bb42-736c0cff98a9 | note | Inspection: By - WS/CR, IP
caf63ee8-3d6d-471e-9d9b-d69102ea28b9 | checkpoint | 4.3 - Weld Completion
f48c3e1d-f12d-5fa0-9cb1-9c137fb97db0 | note | Inspection Point: Quality Control Activity - Weld completed to required standard and specification.
96ef4892-7de2-5642-9927-5e5b787c8c00 | note | ○ Only move strings after EF’s have cooled!
d9d39a04-2d8d-5dc7-8c0c-e6229c138779 | note | Acceptance Criteria - Pass/Fail
21dd90ce-d95a-5ab3-a61a-d23dde56e35a | note | ○ PIPA POP001 version 8.1 2021 and POP014
e21bbae8-6855-5024-92bc-486319492605 | note | ○ EF controller printout for all EF joints
8990d69a-f1f6-511d-989a-feec0249e218 | note | Verifying Document - Power App or manual records
f881470e-c718-59a7-bbfa-b765d2775d15 | note | ○ Data log from welding equipment
6a5bc7c6-344b-5943-9e92-7614bbcd020f | note | ○ Photo Log
dad5ab20-fd46-5c6b-98ac-f369722756d4 | note | Frequency - Each weld
932425f7-f076-5264-a500-38cbf115a9bb | note | Inspection Type (Visual, other) - Check, Dimension Inspection
39180c62-44ad-5a86-9638-28a2cfa36ea1 | note | Inspection: Key - C, D, R
53e436e2-ea2e-5b4c-b168-6a5a61b8e33a | note | Inspection: By - WS/CR, IP
f76a43e5-c841-45a0-8de7-fe42284394af | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
c9eb3f10-4ec9-4f87-86d6-0444ab171484 | checkpoint | 5.1 - Completion of QA
125ab79b-aabf-5a14-a788-e0ca845c5f9b | note | Inspection Point: Quality Control Activity - Ensure QA package complete.
08bf1b7c-bde5-546b-8eaf-9912de178dd4 | note | Acceptance Criteria - all necessary documents including HDPE welding compiled and handed over to ER in completeness.
e4f7096c-eb81-500a-a658-5f1c1b08fa7f | note | Verifying Document - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment.
5710ba99-1c92-52d2-972c-472f518c7dfa | note | Frequency - Before practical completion
aa5d2773-c0b5-5669-9695-9279e2340d17 | note | Inspection Type (Visual, other) - Inspection, Monitor on Random Basis
cf7612c7-4d00-5c56-8ed8-ba5e9712d79c | note | Inspection: Key - I, M
73bb0bd1-8783-5207-ac22-181f100100f0 | note | Inspection: By - CR, IP
78a5e8cf-f302-4b37-bf8c-6f3a719be665 | checklist | Water Lateral Connections Checklist |  | Water Lateral Connections Checklist
3180a106-1f01-467b-89af-0b3a2d0d5adf | section | Details Connection
8da5f21b-f809-4c19-af9f-bb9b438174b4 | checkpoint-no-value | Details Connection
d6584949-c06a-5379-bb4c-902701d1da7c | date | Date
119f6fff-205a-5198-bb06-ff0645256221 | textbox | Installer Name
e7a312e8-c7ef-5f4b-8c61-d3e28d3345af | textbox | Property Address
88b8ebab-0ba9-45ae-a409-97682abcbd4c | checkpoint | Talbot nut tightened
de6ce613-400f-4b67-8b34-94ea81d11441 | checkpoint | Talbot open
838dbd07-9aae-443b-a89c-d92a23611ac1 | checkpoint | Denso tape applied
c7aea7db-25e2-4c0f-97fb-6942964cac9c | checkpoint | Site photo attached
bc671b2d-a09c-46a6-977a-390ffc20419f | checkpoint | Install Accepted
f6efecac-746a-427f-bd3c-9e707c104182 | section | Details Manifold
9f514f0d-cc05-41c3-966c-b7c772769f87 | checkpoint-no-value | Details Manifold
f290a114-5966-5032-ac6b-b98af9d6755d | date | Date
ef9353a8-a555-5f4b-88be-4d1723bf4fa1 | textbox | Installer Name
90066fc9-e906-52ab-ba6c-9caaf3131143 | textbox | Approx distance from main (m)
ceac0122-889b-4d67-84e6-40e838aa293d | checkpoint | Trace wire installed and visible in box
4612ba58-00a0-4d31-bb0c-41e6e3476a50 | checkpoint | Box set up 250mm from boundary
559297d2-7991-49c7-955f-81e651c99b16 | checkpoint | Manifold 165mm below lid
7bf695bf-7889-42b6-a33a-5b4cad2adf42 | checkpoint | Site photo attached
b9881ddd-a41d-467b-83a0-c3bd31cc8ac7 | checkpoint | Install Accepted
3360f986-2bed-4cd2-8a08-9a18bc7150f0 | checkpoint | Final Signoff
773a8d87-293a-4130-9501-dc010e49c7da | signoff | SIGNOFF / REQUEST SIGNOFF