## General
SECTION 1 – GENERAL DETAILS
Project Name: | DCC9459 - Reid Avenue, Mosgiel - Stormwater Upgrade | [5 empty] | Inspection Key |  | Responsibilities
Project Number: | 561461 | [5 empty] | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council | [5 empty] | B | Report by Breach | ER | Engineers Representative | Will Heffernan Meng Hong Loh
Contract Number: | DCC9459 | [5 empty] | C | Check | CR | Cust. Representative | Todd Williams
Area/ Sub-System: | Reid Avenue, Mosgiel - Stormwater Upgrade |  |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel | Aaron Sutherland
[7 empty] | E | Examine | MC | Material Controller
ITP Number: | Installation of concrete SW Pipework |  |  | Version: | 2 |  | H | Hold Point | OP | Operations Manager
ITP Description: | General ITP for Installation of Concrete Stormwater Pipe | [5 empty] | I | Inspection | PM | Project Manager | Philip Rowley
Discipline: | Utilities | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor | Matt Paterson
Specification: | Three Waters Infrastructure Renewals & Upgrade. Specification - Reid Avenue, Mosgiel | [5 empty] | O | Operation | QE | Quality Engineer | Matt Paterson
[7 empty] | R | Review | QM | QA Manager
Drawings: | WSP 6-CD109.96 Drawings C101, C102, C110 through C114, C120, C121, C200 through C204 & C210 | [5 empty] | S | Subcontractor | SP | Supervisor | Aaron Sutherland
[7 empty] | V | Visual Verification | ST | Superintendent
Prepared By: | Matt Paterson |  |  | Date: | 2025-06-18 |  | W | Witness Point | SV | Surveyor | Eroni Vari
Quality Specified: | [8 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: | Aaron Sutherland |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: | Matt Paterson / Phil Rowley |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: | Will Heffernan / Meng Hong Loh |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type | Inspection
[7 empty] | Key | By
3.1 | Material Delivery | Inspect for damage and wear, Confirm items are correct as per drawings and Specifications | -Pipes shall be DN600 Class 2 RCRRJ - Items are approved as per contract specification - DCC approved | Photos, delivery docket, MDD results & Materials grading for backfill materials | On Delivery | Visual | C | QE
3.2 | Set out | Set out completed by an approved surveyor marked allignment | Allignment set out matches drawings or aggreed by the Engineer | Survey marks, photos | Prior to commencement of works | Visual, Instrumental | H | SV SP QE PM ER
3.3 | Embedment Zone Materials - AP20 | Visual quality check AP20 is evenly graded granular material free of detritus | Material Approval by Quality Engineer | Photograph | On Delivery | Review & Approval | R | QE
3.4 | Backfill Material - AP65 | Submission of Test Sheets for review | Material Approval by Engineer Rep | Test Certification | Once | Review & Approval | R | QE ER
3.5 | Pavement Preparation Material - M440 | Submission of Test Sheets for review | Material Approval by Engineer Rep | Test Certification | Once | Review & Approval | R | QE ER

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type | Inspection
[7 empty] | Key | By
4.1 | Trench Excavation | - Excavate to achieve required depth to invert as per C111 to C113 - Trench width to allow for sufficient clearance to accomodate trench shield and effective compaction between springline of the pipe and trench wall or an adjacent pipe - Floor of trench to be even across width and length | - Allow 150mm for bedding - Allow for cover as per long section drawing (minimum cover of 750mm). | Photos, measurement checks | During Installation | Visual | C | SP QE CM
4.3 | Foundation | Scala tests on base of trench | Minimum of 3 blows per 100mm to achieve a CBR 5 or 100kPa Ground Bearing Pressure | Test results | During installation, per 20m | Visual, On site test | H | SP QE ER
4.2 | 40 Clean drain detail | Install undercut detail if soft ground conditions or groundwater is encountered. | - 200mm depth Clean 40 wrapped in Bidim A29 geotextile | Photos | During Installation | Visual | C & I | SP QE ER
4.4 | Install Pipe | Pipe installed to grade as per drawing C111-C113 and referencing Project Specification - Appendix D2 | - Pipe not damaged during installation - Pipe installed to grade within tolerances specification GP 3.1.8 | Photos, Grade check sheet, Survey of position for asbuilt | During installation | Visual, instrumental | C & I | SP QE ER
4.5 | Embedment zone | Embedment material shall be AP20 as approved by the Engineer (Refer section 3.3 of this ITP) | - Min 150mm bedding - 150mm overlay | Photos Site Check Measurements | During Installation | Visual, measurement check | C | SP QE
4.6 | Backfill and Compact | Backfill AP65 in 200mm (Materials to be layers of compacted material as approved bt the Engineer (Refer Section 3.4 of this ITP) - Compaction testing one test every two layers as required | 95% MDD in roads, paths, and pavements | Photos, Compaction test results | During Installation, compaction testing per 50m of pipeline or per straight section of pipeline at each alternate layer | Visual, On Site test | H | SP QE ER
4.7 | Materials compaction | Each Layer (200mm) compaction using plate compactor 8No back and forward passes | Compacted layer is 200mm | Photos, visual, measurement | 16No passes (8no x 2) | Visual, Photograph | V | SP QE ER
4.8 | Pavement reinstatement and surfacing | Place and compact M440 as approved by the Engineer (Refer Section 3.5 of this ITP) basecourse in preparation for 50mm asphalt | - Average 98% MDD in roads with no test lower than 95%. - Over cut trench 100mm from trench wall - Prep 50mm below staright edge | Photos, Compaction test results | During Installation, compaction testing per 50m of pipeline or per straight section of pipeline | Visual, On Site test | H | SP QE ER

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type | Inspection
[7 empty] | Key | By
5.1 | CCTV | CCTV inspection to confirm pipeline conforms with specification | Pipeline will fail is any of the following is visible: - pipe misalignment or deformation more than 5% of the pipe diameter - defects such as open joints, potruding laterals, cracked barrels, or similar | Test Records, CCTV footage | Every section of pipe completed | On-Site Test | H | SP QE CM ER
5.2 | Leak Testing | Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4 | Engineer Approval | Test Records | Every section of pipe installed | On-Site Test | H | SP QE CM ER
5.3 | Red pen markups | Complete mark up of any changes from supplied drawings | Installation complete | Original Drawings & Documentation | After completion of pipe section | Measure & Record | H | SP QE CM ER
5.4 | As-Built Survey | At project completion | Engineer approval | As-Built Drawings | Completion of Project | Submission of Documentation | R | ER
5.5
5.6
5.7
5.8
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: