## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | 561461-ITP-002 - Installation of SW Manhole | itp |  |  |  |  | 561461-ITP-002 - Installation of SW Manhole v1
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Manhole Delivery
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm Manhole is correct type & dimensions correct as per drawings and Specifications
label | Acceptance Criteria - Items are approved as per contract specification
label | ○ DCC approved
label | Verifying Document - Photos, delivery docket
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 3.2 - Set out & Locations
label | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
label | Acceptance Criteria - - Allignment set out matches drawing C111(rev1) or aggreed with the Engineer
label | Verifying Document - Survey marks, photos
label | Frequency - Prior to commencement of works
label | Inspection Type (Visual, other) - Survey
label | Inspection: Key - H
label | Inspection: By - SV, SP, QE, ER
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Backfill / Bedding Material
label | Inspection Point: Quality Control Activity - Approved Material, AP20 on site
label | Acceptance Criteria - As per Details on WSP drawing C121(rev1)
label | Verifying Document - Delivery dockets, photos
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 3.4 - Delivery of Corbel Reinforcing Bars
label | Inspection Point: Quality Control Activity - Insect for the correct quantity supplied, Correct Material & Dimensions
label | Acceptance Criteria - As detailed on Drawing C201 (Section 4 & Detail A)
label | Verifying Document - Delivery dockets, photos
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 3.5 - Delivery of HILTI RE-500 Chemical Anchor
label | Inspection Point: Quality Control Activity - Inspect Packaging and condition of product & application gun. Check if application gun is compatable with product
label | Acceptance Criteria - No damage and gun is correct for product
label | Verifying Document - Nil
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 3.6 - Manhole Lid & Sealant
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm Manhole Lid & Sealant is correct type & dimensions/quantities correct as per drawings and Specifications
label | Acceptance Criteria - Items are approved as per contract specification
label | ○ DCC approved
label | Verifying Document - Delivery docket
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 3.7 - Manhole Adjstment rings
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm Manhole is correct type & dimensions correct as per drawings and Specifications
label | Acceptance Criteria - Items are approved as per contract specification
label | ○ DCC approved
label | Verifying Document - Delivery docket
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 3.8 - Manhole Korum
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm Manhole is correct type & dimensions correct as per drawings and Specifications
label | Acceptance Criteria - Items are approved as per contract specification
label | ○ DCC approved
label | Verifying Document - Delivery docket
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP, QE
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
label | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C121(rev1)
label | ○ Trench width 1300mm to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
label | ○ Floor of trench to be even across width and length
label | Acceptance Criteria - Depth is correct using measurements from RL's provided by surveyer
label | Verifying Document - Photos, measurement checks
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
label | Inspection: By - SP, QE
checkpoint | 4.2 - Foundation
label | Inspection Point: Quality Control Activity - Scala test on base of trench
label | Acceptance Criteria - 100kPa Allowable Bearing Stress. 600mm maximum Foundation required. Ballast to be added if required subject to
label | Verifying Document - Test results & Engineer approval if below 100kPa
label | Frequency - At each Manhole Location
label | Inspection Type (Visual, other) - Visual, On site test
label | Inspection: Key - H
label | Inspection: By - SP, QE, ER
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.3 - Bedding - Primary
label | Inspection Point: Quality Control Activity - Bedding minimum 200mm compacted AP40
label | Acceptance Criteria - - Bedding to comply with WSP requirements
label | Verifying Document - Photo
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual, Measurement Check
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 4.4 - Bedding - Secondary
label | Inspection Point: Quality Control Activity - Bedding minimum 75mm compacted AP150
label | Acceptance Criteria - - Bedding to comply with WSP requirements
label | Verifying Document - Photo
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual, Measurement Check
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 4.5 - MH Installation
label | Inspection Point: Quality Control Activity - MHs to be installed true to the design level includung riser, sealing strip/lid and neck rings and Manhole Korum Ductile Iron cover.
label | Acceptance Criteria - -Final levels are in accordance with the C4300 or within tolerance and agreed with the Engineer
label | Verifying Document - Photos, As-built
label | Frequency - During installation
label | Inspection Type (Visual, other) - Survey
label | Inspection: Key - H
label | Inspection: By - SP, QE, ER
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.6 - Cutting of Manhole wall for pipe installation
label | Inspection Point: Quality Control Activity - Marking out of the Pipe entry & Exit positions
label | Acceptance Criteria - Pipe invert levels are correct as per long section drawings
label | Verifying Document - Photos & Measurement checks
label | Frequency - 2 per manhole (Inlet & Outlet)
label | Inspection Type (Visual, other) - Measurement check, Photos
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 4.7 - Installation of HD12 L Bar (hook)
label | Inspection Point: Quality Control Activity - Marking out of Bar locations as per drawing as agreed with the Engineer
label | Acceptance Criteria - Bars installed as per drawings ensuring a minimum of 50mm cover to all reinforcing
label | Verifying Document - Photos & Measurement checks
label | Frequency - As each Manhole Penetration
label | Inspection Type (Visual, other) - Measurement check, Photos
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 4.8 - Pipe starter install
label | Inspection Point: Quality Control Activity - Determine the correct required starter length. Confirm diameter is correct
label | Acceptance Criteria - Starter pipe is in correct position and is of suitable length so not to obstruct Corbel. Consider the length of the next pipe section (short)
label | Verifying Document - Drawings & Measurement checks
label | Frequency - 2 per manhole (Inlet & Outlet)
label | Inspection Type (Visual, other) - Measurement check, Photos
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 4.9 - Epoxy Mortar Install
label | Inspection Point: Quality Control Activity - Epoxy Mortar is installed in accordance with Product Specifications & drawing C201 (Detail A)
label | Acceptance Criteria - Epoxy Mortar is cured and provides a waterproof seal and is visually free of imperfections
label | Verifying Document - Product Data Sheet, Drawings
label | Frequency - 2 per manhole (Inlet & Outlet)
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 4.10 - Corbel Boxing
label | Inspection Point: Quality Control Activity - Construction of Boxing in preparation for casting
label | Acceptance Criteria - Boxing is constructed to the correct
label | Verifying Document - Drawings & Measurement checks
label | Frequency - 2 per manhole (Inlet & Outlet)
label | Inspection Type (Visual, other) - Measurement check, Photos
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 4.11 - Corbel Casting
label | Inspection Point: Quality Control Activity - Determine concrete quantity and confirm delivery.
label | ○ Vibrate as required to remove entrained air
label | Acceptance Criteria - All entrained air removed
label | Verifying Document - Supplier document certifying 30MPa
label | Frequency - 2 per manhole (Inlet & Outlet)
label | Inspection Type (Visual, other) - Visual, Supplier Documentation
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 4.12 - Benching
label | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 10MPa at 28 days.
label | ○ Benching shape to have smooth transitions at bends and junctions
label | Acceptance Criteria - - Benching built up & shaped to the drawings & specifications
label | Verifying Document - Photos
label | Frequency - During benching contruction
label | Inspection Type (Visual, other) - Visual, Test Results
label | Inspection: Key - H
label | Inspection: By - SP, QE, ER
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.13 - Backfill and Compact
label | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted AP65
label | ○ Compaction testing one test every two layers as required
label | Acceptance Criteria - - 95% MDD in roads, paths, and pavements
label | Verifying Document - Photos, Compaction test results
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual, On Site test
label | Inspection: Key - H
label | Inspection: By - SP, QE, ER
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.13 - Materials compaction
label | Inspection Point: Quality Control Activity - Each Layer (200mm) compaction using plate compactor/foot wacker 8No back and forward passes
label | Acceptance Criteria - Compacted layer is 200mm
label | Verifying Document - Photos, visual, measurement
label | Frequency - 16No passes (8no x 2)
label | Inspection Type (Visual, other) - Visual, Photograph
label | Inspection: Key - V
label | Inspection: By - SP, QE, ER
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Red pen markups
label | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
label | Acceptance Criteria - Installation complete
label | Verifying Document - Original Drawings & Documentation
label | Frequency - After installation of SWMH
label | Inspection Type (Visual, other) - Document
label | Inspection: Key - H
label | Inspection: By - SP, QE, ER
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - As-Built Survey
label | Inspection Point: Quality Control Activity - At project completion
label | Acceptance Criteria - Engineer approval
label | Verifying Document - As-Built Drawings
label | Frequency - Completion of Project
label | Inspection Type (Visual, other) - Submission of Documentation
label | Inspection: Key - R
label | Inspection: By - ER
checklist | 561461-ITP-001 - Concrete Stormwater | itp |  |  |  |  | 561461-ITP-001 - Concrete Stormwater v2
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
label | Acceptance Criteria - Pipes shall be DN600 Class 2 RCRRJ
label | ○ Items are approved as per contract specification
label | ○ DCC approved
label | Verifying Document - Photos, delivery docket, MDD results & Materials grading for backfill materials
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE
checkpoint | 3.2 - Set out
label | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
label | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
label | Verifying Document - Survey marks, photos
label | Frequency - Prior to commencement of works
label | Inspection Type (Visual, other) - Visual, Instrumental
label | Inspection: Key - H
label | Inspection: By - SV, SP, QE, PM, ER
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Embedment Zone Materials - AP20
label | Inspection Point: Quality Control Activity - Visual quality check AP20 is evenly graded granular material free of detritus
label | Acceptance Criteria - Material Approval by Quality Engineer
label | Verifying Document - Photograph
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Review & Approval
label | Inspection: Key - R
label | Inspection: By - QE
checkpoint | 3.4 - Backfill Material - AP65
label | Inspection Point: Quality Control Activity - Submission of Test Sheets for review
label | Acceptance Criteria - Material Approval by Engineer Rep
label | Verifying Document - Test Certification
label | Frequency - Once
label | Inspection Type (Visual, other) - Review & Approval
label | Inspection: Key - R
label | Inspection: By - QE, ER
checkpoint | 3.5 - Pavement Preparation Material - M440
label | Inspection Point: Quality Control Activity - Submission of Test Sheets for review
label | Acceptance Criteria - Material Approval by Engineer Rep
label | Verifying Document - Test Certification
label | Frequency - Once
label | Inspection Type (Visual, other) - Review & Approval
label | Inspection: Key - R
label | Inspection: By - QE, ER
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
label | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per C111 to C113
label | ○ Trench width to allow for sufficient clearance to accomodate trench shield and effective compaction between springline of the pipe and trench wall or an adjacent pipe
label | ○ Floor of trench to be even across width and length
label | Acceptance Criteria - Allow 150mm for bedding
label | ○ Allow for cover as per long section drawing (minimum cover of 750mm).
label | Verifying Document - Photos, measurement checks
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP, QE, CM
checkpoint | 4.3 - Foundation
label | Inspection Point: Quality Control Activity - Scala tests on base of trench
label | Acceptance Criteria - Minimum of 3 blows per 100mm to achieve a CBR 5 or 100kPa Ground Bearing Pressure
label | Verifying Document - Test results
label | Frequency - During installation, per 20m
label | Inspection Type (Visual, other) - Visual, On site test
label | Inspection: Key - H
label | Inspection: By - SP, QE, ER
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - 40 Clean drain detail
label | Inspection Point: Quality Control Activity - Install undercut detail if soft ground conditions or groundwater is encountered.
label | Acceptance Criteria - - 200mm depth Clean 40 wrapped in Bidim A29 geotextile
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C & I
label | Inspection: By - SP, QE, ER
checkpoint | 4.4 - Install Pipe
label | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C111-C113 and referencing Project Specification - Appendix D2
label | Acceptance Criteria - Pipe not damaged during installation
label | ○ Pipe installed to grade within tolerances specification GP 3.1.8
label | Verifying Document - Photos, Grade check sheet, Survey of position for asbuilt
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual, instrumental
label | Inspection: Key - C & I
label | Inspection: By - SP, QE, ER
checkpoint | 4.5 - Embedment zone
label | Inspection Point: Quality Control Activity - Embedment material shall be AP20 as approved by the Engineer (Refer section 3.3 of this ITP)
label | Acceptance Criteria - Min 150mm bedding
label | ○ 150mm overlay
label | Verifying Document - Photos, Site Check Measurements
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual, measurement check
label | Inspection: Key - C
label | Inspection: By - SP, QE
checkpoint | 4.6 - Backfill and Compact
label | Inspection Point: Quality Control Activity - Backfill AP65 in 200mm (Materials to be layers of compacted material as approved bt the Engineer (Refer Section 3.4 of this ITP)
label | ○ Compaction testing one test every two layers as required
label | Acceptance Criteria - 95% MDD in roads, paths, and pavements
label | Verifying Document - Photos, Compaction test results
label | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline at each alternate layer
label | Inspection Type (Visual, other) - Visual, On Site test
label | Inspection: Key - H
label | Inspection: By - SP, QE, ER
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.7 - Materials compaction
label | Inspection Point: Quality Control Activity - Each Layer (200mm) compaction using plate compactor 8No back and forward passes
label | Acceptance Criteria - Compacted layer is 200mm
label | Verifying Document - Photos, visual, measurement
label | Frequency - 16No passes (8no x 2)
label | Inspection Type (Visual, other) - Visual, Photograph
label | Inspection: Key - V
label | Inspection: By - SP, QE, ER
checkpoint | 4.8 - Pavement reinstatement and surfacing
label | Inspection Point: Quality Control Activity - Place and compact M440 as approved by the Engineer (Refer Section 3.5 of this ITP) basecourse in preparation for 50mm asphalt
label | Acceptance Criteria - Average 98% MDD in roads with no test lower than 95%.
label | ○ Over cut trench 100mm from trench wall
label | ○ Prep 50mm below staright edge
label | Verifying Document - Photos, Compaction test results
label | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
label | Inspection Type (Visual, other) - Visual, On Site test
label | Inspection: Key - H
label | Inspection: By - SP, QE, ER
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - CCTV
label | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
label | Acceptance Criteria - Pipeline will fail is any of the following is visible:
label | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
label | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
label | Verifying Document - Test Records, CCTV footage
label | Frequency - Every section of pipe completed
label | Inspection Type (Visual, other) - On-Site Test
label | Inspection: Key - H
label | Inspection: By - SP, QE, CM, ER
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Leak Testing
label | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
label | Acceptance Criteria - Engineer Approval
label | Verifying Document - Test Records
label | Frequency - Every section of pipe installed
label | Inspection Type (Visual, other) - On-Site Test
label | Inspection: Key - H
label | Inspection: By - SP, QE, CM, ER
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.3 - Red pen markups
label | Inspection Point: Quality Control Activity - Complete mark up of any changes from supplied drawings
label | Acceptance Criteria - Installation complete
label | Verifying Document - Original Drawings & Documentation
label | Frequency - After completion of pipe section
label | Inspection Type (Visual, other) - Measure & Record
label | Inspection: Key - H
label | Inspection: By - SP, QE, CM, ER
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.4 - As-Built Survey
label | Inspection Point: Quality Control Activity - At project completion
label | Acceptance Criteria - Engineer approval
label | Verifying Document - As-Built Drawings
label | Frequency - Completion of Project
label | Inspection Type (Visual, other) - Submission of Documentation
label | Inspection: Key - R
label | Inspection: By - ER