## Table 1
Project: New Footscray hospital Project No. V0-175
Inspection & Test Plan No. |  |  |  | Revision No.
Task: Pile Caps |  |  |  | Project Manager: Timothy Gannon
Location: New Footscray Hospital |  |  |  | Date:
Item | Operational Activities | Acceptance Criteria | Check Box |  | Inspection & Sign |  |  | Comments/ Attachment
[5 empty] | Delta | Multiplex | DoT
1 | Pile Cap Documentation &Setout
1.1 | Documentation |  Drawing & Revision Number:  | ☒ Yes ☐ No
1.2 | Survey Set out – check position |  Binding RL:  Top of Footing RL: | ☒ Yes ☐ No
1.3 | Waterproofing membrane installed by other |  | ☐ Yes ☒ N/A
2 | Pile Cap Pre-Pour inspection
2.1 | Pile Reo Length and Referenced |  Pile Length:  Top of Steel: | ☒ Yes ☐ No
2.2 | Pile Cap reinforcement check and accurate to specifications |  Bottom Reo:  Top Reo:  Column Start Bar:  Cover: | ☒ Yes ☐ No |  |  |  |  | Photos attached
2.3 | Sign offs Required |  | ☒ Yes ☐ No |  |  |  |  | Hold Point – Ensure Engineer/Building surveyor/Department of Transport sign offs are completed before pour- Attached report as applicable.
2.4 | Commencement of Pour |  Delta Group representative signed  Multiplex representative signed | ☒ Yes ☐ No |  |  |  |  | Hold Point - Pass once all pre-pour checks have been completed and ready to pour concrete
3 | Pile Cap Concrete Placement
3.1 | Date of Pour Entered |  Date: | ☒ Yes ☐ No
3.2 | Concrete Delivery Docket |  Docket Number: | ☒ Yes ☐ No |  |  |  |  | Concrete Docket attached
3.3 | Concrete Details Complete |  Concrete Grade: VR 450/50 | ☒ Yes ☐ No |  |  |  |  | Concrete Batch mix strength and slump test – refer Mix Design
3.4 | Mud Map attached to indicate date and location of pour |  | ☒ Yes ☐ No |  |  |  |  | Attached Mud Map
4 | Pile cap post pour-sign off/ Handover
4.1 | Concrete testing |  Slump at least one truck  One set of 3 cylinders per 50m3 poured. Minimum compressive strength requirements:  1@ 3 days: 23MPA  1@ 7 days: 35MPA  1@28 days: 50MPA  Maximum VPV values at 28days provided if required | ☒ Yes ☐ No |  |  |  |  | Attached Concrete compressive report Attached as built drawing
4.2 | Post Pour Signoffs |  Delta Group representative signed  Multiplex representative signed | ☒ Yes ☐ No