## Table 1
Project: New Footscray hospital Project No. V0-175
Inspection & Test Plan No. |  |  |  | Revision No.
Task: Foundation Pile |  |  |  | Project Manager: Timothy Gannon
Location: New Footscray Hospital |  |  |  | Date:
Item | Operational Activities | Acceptance Criteria | Check Box |  | Inspection & Sign |  |  | Comments/ Attachment
[5 empty] | Delta | Multiplex | DoT
1 | Foundation Pile Documentation &Setout
1.1 | Documentation |  Drawing & Revision Number:  | ☒ Yes ☐ No
1.2 | Survey Set out – check position |  Binding RL:  Top of Footing RL: | ☒ Yes ☐ No
2 | Foundation Pile Information
2.1 | Pile Detail |  Pile Diameter:  Top of Steel RL:  Length of Pile (m):  Top of Pile (RL):  Pile Socket Length: | ☒ Yes ☐ No
2.2 | Pile Hole Inspection |  Check for excessive water in hole | ☒ Yes ☐ No
2.3 | Pile Reinforcement |  Main Bars:  Ligs:  Cage Length: | ☒ Yes ☐ No |  |  |  |  | Photos attached
2.4 | Sign offs Required |  | ☒ Yes ☐ No |  |  |  |  | Hold Point – Ensure Engineer/Building surveyor/Department of Transport sign offs are completed before pour- Attached report as applicable.
2.5 | Commencement of Pour |  Delta Group representative signed  Multiplex representative signed | ☒ Yes ☐ No |  |  |  |  | Hold Point - Pass once all pre-pour checks have been completed and ready to pour concrete
3 | Foundation Pile Concrete Placement
3.1 | Date of Pour Entered |  Date: | ☒ Yes ☐ No
3.2 | Concrete Delivery Docket |  Docket Number: | ☒ Yes ☐ No |  |  |  |  | Concrete Docket attached
3.3 | Concrete Details Complete |  Concrete Grade:  Cover: 75mm | ☒ Yes ☐ No |  |  |  |  | Concrete Batch mix strength and slump test – refer Mix Design
3.4 | Mud Map attached to indicate date and location of pour |  | ☒ Yes ☐ No |  |  |  |  | Attached Mud Map
4 | Foundation Pile post pour-sign off/ Handover
4.1 | Concrete testing |  Slump at least one truck  One set of 3 cylinders per 50m3 poured.  28 Day Concrete Compressive Strength (MPa) | ☒ Yes ☐ No |  |  |  |  | Attached Concrete compressive report Attached as built drawing
4.2 | Post Pour Signoffs |  Delta Group representative signed.  Multiplex representative signed. | ☒ Yes ☐ No