## Structure
Tier 1 | Tier 2 | Tier 3 | Tier 4 | Tier 5 | Tier6 | Instruction to CONQA | Checklist Name
Building Services
Building Services by Area
|  | SP2A - L2 Lounge & Fire Egress Stairs |  |  |  | prepopulate | Above Ground Stormwater Installation
[6 empty] | prepopulate | Above Ground Sewer Drain
[6 empty] | prepopulate | Pipework Test Sheet
SP3 - Power Centre 69 (PC69)
[6 empty] | prepopulate | Above Ground Stormwater Installation
[6 empty] | prepopulate | Pipework Test Sheet

## Resources
type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist | Above Ground Stormwater Installation | [5 empty] | Above Ground Stormwater Installation
checkpoint | Clean out points for pipes accessible and correctly located
checkpoint | Clean out points intersect drain at angle no greater than 45°
checkpoint | Clean out points are terminated with screw cap legibly marked 'SW'
checkpoint | Pipes and fittings have been cleaned internally prior to installation
checkpoint | Appropriately jointed (where applicable)
checkpoint | Seismic bracing installed
checkpoint | Appropriate access to above ground inspection openings available
checkpoint | Minimum gradient of stormwater drain achieved
checkpoint | Exact location and details noted on as-builts
checkpoint | Drains are watertight
checkpoint | Acoustic insulation installed
checkpoint | Report sent through to client
checklist | Pipework Test Sheet | [5 empty] | Pipework Test Sheet
checkpoint | Labels installed to pipework
checkpoint | Penetrations sealed through floor
checkpoint | Schematic / plan drawing attached
checkpoint | Test no 1
textbox | Duration of test
textbox | Flood
checkpoint | Test no 2
textbox | Duration of test
textbox | Flood
checkpoint | Test no 3
textbox | Duration of test
textbox | Flood
checkpoint | Test no 4
textbox | Duration of test
textbox | Flood
checklist | No QA in this room | [5 empty] | No QA in this room
checkpoint | This room does not contain any QA
note | Pass this checkpoint when the information below has been completed
textbox | Reason this room does not require QA
textbox | If QA for this room is captured under a different area, please specify the Area / Room number
checklist | Second Fix QA | [5 empty] | Second Fix QA
section | Equipment
checkpoint | WHB
checkpoint | WC
checkpoint | SHR
checkpoint | Water meter
checkpoint | Kitchen sink
checkpoint | Hose tap
checkpoint | Hotwater cylinder
section | Wash Hand Basin
checkpoint | WHB secured to wall
checkpoint | WHB Sealed to wall
checkpoint | Waste installed
checkpoint | Tapware installed
section | WC
checkpoint | Floor Vinyl installed
checkpoint | WC installed and bolted down
checkpoint | Waste connected
checkpoint | FW connected
checkpoint | Seat tightened
section | Kitchen Sink
checkpoint | Sink insert in benchtop
checkpoint | Waste installed
checkpoint | Tapware installed
checkpoint | Water connected
section | Hosetap
checkpoint | Installed in correct location
checkpoint | Vacuum breaker installed
section | Hot water cylinder
checkpoint | Correct size HWC and pump installed
checkpoint | Safe tray installed and piped to drain
checkpoint | Thermostatic pressure relief valve installed and piped to drain
checkpoint | Cold water available
checkpoint | Water meter installed.
checkpoint | Report sent through to client
checklist | First Fix QA Checklist | [5 empty] | First Fix QA Checklist
checkpoint | Correct set out for all fixtures
checkpoint | Checked for cross overs
checkpoint | All pipe penetrations siliconed
checkpoint | All pipe penetrations fire rated
checkpoint | All pipes clipped securely
checkpoint | All pipework pressure tested
checkpoint | All waste pipes flood tested
checkpoint | All in-wall cisterns installed
checkpoint | All in-wall flushing devices installed
checkpoint | Fixing for all fixtures
checkpoint | Hot water supply lagged
checkpoint | WHBs level and securely screwed
checkpoint | Correct set out for disabled fixtures
checkpoint | All floor flanges ground / glued in
checkpoint | Report sent through to client
checklist | Above Ground Sewer Drain | [5 empty] | Above Ground Sewer Drain
checkpoint | Clean out points for pipes accessible and correctly located
checkpoint | Clean out points intersect drain at angle no greater than 45°
checkpoint | Clean out points are terminated with screw cap legibly marked 'SW'
checkpoint | Pipes and fittings have been cleaned internally prior to installation
checkpoint | Pipes and fittings in drains are continuously supported by embedment
checkpoint | Appropriately jointed (where applicable)
checkpoint | Seismic bracing installed
checkpoint | Appropriate access to above ground inspection openings available
checkpoint | Minimum gradient of stormwater drain achieved
checkpoint | Exact location and details noted on as-builts
checkpoint | Drains are watertight
checkpoint | Report sent through to client