## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | QA - Bulk Tank |  |  |  |  | Yes | QA - Bulk Tank | 1857e74d-58ff-4ac7-9279-113b0ad5c106
checkpoint-status |  |  | checkpoint | Photo of item
checkpoint-status |  |  | checkpoint | Size and dimensions are manufactured according to approved shop drawing
checkpoint-status |  |  | checkpoint | No visible damage
checkpoint-status |  |  | checkpoint | Bulk Tank clean and in good condition
checkpoint-status |  |  | checkpoint | Secured to Plinth/Platform
checkpoint-status |  |  | checkpoint | Hold down bolts are present
checkpoint-status |  |  | checkpoint | All tank fittings are secured correctly including gaskets and fastenings
checkpoint-status |  |  | checkpoint | HSNO stickers applied
checkpoint-status |  |  | checkpoint | Directional flow stickers on the pipework (Above ground)
checkpoint-status |  |  | checkpoint | Equipment tags for all items
checkpoint-status |  |  | checkpoint | Check Tank Ladder provides adequate access
checklist-flat |  |  | checklist | QA - Bulk Tank Install |  |  |  |  | Yes | QA - Bulk Tank Install | 3b5eea77-f926-44e6-bd95-44faa9c80999
checkpoint-status |  |  | checkpoint | Mechanical overfill protection installed correctly
checkpoint-status |  |  | checkpoint | Anti Syphon valves correctly installed
checkpoint-status |  |  | checkpoint | Bulk tank level transmitters installed, cable installed and tested
checkpoint-status |  |  | checkpoint | Bulk tank leak detectors, properly installed, cable installed and tested
checkpoint-status |  |  | checkpoint | Bulk tank vents installed as per the drawing
holdpoint |  |  | signoff | Request signoff
checklist-sectioned |  |  | checklist | QA - Conduit and Durapipe Laying |  |  |  |  | Yes | QA - Conduit and Durapipe Laying | 51e558c2-7018-41cd-9d9d-410d44c4ca9b
checkpoint-group |  |  | section | Pipe Laying
checkpoint-status |  |  | checkpoint | Pipes were laid as per approved shop drawings
checkpoint-status |  |  | checkpoint | Pipe grades are in accordance with the drawings
checkpoint-status |  |  | checkpoint | Pipe materials comply with specifications
checkpoint-status |  |  | checkpoint | Trench excavation to line level and grade
checkpoint-status |  |  | checkpoint | Correct bedding provided
checkpoint-status |  |  | checkpoint | Jointing system as per specifications and manufacturers recommendation
checkpoint-status |  |  | checkpoint | Anchor/ thrust block provided (if any)
checkpoint-status |  |  | checkpoint | Pipes flushed and cleaned
checkpoint-status |  |  | checkpoint | Pipes tested in accordance with specifications
checkpoint-status |  |  | checkpoint | Directional flow stickers on the pipework (Above ground)
checkpoint-status |  |  | checkpoint | Equipment tags for all items
holdpoint |  |  | signoff | Inspected by local authority (Council)
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Subgrade tested and passed
button | c42db162-6b2a-5d0e-bc59-3e612f6b34b4 |  | button | Any undercutting required? | Yes, No
text | d4d3cf3a-ebce-52da-ac40-3eaacb3da132 |  | textbox | Undercutting/other remedials as instructed by Jacobs (if required)
checkpoint-status |  |  | checkpoint | Bedding material installed to correct level
checkpoint-status |  |  | checkpoint | Side support material installed to the correct level
checkpoint-status |  |  | checkpoint | Haunching?
checkpoint-status |  |  | checkpoint | 25Mpa concrete corbel around inlet and outlet pipes
checkpoint-status |  |  | checkpoint | Voids filled with epoxy mortar or concrete
checkpoint-status |  |  | checkpoint | Pipe overlay to correct level
checkpoint-status |  |  | checkpoint | Backfill to the underside of pavement and compacted
checkpoint-status |  |  | checkpoint | Service placed at design RL?
checkpoint-status |  |  | checkpoint | Invert levels checked and correct
checkpoint-status |  |  | checkpoint | Trades QA completed, received & reviewed
checkpoint-status |  |  | checkpoint | General progress photos recorded
holdpoint |  |  | signoff | Request signoff
checklist-flat |  |  | checklist | QA - Fuel System Installation Checklist: Admin Tank |  |  |  |  | Yes | QA - Fuel System Installation Checklist: Admin Tank | 6e3afe27-71dc-4cae-9c1e-577ccfb7fe37
checkpoint-status |  |  | checkpoint | Admin Tank clean and in good condition
checkpoint-status |  |  | checkpoint | Admin tank connections are as per the drawing
checkpoint-status |  |  | checkpoint | All mounting, fixtures and equipment are fit for purpose
checkpoint-status |  |  | checkpoint | Pipework pressure tested with no leaks prior to getting fuel through
checkpoint-status |  |  | checkpoint | All valves and fittings are in good condition
checkpoint-status |  |  | checkpoint | Admin Tank Solenoid Valve, installed as per the drawing, cable installed and tested
checkpoint-status |  |  | checkpoint | Admin tank local level indicator installed
checkpoint-status |  |  | checkpoint | Admin tank level sensor installed, and cable installed and tested
checkpoint-status |  |  | checkpoint | Valves as per the drawing
checkpoint-status |  |  | checkpoint | Fuel flow switch properly installed
checkpoint-status |  |  | checkpoint | Fusible link over the generator and shut off valve, properly installed
checkpoint-status |  |  | checkpoint | Admin tank leak detector properly installed, cable installed and tested
checkpoint-status |  |  | checkpoint | Admin tank E-Stop properly installed, cable installed and tested
checkpoint-status |  |  | checkpoint | HSNO stickers applied
checkpoint-status |  |  | checkpoint | Directional flow stickers on the pipework (Above ground)
checkpoint-status |  |  | checkpoint | Equipment tags for all items
checklist-flat |  |  | checklist | QA - Fuel System Installation Checklist: Common Equipment |  |  |  |  | Yes | QA - Fuel System Installation Checklist: Common Equipment | 7047eee9-c469-43e4-8131-baeb85d395ac
checkpoint-status |  |  | checkpoint | Fuel pump No 1, clean and in good condition, cable installed and tested
checkpoint-status |  |  | checkpoint | Fuel pump No 2, clean and in good condition, cable installed and tested
checkpoint-status |  |  | checkpoint | Fuel pump No 3, clean and in good condition, cable installed and tested
checkpoint-status |  |  | checkpoint | Fuel pump No 4, clean and in good condition, cable installed and tested
checkpoint-status |  |  | checkpoint | Fuel pump No 5, clean and in good condition, cable installed and tested
checkpoint-status |  |  | checkpoint | Fuel pump No 6, clean and in good condition, cable installed and tested
checkpoint-status |  |  | checkpoint | Fuel pump No 7, clean and in good condition, cable installed and tested
checkpoint-status |  |  | checkpoint | Fuel pump No 8, clean and in good condition, cable installed and tested
checkpoint-status |  |  | checkpoint | Fuel polishing pump, clean and in good condition, cable installed and tested
checkpoint-status |  |  | checkpoint | All mounting, fixtures and equipment are fit for purpose
checkpoint-status |  |  | checkpoint | Pipework to the bulk tank pressure tested with no leaks prior to getting fuel through
checkpoint-status |  |  | checkpoint | All valves and fittings are installed, in good condition and as per the Fuel PID
checkpoint-status |  |  | checkpoint | Fuel filter / water separator, properly installed
checkpoint-status |  |  | checkpoint | Flow switches for Pump 1, 2,3,4,5,6,7,8 and polishing pump properly installed, cable installed and tested
checkpoint-status |  |  | checkpoint | Motor Control Centre (MCC) properly installed
checkpoint-status |  |  | checkpoint | Fuel fill box installed and fixed properly
checkpoint-status |  |  | checkpoint | Fuel fill control panel installed inside the fill box, cables installed and tested
checkpoint-status |  |  | checkpoint | Directional flow stickers on the pipework (Above ground)
checkpoint-status |  |  | checkpoint | Equipment tags for all items
checklist-flat |  |  | checklist | QA - Fuel System Function Checklist: Bulk Tanks |  |  |  |  | Yes | QA - Fuel System Function Checklist: Bulk Tanks | 93693667-6cf1-4c94-9c61-336126fc4621
checkpoint-status |  |  | checkpoint | Check the manual operation of the fuel pumps.
checkpoint-status |  |  | checkpoint | Fill the Bulk tank and check the fuel level reading of the level indicator with the dip stick
checkpoint-status |  |  | checkpoint | Check the pump stops, once the fuel level reaches 90%
checkpoint-status |  |  | checkpoint | Force the pump operation till the level reaches 95%, check the Hi-Level alarm is triggered at MCC
checkpoint-status |  |  | checkpoint | Force the pump operation and check the return flow into the bulk tank, the return flow should be greater than the fuel
checkpoint-status |  |  | checkpoint | supply to the tank. Do necessary adjustments if required.
checkpoint-status |  |  | checkpoint | Drain the tank and check the fuel pump starts at 50%.
checkpoint-status |  |  | checkpoint | Stop the pump manually and keep draining the tank, check the low level alarm is triggered at 40% at MCC
checkpoint-status |  |  | checkpoint | Keep draining the tank, check the Low-low level alarm is triggered at 10% and at MCC
checkpoint-status |  |  | checkpoint | Check the Solenoid valve operates correctly and the indicator on the MCC HMI is ON when the solenoid is open.
checkpoint-status |  |  | checkpoint | While the pump is running, press the E-Stop and check the pump stops
checkpoint-status |  |  | checkpoint | Simulate the Admin tank leak detector and check the alarm is raised at MCC
checklist-flat |  |  | checklist | QA - Fuel System Function Checklist: Common Equipment |  |  |  |  | Yes | QA - Fuel System Function Checklist: Common Equipment | 9624c96d-bb68-46ed-a3dd-7faf3cc908aa
checkpoint-status |  |  | checkpoint | Compare the level indicator readings of the fuel fill control panel (FFCP) with the bulk tank dip stick and do necessary adjustments in the level indicator setup to match with the actual reading
checkpoint-status |  |  | checkpoint | Simulate the Hi-Level alarm of the bulk tank and check the FFCP buzzer is triggered
checkpoint-status |  |  | checkpoint | Compare the level indicator readings of the Main fuel control panel with the FFCP and do necessary adjustments in the level indicator setup to match with the actual reading
checkpoint-status |  |  | checkpoint | Simulate the low level of the bulk tank and check the signal is alarm is triggered at the MCC
checkpoint-status |  |  | checkpoint | Simulate the bulk tank leak detector and check the alarm is triggered at MCC
checkpoint-status |  |  | checkpoint | Check the fuel polishing pump operation #1
checkpoint-status |  |  | checkpoint | Check the fuel polishing pump operation #2
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #1 Flow meter fault and check the alarm is triggered at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #2 Flow meter fault and check the alarm is triggered at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #3 Flow meter fault and check the alarm is triggered at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #4 Flow meter fault and check the alarm is triggered at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #5 Flow meter fault and check the alarm is triggered at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #6 Flow meter fault and check the alarm is triggered at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #7 Flow meter fault and check the alarm is triggered at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #8 Flow meter fault and check the alarm is triggered at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel polishing Flow meter fault and check the alarm is triggered at MFCP
checkpoint-status |  |  | checkpoint | Simulate fuel water separator detector and check the alarm is triggered at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #1 fault and check the alarm is raised at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #2 fault and check the alarm is raised at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #3 fault and check the alarm is raised at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #4 fault and check the alarm is raised at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #5 fault and check the alarm is raised at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #6 fault and check the alarm is raised at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #7 fault and check the alarm is raised at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel pump #8 fault and check the alarm is raised at MCC
checkpoint-status |  |  | checkpoint | Simulate the fuel Polishing pump fault and check the alarm is raised at MCC
checklist-flat |  |  | checklist | QA - Fuel System Installation Checklist: Bulk Tanks |  |  |  |  | Yes | QA - Fuel System Installation Checklist: Bulk Tanks | 99d6e668-62a3-4e7d-88bc-581c39971bae
checkpoint-status |  |  | checkpoint | Bulk tank connections are as per the drawing
checkpoint-status |  |  | checkpoint | All mounting, fixtures and equipment are fit for purpose
checkpoint-status |  |  | checkpoint | Pipework pressure tested with no leaks prior to getting fuel through
checkpoint-status |  |  | checkpoint | All valves and fittings are in good condition
checkpoint-status |  |  | checkpoint | Bulk Tank Solenoid Valve, installed as per the drawing, cable installed and tested
checkpoint-status |  |  | checkpoint | Bulk tank local level indicator installed
checkpoint-status |  |  | checkpoint | Bulk tank level sensor installed, and cable installed and tested
checkpoint-status |  |  | checkpoint | Valves as per the drawing
checkpoint-status |  |  | checkpoint | Fuel switch meter properly installed
checkpoint-status |  |  | checkpoint | Fusible link over the generator and shut off valve, properly installed
checkpoint-status |  |  | checkpoint | Bulk tank leak detector properly installed, cable installed and tested
checkpoint-status |  |  | checkpoint | Bulk tank E-Stop properly installed, cable installed and tested
checklist-flat |  |  | checklist | QA - Interface Checklist: With MCC |  |  |  |  | Yes | QA - Interface Checklist: With MCC | c8f2a191-c813-47fb-8b58-5eac5238cf14
checkpoint-status |  |  | checkpoint | Bulk tank fuel content
checkpoint-status |  |  | checkpoint | Bulk tank high level alarm
checkpoint-status |  |  | checkpoint | Bulk tank low level alarm
checkpoint-status |  |  | checkpoint | Day tank H high-high level alarm
checkpoint-status |  |  | checkpoint | Day tank H low level alarm
checkpoint-status |  |  | checkpoint | Day tank H low-low level alarm
checkpoint-status |  |  | checkpoint | Day tank S high-high level alarm
checkpoint-status |  |  | checkpoint | Day tank S low level alarm
checkpoint-status |  |  | checkpoint | Day tank S low-low level alarm
checkpoint-status |  |  | checkpoint | Fuel pump #1 fault
checkpoint-status |  |  | checkpoint | Fuel pump #2 fault
checkpoint-status |  |  | checkpoint | Fuel polishing pump fault
checkpoint-status |  |  | checkpoint | Day tank fibre connection
checkpoint-status |  |  | checkpoint | Day tank fibre connection
checkpoint-status |  |  | checkpoint | Equipment tags for all items
checklist-flat |  |  | checklist | QA - Fuel System Function Checklist: Admin Tank |  |  |  |  | Yes | QA - Fuel System Function Checklist: Admin Tank | f9d56519-2b6b-410f-b6b5-a0fbd416e954
checkpoint-status |  |  | checkpoint | Check the manual operation of the fuel pumps.
checkpoint-status |  |  | checkpoint | Fill the Admin tank and check the fuel level reading of the level indicator with the dip stick
checkpoint-status |  |  | checkpoint | Check the pump stops, once the fuel level reaches 90%
checkpoint-status |  |  | checkpoint | Force the pump operation till the level reaches 95%, check the Hi-Level alarm is triggered at MCC
checkpoint-status |  |  | checkpoint | Force the pump operation and check the return flow into the bulk tank, the return flow should be greater than the fuel
checkpoint-status |  |  | checkpoint | supply to the tank. Do necessary adjustments if required.
checkpoint-status |  |  | checkpoint | Drain the tank and check the fuel pump starts at 50%.
checkpoint-status |  |  | checkpoint | Stop the pump manually and keep draining the tank, check the low level alarm is triggered at 40% at MCC
checkpoint-status |  |  | checkpoint | Keep draining the tank, check the Low-low level alarm is triggered at 10% and at MCC
checkpoint-status |  |  | checkpoint | Check the Solenoid valve operates correctly and the indicator on the MCC HMI is ON when the solenoid is open.
checkpoint-status |  |  | checkpoint | While the pump is running, press the E-Stop and check the pump stops
checkpoint-status |  |  | checkpoint | Simulate the day tank leak detector and check the alarm is raised at MCC