## Master List Templates
Id | Type | Name | Values | Prompting Name
561008bb-58d2-48f6-bd38-674610c2eb61 | checklist | Add Concrete Pour Record |  | Load No.
c5ccbbbb-305b-4d59-b2a8-a2529972fe8d | section | Details
e5b2b6c7-fb17-4b0c-875a-19f20460fc2c | checkpoint | Details
d0f39a05-355d-5237-ac26-3dacbad4a401 | textbox | Docket No
04145c0b-7fe4-53ed-9c42-24e161783c74 | textbox | Time Batched
2780b034-47cf-57e6-a289-34f1395ee555 | textbox | Arrived on site
68785430-9a4f-5de5-8eac-8f7ec1be1638 | textbox | Dispatch Commenced
42b65e86-ca78-5907-9eee-970e854e40e8 | textbox | Completed
0df7555b-8dfa-524a-b82c-7068f6c709ba | textbox | Concrete Volume: Vol
82c05a1b-cd01-5cfe-97fa-cad0dedf9eb2 | textbox | Concrete Volume: Cum. Vol
0e983d07-bcf9-5fce-a248-9a3448207bcc | textbox | Initial Slump (mm)
5a5d397c-f34f-59e2-944d-16b1dff57f54 | textbox | Concrete Temp (Degrees C)
62a2c26b-df38-55d3-a8d9-de9bec659c55 | textbox | Water added on Site: Qty (L)
c6437bc2-1f8b-58ca-bb01-c1b7643f1b44 | textbox | Water added on Site: Final Slump (mm)
9ec7919a-4aeb-5134-a0b4-ddf5187c2102 | textbox | Ambient Temperature (Degrees C)
29cbd7d3-c9f2-55cc-a516-04f4e1479193 | textbox | No./ Days of Cylinder Taken
17cf5b4e-2f18-553a-bfe0-2aeafe338588 | textbox | Remarks
e6cf256a-8749-409c-96e6-08884942cf3f | checklist | General QA Checklist |  | General QA Checklist
af8bde2f-abf6-4229-b3f5-8ba8aef22176 | section | Details
753a5922-ac4f-4ace-a07f-db7ee4542692 | checkpoint-no-value | QA - Title & Date
64b537b7-5f9e-49de-a91b-4a89fcb44d30 | checkpoint | QA - Drawings or markups uploaded
7d83c687-eec4-4276-9700-2cee430d92f9 | checkpoint | QA - Survey or asbuilt uploaded
d4984f70-ff9c-4b10-bb7f-72d6c90f6a6f | checkpoint | QA - Supporting photograph(s) uploaded
d57baf63-3f69-41b7-970e-099c473fa974 | checklist | Lot Checks | itp | Lot
81b6d5a2-04e6-488a-8389-23b47616dcb6 | section | Section 1: Preliminaries & Permits
21e42e79-ebf9-4a61-bc6e-048f3f84a20c | checkpoint | 1.1 - Collect and verify information (Site boundary, utilities, survey map, design drawings)
517ea329-99f7-5146-a7f8-c92daa9c1fe0 | note | Responsibility - SE/PE
160f9ef5-41ed-5eb1-9098-5ffc605ae160 | note | Specification Reference - WBS-SS-CI-SPC-0006
da211c9a-0793-5138-90e1-433cb41258ce | note | Conformance Criteria Summary - Results included in work pack
0c9bd694-eea8-5e54-9736-c6c9342b7cc5 | note | Method - R
cb926d55-afe2-5620-b8b4-795b2928b97b | note | Frequency - PW
dbc1dcde-d837-5ea4-8960-bddb77539d76 | note | Hold/Witness Point Requirements: ROBAR - V
70e19a14-9c94-5f9a-bf8d-a0e6426c1360 | note | Hold/Witness Point Requirements: SEPD - NA
63312388-8d5d-588c-9d80-43f9dd25d2e3 | note | Hold/Witness Point Requirements: Client - NA
c2f3c05c-8489-52f0-abfa-3f1e7ee5f9f9 | note | Records or Checklist Document Number - IFC Drawings
26a56964-cefd-49e6-b86a-99b899ebad17 | checkpoint | 1.2 - Permit approval (GDA/GDP)
181fbc36-0c87-5125-b776-d46f1fbfa249 | note | Responsibility - SE/PE
c384d9c2-95c8-5619-b80c-433fa963586a | note | Specification Reference - WBS-SS-CI-SPC-0006
e9046fd9-fb2f-5fb1-8b58-1bdaef79dc34 | note | Conformance Criteria Summary - Approved excavation permit (GDP) prior to commencing works
f8891bf4-4e40-5294-b700-8663dfe2511a | note | Method - R
41ec940f-bc63-5b16-b09e-0d84f531f61a | note | Frequency - PW
a2aedd50-b396-596a-a9ac-290a678e8c8c | note | Hold/Witness Point Requirements: ROBAR - HP
9d26b4f7-a0ee-5a74-a299-e8728060e637 | note | Hold/Witness Point Requirements: SEPD - HP
0a8dac73-f512-5156-a30d-00390494ecbf | note | Hold/Witness Point Requirements: Client - NA
4252bcd5-9765-5a62-a33d-cb2164e31524 | note | Records or Checklist Document Number - RR-SEPD-CI-SOW-002-01
fe2d3215-616d-4c4e-8e97-b61e1c747704 | signoff | HOLD POINT
f585a2e6-bcdb-49de-8e67-3579fa5c7292 | checkpoint | 1.3 - Site set-out
fcf9d8df-3bfb-542d-a651-831cb0047dea | note | Responsibility - SE/PE
a6305e80-7e9e-5a3a-9ff4-4b4f43cef341 | note | Specification Reference - WBS-SS-CI-SPC-0006
1a27382a-4567-5502-97c7-4873db123967 | note | Conformance Criteria Summary - Verify levels, site boundaries, and physical bounds per IFC drawings
b6211579-1202-5758-9fb2-640df1d3ba25 | note | Method - R
24792a94-b2ec-5b35-a948-317f5de8910c | note | Frequency - PW
6c036614-438c-537b-99d9-36590fc17cc3 | note | Hold/Witness Point Requirements: ROBAR - V
a5c59ab1-7895-50af-888f-04d4c46f8308 | note | Hold/Witness Point Requirements: SEPD - NA
93bd7cd7-748e-5f1d-ae32-f456e3f71105 | note | Hold/Witness Point Requirements: Client - NA
890f900e-2c7a-53be-8b81-7a06c7251042 | note | Records or Checklist Document Number - IFC Drawings
6d96e2a7-7e12-46c4-a019-688797ea0931 | checkpoint | 1.4 - Sediment control plan
28bbf8d2-77d0-5211-b5b2-4150183eb337 | note | Responsibility - SE/PE
1d7b93cd-0cb1-566c-a564-bb783a564ce1 | note | Specification Reference - WBS-SS-PM-PLN-0024, WAE230103-03-003 TM Rev0
a4ceab7b-56da-5874-a76f-fa1b5e25a2f1 | note | Conformance Criteria Summary - Sediment control measures in place
f98306a0-a1ae-50fa-95e8-ea3a1e482f7a | note | Method - R
2c5ae9cc-914b-53b8-aca4-fd45b66ae0a2 | note | Frequency - PW
ae5c7e9f-bbab-5feb-a8fe-71dfb6362fc8 | note | Hold/Witness Point Requirements: ROBAR - V
6c2668fe-9d3b-58eb-810f-8d0c33fd7c3e | note | Hold/Witness Point Requirements: SEPD - NA
9afa84a2-9df3-51d1-945d-5eef20e778cf | note | Hold/Witness Point Requirements: Client - NA
87ceb740-8b04-52ea-aa2a-83b8557331e3 | note | Records or Checklist Document Number - SEPD environment-al plan
e9282161-19a1-4690-8aa7-5d5c56e3f968 | checkpoint | 1.5 - Dust control plan
20865913-c2ae-5dfd-9f53-78bf3d512b2b | note | Responsibility - SE/PE
a4927cc6-c434-5362-b50e-b13e420335cb | note | Specification Reference - PP3 section 1.5 and section 4.1
9ceddbeb-632d-5911-a67c-3e32534a5a1f | note | Conformance Criteria Summary - Dust control measures in place
bbde52a1-8a7b-59ef-a258-8114ba8c0b39 | note | Method - R
a7de38da-0f7d-52f0-a199-6e7c6808f344 | note | Frequency - PW
c0e41ad6-dfa6-5df5-b283-0f114b063588 | note | Hold/Witness Point Requirements: ROBAR - V
357a855e-6abe-5eea-bb99-b32b5fc10db0 | note | Hold/Witness Point Requirements: SEPD - NA
05ca8daf-1690-5278-bca9-2fdfbcbe65de | note | Hold/Witness Point Requirements: Client - NA
cc44d686-d3d2-5ea1-a9c3-277159fa9198 | note | Records or Checklist Document Number - SEPD environment-al plan
0d8e3b65-3346-41c8-a87c-796d04c01156 | section | Section 2: Materials
1db4105c-99ea-4a99-b1ee-904d78f7cc5b | checkpoint | 2.1 - Import fill material inspection
acca818f-5d20-511f-8bdc-5c1fdf2de180 | note | Responsibility - SE/PE
6f98fe80-e26d-5d04-8b3a-47634020ba74 | note | Specification Reference - WBS-SS-CI-SPC-0006
b00ba6d2-bcc4-590d-8ee0-c1536e513118 | note | Conformance Criteria Summary - Material certificate and test report for particle size distribution, moisture content, MMDD
3e0e2000-cbee-5993-9d3f-47671e7a6802 | note | Method - R
0aeebea1-19c5-5aa6-8d22-2eb2069cf25a | note | Frequency - PW
2c79cc86-928a-5356-86c0-dbb90fb0ace7 | note | Hold/Witness Point Requirements: ROBAR - V
130008e6-2abc-526d-9a1d-12fface921bd | note | Hold/Witness Point Requirements: SEPD - V
d42ce498-e38a-53af-9c84-2146152fbabd | note | Hold/Witness Point Requirements: Client - NA
0ade8a38-9005-5a74-a7dc-f62d0af88d76 | note | Records or Checklist Document Number - Material certificates
cdc19136-59a5-4850-bf29-c4292435e444 | checkpoint | 2.2 - Verify suitable foundation material (compaction >95% MMDD)
0234c66c-cb17-50dd-a85b-d0d0c3076efb | note | Responsibility - SE/PE
ba23a6d0-f415-57d6-b045-221af3f0d771 | note | Specification Reference - WBS-SS-CI-SPC-0006
63afde34-2d4d-5be8-b7e7-bccf6f820e24 | note | Conformance Criteria Summary - Geotechnical test results showing compliance
9e7c624e-62f3-5bf6-8d9a-3ebc53a1705d | note | Method - R
8e4eadfc-7931-5bc8-89a3-e685b1c5b4ba | note | Frequency - PW
24a8f820-75e3-5985-b757-ca9ef7bdc93f | note | Hold/Witness Point Requirements: ROBAR - HP
ea1c18e0-fa29-5d62-ad79-584ac1e10913 | note | Hold/Witness Point Requirements: SEPD - HP
6813823b-d5e6-5a82-82a5-39a3e00e6218 | note | Hold/Witness Point Requirements: Client - NA
95b2f260-9f23-53a9-a968-19c6956f254b | note | Records or Checklist Document Number - Test results
63d8d3a9-05df-4fb2-9c2e-459760a59c6a | signoff | HOLD POINT
96cc5f97-3d84-4991-bcc1-63a0e27cdf7e | checklist | Lot Checks (Concrete Slabs) | itp | Lot
c0713e5b-f38b-427e-a0c2-d1cc91e9f790 | section | Section 1: Preliminaries
3216f4d6-e026-4dc4-8e39-1631c19f513b | checkpoint | 1.1 - Review of approved construction drawings and specifications
30634337-aeb9-52c7-a6a2-ba6931542675 | note | Responsibility - SE/PE
ce342923-6474-5f8e-a3f9-cf15f52d378b | note | Specification Reference - WBS-SS-CI-SPC-0007
e8b694d1-d11b-5f0b-aa17-8c31e81465c0 | note | Conformance Criteria Summary - Approved IFC drawings and project specifications available on-site
40cc3de6-96a7-554c-92c1-38745e565429 | note | Method - R
746b7796-8b06-5be1-8c9e-aa9d7e9ecc17 | note | Frequency - PW
c7e54883-f05d-501e-96e4-95ac5a6683bb | note | Hold/Witness Point Requirements: ROBAR - V
07aa42f2-cff4-53a9-9644-12309f1207ef | note | Hold/Witness Point Requirements: SEPD - NA
7eaa43f8-0d26-5581-b636-7608bd854ca4 | note | Hold/Witness Point Requirements: Client - NA
ea9ce35b-619c-59ef-b6b2-8f00a36c0300 | note | Records or Checklist Document Number - IFC Drawings
53062163-1859-4fa7-b2f8-31d64cbc3bb6 | checkpoint | 1.2 - Site condition check and access preparation
50484d3a-6a21-5a02-b740-996091e20fee | note | Responsibility - SE/PE
e0f6344d-7d90-573f-beb2-f539a4499265 | note | Specification Reference - WBS-SS-CI-SPC-0007
ad2ba613-c194-51a4-ae48-44754689465e | note | Conformance Criteria Summary - Site cleared, accessible, and suitable for concrete slab works
170533d8-1743-5c2a-a532-6a15da98fd28 | note | Method - R
c151e7d2-767a-5ec8-8a0f-9524abd6f7fe | note | Frequency - PW
a2e0bbc1-f547-57e3-be5e-69089a81717d | note | Hold/Witness Point Requirements: ROBAR - V
e7a141bb-9085-5661-ae0a-617dc04088ab | note | Hold/Witness Point Requirements: SEPD - NA
aafa5886-f65f-5524-b7cc-b102e3712376 | note | Hold/Witness Point Requirements: Client - NA
3c567f8e-313c-4573-85ac-be41f5c7d487 | checkpoint | 1.3 - Site safety induction and toolbox talks
cb2fe68b-bcfc-5124-8280-3d03c8e39cbe | note | Responsibility - SE/PE
9f1aaf4d-b4cf-5803-96da-facc6d644cd1 | note | Specification Reference - WBS-SS-CI-SPC-0007
f744793a-e557-52c7-b6fb-0ee18fb0a5e2 | note | Conformance Criteria Summary - All personnel inducted and briefed on safety, site-specific risks
ef7736e8-4815-5444-8a18-2e53b68fe7d9 | note | Method - R
720a21eb-e8c2-5fd1-85bd-c22fd51cf8b3 | note | Frequency - PW
daff337a-af5a-5ad0-8d85-0ab42a1cf25b | note | Hold/Witness Point Requirements: ROBAR - V
15ea763b-c6ae-587b-a525-db22c81ab913 | note | Hold/Witness Point Requirements: SEPD - NA
5c427e72-f2d5-5172-9d0b-66b8ffb00715 | note | Hold/Witness Point Requirements: Client - NA
578a4538-b90d-5ba6-925f-e6949a837e66 | note | Records or Checklist Document Number - Site inductions records
ca5e858f-d4ad-4075-8b8b-ecdc4d15e0fe | checkpoint | 1.4 - Inspection of plant and equipment (e.g., concrete pump, vibrators)
fc620d9c-78e3-5f66-a773-b8379dd08c05 | note | Responsibility - SE/PE
96f8c4ee-db01-5b5f-9b4b-114857c0495a | note | Specification Reference - WBS-SS-CI-SPC-0007
bd11f0e9-597d-5efa-a9e0-f7d589d32012 | note | Conformance Criteria Summary - All equipment calibrated and operational
8d8cffb2-f356-5851-a3d2-67fc5866e434 | note | Method - R
d2fc6994-6cc7-57e4-9fd9-4121df7daf71 | note | Frequency - PW
b4199594-5402-5dcf-9677-2d0b90087c56 | note | Hold/Witness Point Requirements: ROBAR - V
6e449897-3023-5f59-82d2-99b9c4d56d9f | note | Hold/Witness Point Requirements: SEPD - NA
499815ea-5f9e-5056-b60c-448ed769b38e | note | Hold/Witness Point Requirements: Client - NA
1ae04ce8-9a84-58bf-8050-33ffdaf63f94 | note | Records or Checklist Document Number - Calibration/Pre-start
e2941036-a84d-40e2-a845-9ac73cb9f93a | checkpoint | 1.5 - Foundation preparation
0102e900-2156-56f3-b919-24ef3c683755 | note | Responsibility - SE/PE
d8aa87a3-620f-5534-8488-b12e6a4a8a3a | note | Specification Reference - Geotechnical report/memo/ geotechnical engineer’s specifications
81c28f69-232a-50d6-95d2-694dc492f75c | note | Conformance Criteria Summary - Compaction test reports/geotechnical engineer’s specifications
b56713b3-ce50-596d-9332-cd41cbddea3e | note | Method - R
adc1dbe3-a81e-5403-9895-9a180ed15f2e | note | Frequency - PW
85fb2871-e84f-5d12-b281-c69d53ee2413 | note | Hold/Witness Point Requirements: ROBAR - V
e5965c68-eec9-585c-9cfd-c4cc37b39a08 | note | Hold/Witness Point Requirements: SEPD - V
20c21cc9-4ed2-52f3-90ff-24ce1b5e7c05 | note | Hold/Witness Point Requirements: Client - NA
b0a498c2-6073-5dcb-a4c7-1043e769b680 | note | Records or Checklist Document Number - Calibration/Pre-start
27628760-c1d0-4925-a906-d92d297e2d37 | section | Section 2: Pre-pour preparations
eb123bd9-2cc5-4fa8-9d14-1bb322177202 | checkpoint | 2.1 - Verification of work permits
6e14a383-699a-5c04-96c4-29dc5797e344 | note | Responsibility - SE/PE
7dd8df56-24cd-5077-a1d1-0a2963f3965f | note | Specification Reference - WBS-SS-CI-SPC-0007
178c7b72-ad5e-5bbb-b779-30f759a22404 | note | Conformance Criteria Summary - All necessary permits for concrete works in place (GDA/GDP)
fa935abd-695d-5741-9510-d499ec26ee50 | note | Method - R
3c16a583-4ccb-5678-9e8b-f72e5e392a6a | note | Frequency - PL
f8e3d89b-ded6-5dc7-b75f-d9f3e1007698 | note | Hold/Witness Point Requirements: ROBAR - V
8009902f-1a5e-597e-b980-29b7279ae0d1 | note | Hold/Witness Point Requirements: SEPD - V
980f19a2-aa00-586b-9735-9de0b69cdef9 | note | Hold/Witness Point Requirements: Client - NA
0c6ffcdb-e15e-51d6-8bc2-5925e2868f17 | note | Records or Checklist Document Number - GDA/GDP
10a621f5-d2ac-4f6c-9f81-2ceb5acff69e | checkpoint | 2.2 - Blinding concrete installation
f28599cf-70df-5bd5-ac3c-78130525c8fc | note | Responsibility - SE/PE
c5357609-9551-5a4e-8b45-de6f8afc283a | note | Specification Reference - WBS-SS-CI-SPC-0007 Design drawings
9e040952-9858-5800-93ed-98705a77cadf | note | Conformance Criteria Summary - Approved mix design
1c6bb724-c40c-560e-a898-e5c31cb0caf9 | note | Method - R
3cb0c7fe-c406-5b1c-8fda-adffb51d9d43 | note | Frequency - PL
1bacabb1-5693-5469-9ffe-50f2b0ccb849 | note | Hold/Witness Point Requirements: ROBAR - V
80196435-c18c-5c71-a024-ad99c6f878e3 | note | Hold/Witness Point Requirements: SEPD - V
f9cc6e4d-a4d7-58c4-86ed-828135a477e7 | note | Hold/Witness Point Requirements: Client - NA
b15b8af5-1c3c-5e70-bc8a-155e96385cf8 | note | Records or Checklist Document Number - FIC
e3436f17-5aca-4d41-9129-eacb7bffaa00 | checkpoint | 2.3 - Review of concrete mix design and material certificates
367029cb-334e-565c-8ce0-605af9ddcc4b | note | Responsibility - SE/PE
cd9d91f7-8e40-57aa-a54e-858275268dbb | note | Specification Reference - WBS-SS-CI-SPC-0007
47130eeb-6259-5d53-b2a7-41f7a4e4025a | note | Conformance Criteria Summary - Approved mix design, material certificates compliant with AS 1379
f9fd0a5b-0eaa-5c6c-aa42-b69d37639467 | note | Method - R
6c95c87b-cdd9-5567-a647-671614d38aa0 | note | Frequency - PW
aa4f5da2-9f5a-514c-a4ab-8a31dfff6459 | note | Hold/Witness Point Requirements: ROBAR - HP
0dab5c73-3849-5514-8143-9ef691c51e71 | note | Hold/Witness Point Requirements: SEPD - HP
8f28c926-0fda-5dc8-9930-83e9eeb289ae | note | Hold/Witness Point Requirements: Client - NA
7db7a1cf-1022-5ad1-b813-00ef7b8460f0 | note | Records or Checklist Document Number - Product certificate of compliance
b5601acd-f415-4999-bc62-db3019f63715 | signoff | HOLD POINT
9de0b92e-2b18-4ae6-a65b-70aafcd2cf16 | checkpoint | 2.4 - Formwork inspection – alignment, cleanliness, and dimensions
66900275-64a4-5bc3-98e7-122dde270939 | note | Responsibility - SE/PE
266f612d-35d8-598b-b293-80e4cf752777 | note | Specification Reference - WBS-SS-CI-SPC-0007
c4149233-a951-586d-a51a-c653dfb6abd7 | note | Conformance Criteria Summary - Formwork in line with drawings, clean, and dimensionally correct
c1ec5f01-8d50-5ac6-992a-3977e52f4acb | note | Method - R
ec32cd81-e65c-5646-8918-6b3630d68fe8 | note | Frequency - PW
7a653f91-226f-5af5-bb31-b694ee48887f | note | Hold/Witness Point Requirements: ROBAR - HP
debce9a9-9263-5736-9081-8a0d0c5b2e2a | note | Hold/Witness Point Requirements: SEPD - HP
b0c7df6c-9a13-51ed-867b-9531c2eaad55 | note | Hold/Witness Point Requirements: Client - NA
d8e0bfe7-2b37-58de-aba4-7168516b7a93 | note | Records or Checklist Document Number - TWD FIC
98a61297-bc49-46ca-928c-b243f4232028 | signoff | HOLD POINT
a2578135-830c-40a3-921b-0c5c8795197a | checkpoint | 2.5 - Reinforcement inspection (size, spacing, placement, cover)
d7e2d0ac-21d7-5b31-bd12-ed44f75a4926 | note | Responsibility - SE/PE
7c37ba0c-d41f-5998-9895-5dc3d6bbfd67 | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 4671
187b5e04-9887-5bbc-8632-897274060343 | note | Conformance Criteria Summary - Correct bar size, spacing, reinforcement securely tied, adequate cover
daf55450-c312-5d5a-a4b7-e9b8f8253dcc | note | Method - R
4ef04433-d51e-5075-912a-30fa5c9371a5 | note | Frequency - PW
bc31033c-7a03-5c99-a7c7-007016017627 | note | Hold/Witness Point Requirements: ROBAR - HP
c0c2a46b-d33f-5577-9f2b-b958eefb3239 | note | Hold/Witness Point Requirements: SEPD - HP
499c692f-9855-56c9-ba22-9f2db3dee9e7 | note | Hold/Witness Point Requirements: Client - NA
30d30c58-48c1-5854-a5fc-451091a3bc69 | note | Records or Checklist Document Number - IFC Drawings FIC
f1bd02c9-7876-4621-9bd8-bde7df88e2fe | signoff | HOLD POINT
8718e6e0-14fb-4f78-88f3-81b87b0bc863 | checkpoint | 2.6 - Verify waterproofing membrane
cd6fd7a0-3e3f-5422-b0c0-66d0cb42d60b | note | Responsibility - SE/PE
dcd8b975-7714-5784-96af-3e69a8f05d65 | note | Specification Reference - WBS-SS-CI-SPC-0007
2497f945-16d2-5cb7-a105-7f7e614f42c4 | note | Conformance Criteria Summary - Membrane installed as per drawings/specs
49be7852-a4a7-5c70-8235-453e437a0d13 | note | Method - R
635120b5-52a5-500f-9065-92bb9791268f | note | Frequency - PW
7b4d2db9-80fb-5d46-9e94-f8b82f1791e7 | note | Hold/Witness Point Requirements: ROBAR - WP
738b9293-d850-50b2-8006-96eb5072413c | note | Hold/Witness Point Requirements: SEPD - WP
6b9b70ab-9fb3-5e10-b46c-dac0b496dacc | note | Hold/Witness Point Requirements: Client - NA
b53602e9-aa3e-5e8c-9754-341c6b36c198 | note | Records or Checklist Document Number - IFC Drawings FIC
ece605ee-80df-45ad-86c2-f138e5ed941b | checkpoint | 2.7 - Re-entrant bars (starter bars) and corner reinforcement
88a20c18-be9c-5e53-8ccf-803e61082746 | note | Responsibility - SE/PE
60993089-3351-5c21-95d4-47648b756f47 | note | Specification Reference - WBS-SS-CI-SPC-0007
0fa97f51-0098-54db-b517-9bbda23bef54 | note | Conformance Criteria Summary - Correct positioning of all embedded items per drawings
5154db5b-609a-5a72-aa24-70c3cb481a91 | note | Method - R
0f82c95f-1340-5d65-89b7-d841dba08163 | note | Frequency - PW
c0aeb55c-eba4-506b-b9ae-31ea18ed0476 | note | Hold/Witness Point Requirements: ROBAR - WP
72ccc7e8-ef5d-5a40-9675-84e6e6e6856c | note | Hold/Witness Point Requirements: SEPD - WP
00868fa0-7a42-5060-a7e7-418b47ab641c | note | Hold/Witness Point Requirements: Client - NA
4ee9788f-b91e-5fcc-ae53-e725868c2130 | note | Records or Checklist Document Number - IFC Drawings FIC
fa7d4f37-3895-4ffd-a2ef-d92c6686c831 | checkpoint | 2.8 - Concrete batch plant inspection
f60f8fae-6678-5783-a839-a31b0993db9e | note | Responsibility - SE/PE
7e4838f5-a7a8-542a-877c-dec96477fc6c | note | Specification Reference - AS 1379
6b66915f-37d8-5a60-bd25-fe01c014963f | note | Conformance Criteria Summary - Batch plant adheres to mix design, and delivery meets timing requirements
9a5d1052-c6ff-5036-9199-badac204888b | note | Method - R
f0a5a163-c484-5b25-a2a9-a18f5d0563f7 | note | Frequency - PW
38adc346-98fe-5c12-8502-e56cdeeb4fd4 | note | Hold/Witness Point Requirements: ROBAR - V
2eabf117-319b-584a-9c85-9b6324c9b122 | note | Hold/Witness Point Requirements: SEPD - NA
3ba16d47-d848-50b3-a3b1-e0b5885bb16a | note | Hold/Witness Point Requirements: Client - NA
e380650d-628f-57f5-b340-42c9cb14b3e7 | note | Records or Checklist Document Number - FIC
989f26da-fed7-4ea1-b745-6c967162e14c | checklist | Project Photos |  | Project Photos
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
2f595e7f-92f4-4834-a1eb-63e97455c8d0 | checkpoint | Upload site photos
326668f9-3d34-495a-b04f-15a1bb0c11f5 | checklist | RR-SEPD-BESS-FIC-001-01 - Earthworks | itp | RR-SEPD-BESS-FIC-001-01 - Earthworks -
87b5eb07-576f-4c2f-b86c-7a82e5812db1 | section | Part 1 – Preliminaries (photos where applicable)
744ef392-bb3f-45c1-8004-612dea734f3d | checkpoint | Review of approved construction drawings and specifications
6f0e6ad6-89f4-5e73-b949-489845d4a418 | note | All drawings and specifications approved and up to date
44cad7ca-783f-5332-b20e-8fb7678881b5 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
8b1d093f-7f56-4ff9-ba46-fdd1e5392c13 | checkpoint | Verification of permits
b7be4f80-1cc7-5bfe-982c-076df4399b70 | note | All relevant permits (GDA/GDP) in place
f33d6102-4868-5d03-bf84-a6ecdfacff7b | note | Specifications/Drawings Reference - GDA/GDP
ff9a08fe-3b3b-4332-9cff-6062ace46577 | checkpoint | Site access and safety preparation
3c444e26-6cc0-5e64-8b8b-ac923e4164bb | note | Site access cleared and made safe
c4f04b07-133b-5075-80a9-e4757167b708 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
8277fff3-b62a-4f92-95da-7c42305b1066 | checkpoint | Safety inductions and toolbox talks
cd737a2d-b8d3-556b-8c5d-b6f33a4923d9 | note | All personnel inducted; safety briefings completed
22fc95ef-c494-5f03-b0d6-a372fcfec36b | note | Specifications/Drawings Reference - Induction record
02e91297-3dfc-41e7-94ae-514b8d678b45 | checkpoint | Environmental controls in place
be7d955d-9f62-5532-b906-09b977ad2a9a | note | Dust, noise, and sediment barriers installed and functioning
44e955b1-9fef-5c42-adf4-b772786f8e59 | note | Specifications/Drawings Reference - SEPD environmental requirements
26ed3d4c-d985-4e94-86c5-f4afec09407d | section | Part 2 – Set-out and excavation (photos where applicable)
77408a55-0ccc-4fb5-9301-3bcc34e1d8b2 | checkpoint | Site set-out verification
1c3438b4-b05e-5510-a48b-e43f82e19b29 | note | Set-out verified and matches IFC drawings
710ee0c9-d13c-5606-9538-84940b38a330 | note | Specifications/Drawings Reference - Site IFC Drawings
8adc9b2c-c704-4d62-9d4f-a051b8e35859 | checkpoint | Excavation to design levels
62d4ce23-a61c-53cc-96ea-3113f13e1694 | note | Excavation within tolerance of design levels
d5da907d-904a-5616-8322-e16f2d09cbd1 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
a02eb524-821f-45ca-9277-6754dadbecfe | checkpoint | Stockpiling of excavated material
8372dd4f-35e1-5a0d-af45-fa68e7a719e4 | note | Material stockpiled properly, no contamination
8793284a-7ea8-5db6-9c5c-973ea6ea9e47 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006 Galt construction sediment control plan
b1d9772c-5c27-4364-a1de-04db1123220d | checkpoint | Subgrade inspection
a9cc5602-680a-5e10-993b-78fd0310a105 | note | Subgrade verified, compacted and stable
b99cb831-aae1-5ca5-b38f-22c05739f05e | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006 Geotechnical report
f50ed6fe-d6f9-4421-b777-b857ad1a4838 | checkpoint | Principal Inspection
9fc4e47e-4748-5f37-94d6-95c75727eb1e | note | Principal’s Project Requirement to have principal release the HOLD POINT for backfilling foundations
704c35a8-2cfa-5b6e-a95c-61319819d8ae | note | Specifications/Drawings Reference - Principal Project Requirements
70f1b27e-7798-4ebd-a45f-58c25fc18a24 | checkpoint | Subgrade compaction testing
87a6505d-6051-56ae-a528-899e6b86c816 | note | CBR and compaction results meet project criteria
33cb3965-0f15-5ec9-b24e-92491629b524 | note | Specifications/Drawings Reference - AS 1289 Geotechnical report WBS-SS-CI-SPC-0006
6a4da468-598e-4c1b-92f7-dd56a304062e | checkpoint | Proof rolling of subgrade
01dfea3b-80f2-52c5-b469-2bd84ec22c51 | note | Subgrade proof-rolled to confirm stability and detect soft spots
a3e95d4e-989b-5ea5-8445-960651db6634 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
edbe548a-c49b-4c74-a48d-0b42c874a7cc | section | Part 3 – Fill material and compaction (photos where applicable)
de39163c-0e46-47ac-9021-6824015056f6 | checkpoint | Imported fill material testing
d056ee87-e0d7-52ab-8376-f0df8008d018 | note | Material complies with particle size, moisture content, MMDD, Die back certificate
7a12e6ce-5912-5e38-9e06-2b86062d74d5 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006 Test material results
58d1fed3-2301-45a0-9b43-ba4062d031ae | checkpoint | Fill placement in 250-300mm lifts
f88395e3-aa3b-5abc-ba20-702209ea54e7 | note | Layers placed in maximum 300mm (loose) thickness
ea04e54e-4d2f-5a65-a07b-bb7d7c27d486 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
69bc23fa-6a29-426e-b40b-d24785ea0999 | checkpoint | Compaction testing
d906db38-7477-5f60-9966-9be6761281b5 | note | Compaction >95% MMDD
c0514e17-a8c8-5df0-ab82-40e57c9534d9 | note | Specifications/Drawings Reference - AS 1289 Compaction test results WBS-SS-CI-SPC-0006
131c31c2-d57a-458a-99eb-339b6a9a04c5 | checkpoint | Level and grading check
68e6e6ec-ed8b-55dd-bb7b-73b2c2f6b931 | note | Levels and grading match design tolerances (+/- 20mm)
3e291cfa-4984-56b8-90e2-e855b1f1074c | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006 Survey Report
22d067fd-7c55-4d53-8b5e-6525e03828ff | section | Part 4 – Environmental and erosion controls (photos where applicable)
752ff6ee-5433-4990-bcf6-17786d554c7b | checkpoint | Dust control measures
e9565d8a-a0ec-549b-a11e-4ad82386c985 | note | Dust suppression methods in place and effective
9dba82b7-6003-556e-ab28-0204d526d2e2 | note | Specifications/Drawings Reference - SEPD Environmental Plan
05f8d015-431c-4995-ba8f-0c6cf8037b89 | checkpoint | Erosion and sediment control measures
a86a2dcc-f6df-541e-963f-6a3e7f0caa3d | note | Sediment barriers, silt fences, and basins installed and maintained
14e05556-4771-5116-a836-3346afc44285 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006 WAE230103-03 003 TM Rev1 CESCMP
e0cd18a2-22a7-4d77-bb43-59239dcc0ce5 | checkpoint | Site drainage
3487a660-65a1-569b-847f-3e14c942ef04 | note | Temporary drainage in place to control stormwater and prevent site flooding
5ef1b87e-9c12-52fa-8dfe-3ef5d250b76b | note | Specifications/Drawings Reference - Drainage Plan Site Inspection Galt construction sediment control plan
018e0979-e3db-4708-877d-1840c866d3cc | section | Part 5 – Final inspections and acceptance (photos where applicable)
db3333a1-736f-4e20-8b47-826e944d804b | checkpoint | Final surface inspection
6e89f35f-2449-5df3-9c8d-b6b0d59582b8 | note | Surface is stable, free from defects, and meets design criteria
276cae38-a1b9-5fb4-a27b-2cfea0f65948 | note | Specifications/Drawings Reference - Site inspection Proof roll
e64612cf-8790-48c0-8603-ae5a3254d227 | checkpoint | As-built survey verification
c716100f-eaf5-5774-8cdd-2257c0cd75c7 | note | As-built levels and layout match design
c654e383-7297-5e6c-adeb-a1814a3f91ae | note | Specifications/Drawings Reference - As-Built Drawings Survey Report
e0f979e1-fd8e-4ff8-804f-c41bc2a72c0d | checkpoint | Removal of temporary works
6c0d3083-e99d-5bd5-94ca-aa5c7f301b3e | note | All temporary structures, barriers, and access points removed
1f310242-56ba-5633-b6e8-07fd031c9014 | note | Specifications/Drawings Reference - Site inspection
ced04db8-c1fd-49a7-bfaf-641ebe0f888b | checkpoint | Final inspection sign-off
2b4f8184-8ae6-57f5-b914-ab5ac7c8d22a | note | Earthworks activities completed and accepted
22e8605c-d619-585c-a560-842a26a7e401 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
1a5b28da-e51d-4fd8-94ff-70f9f62679b8 | section | Document Sign-off
ab136bcf-2721-448a-9da3-e20f41ec1e49 | checkpoint | Prepared by:
ca84f374-4c64-5cd2-8481-5c07a55acae7 | textbox | SEPD (Engineer) - Name:
98308999-ecfe-50f4-a33a-33e5ad8ef017 | date | SEPD (Engineer) - Date:
4f3d84aa-f3a2-4d0e-97a9-ec7a15828610 | signoff | Add Signature
e67c9062-1257-4597-a150-b59aa3a48eeb | checklist | RR-SEPD-BESS-FIC-002-00 - Concrete slabs | itp | RR-SEPD-BESS-FIC-002-00 - Concrete slabs -
97531fa1-8e70-4bd0-8938-256a1a8cc941 | section | Part 1 – Preliminaries (photos where applicable)
73aa77b7-ade6-4e60-95e4-feb19198e094 | checkpoint | Review of approved construction drawings and specifications
2727464c-98cc-52f5-bd08-c825a8eb7f5b | note | All drawings and specifications approved and up to date
6c3b19e1-669e-50bb-ad55-49e74dd6a647 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-007
aa02a855-c7ea-46c3-95e7-4c76126a1f78 | checkpoint | Verification of permits
630db3d5-dd49-5458-a025-e14883cd047c | note | All relevant permits (GDA/GDP) in place
b4fd9c06-30be-5375-a77e-bad44be3be44 | note | Specifications/Drawings Reference - GDA/GDP
c338dedf-87be-4619-826e-26a206fc78f5 | checkpoint | Site access and safety preparation
4a761837-32ce-556b-ad7c-439091c41a6a | note | Site access cleared and made safe
75010945-96b4-5b54-bf3f-4241701a7c6d | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-007
9933934f-36cc-46de-bb6a-94682db37262 | checkpoint | Safety inductions and toolbox talks
02e4e6ee-0ae3-5c94-9805-f2229aaa78a6 | note | All personnel inducted; safety briefings completed
6f518f86-a7c2-5033-8969-13731569e5cd | note | Specifications/Drawings Reference - Induction record
16c590e8-06a0-4bdb-a72b-083f89a8bc20 | checkpoint | Environmental controls in place
012e6832-9e77-5746-b991-d0497ee1a416 | note | Dust, noise, and sediment barriers installed and functioning
b3985007-3aec-5724-ba64-64b03b1b000a | note | Specifications/Drawings Reference - SEPD environmental requirements
77f6771b-1790-4751-baa0-2d42f058f126 | section | Part 2 – Survey (photos where applicable)
55783876-995f-4bfa-94d4-cab35fc59a95 | checkpoint | Set-out of slab location
42d47ccc-a50b-5258-817f-64a8c9e43a26 | note | Slab set-out conforms to approved design coordinates
8a0135f0-3821-5f65-8bbb-df8a8874981b | note | Specifications/Drawings Reference - Site Layout Drawings, Survey Plan
05cee545-64ae-4e81-a5e8-0baa31b7b910 | checkpoint | Level and alignment check
8994addf-d6da-508d-bc80-56967f8fd89b | note | Levels and alignment of formwork and slab position verified
53f4d84c-78d1-5879-8875-26595cf7534b | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007, Survey Report
3084a2d7-1b9c-4761-95d7-0d0f6cfcf090 | checkpoint | As-built survey after formwork and reinforcement
89fb7859-d945-5b31-9ddd-c9d477c6f59a | note | Survey to confirm reinforcement cover and formwork position
789f32f0-4a48-57df-b1b5-089f0262f720 | note | Specifications/Drawings Reference - As-Built Drawings, Survey Report
8b7fa29c-a2b2-432c-b35b-d8cbc8e864b6 | section | Part 3 – Pre-pour inspection (photos where applicable)
1540ac7f-4c40-4bf8-86df-703f79d81ee1 | checkpoint | Review of approved concrete mix design
23accabf-e0b8-5161-a901-bdfc28ccac6b | note | Mix design approved P3220100
93e1ddc7-8d37-5b85-9377-db2e7c7337c9 | note | Specifications/Drawings Reference - AS 1379, WBS-SS-CI-SPC-0007
504b36f6-3b9c-4f50-a8ea-ed28e3177ba1 | checkpoint | Formwork installation
383566d7-5a8a-5186-8680-91f12310d0f5 | note | Formwork aligned, clean, and secure; dimensions correct
245380c0-45a5-51aa-851d-cc6ad13807bf | note | Specifications/Drawings Reference - AS 3610, WBS-SS-CI-SPC-0007
899553bb-a214-409f-b57c-ebd801c69a39 | checkpoint | Reinforcement placement
c0fc234f-77bf-541a-a50a-03204290ae08 | note | Reinforcement size, placement, spacing and cover as per drawings
8421dc20-23ad-54fd-9d1a-eb86fca8655e | note | Specifications/Drawings Reference - AS 4671, WBS-SS-CI-SPC-0007
2e912fe3-37fb-49be-8098-c602abaae4f6 | checkpoint | Reinforcement ties
be900450-a4d0-5225-b1b2-a02ceebb3c31 | note | Reinforcement securely tied in place, no loose bars
7c88349e-e273-5f2d-846e-d3dc8be5004b | note | Specifications/Drawings Reference - AS 4671
914b0012-8d33-48c3-8237-71c22d52c17e | checkpoint | Installation of dowels
693821b5-ab72-5ba8-b67e-f0da7685ba4d | note | Correct placement of all embedded items, dowels aligned
2a97dfc1-b45e-5f9a-bc30-8863396f4408 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007
ef203b77-30b7-43d4-98e1-ace5e791117b | checkpoint | Waterproofing membrane
36646b24-737d-542a-a59f-216b0f9b7bd2 | note | Membrane installed per design; overlaps secured
8c4e0d71-d1ad-5b0a-a545-bc7796cbfe04 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007
99e52d5d-1127-44c3-aac5-2c3287cbe59b | checkpoint | Crack control joints
4f7ce754-8667-5c8e-81e3-31b7cfb9eb2d | note | Joints placed and cut as per drawings and specifications
350e0c0c-8a4a-5baf-88c1-01f880b11d7e | note | Specifications/Drawings Reference - AS 3600, WBS-SS-CI-SPC-0007
bc60da28-8d12-478e-9eb1-a2c3468af046 | checkpoint | Construction joints
56a338b5-8ce8-59a0-a992-e561f99ed015 | note | Joints placed and prepared as per drawings and specifications
33abacb5-290f-59ae-918e-38d60ee05914 | note | Specifications/Drawings Reference - AS 3600, WBS-SS-CI-SPC-0007
8d19c651-accd-453d-8471-d215aa428c58 | checkpoint | Site safety inspection prior to pour
a5f25890-d039-57cd-a6a8-625a9e55f08f | note | Site clear, access routes checked, and emergency plans in place
a448061b-6824-5546-b1ef-1ba4b2aa8286 | note | Specifications/Drawings Reference - Safety Plan, WBS-SS-CI-SPC-0007
4a6337f1-e2da-4b3b-9a81-e091db2d9663 | section | Part 4 – Concrete pouring and compaction (photos where applicable)
12945ad2-b1fb-49a2-a2a3-2349ee5c7948 | checkpoint | Concrete delivery
2dc6cf20-7815-5e92-bc90-6356bb688f5a | note | Delivery in line with approved mix design
f3447ec1-084d-5a1f-9a08-7cdb8e6a16b2 | note | Specifications/Drawings Reference - AS 1379, Delivery dockets
5b784a47-f8d5-4b22-ab3e-11d2d540e881 | checkpoint | Slump test
72907292-bd41-57c5-907b-d750430fc888 | note | Slump within specified range (e.g., 100mm +/- 20mm)
97fd5123-dc31-5ed6-ab17-bc1a96987679 | note | Specifications/Drawings Reference - AS 1012, Slump Test Results
5db39adb-cf85-450e-874d-6f5ba8798ef0 | checkpoint | Concrete placement
906c62fa-6906-5e91-9625-abdb2dc45244 | note | Concrete placed within formwork without segregation or delays
fd07646b-d9c8-50b5-844e-b3c924f99ea4 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007
c13faa7b-37f7-4278-b17e-43a94144694f | checkpoint | Compaction of concrete
05744d26-5d79-5b13-aaa5-7029fca0db2f | note | Concrete compacted using vibrators, no visible voids or honeycombing
c4102f86-bb81-5af6-b1b7-03318728a4d0 | note | Specifications/Drawings Reference - AS 3600, WBS-SS-CI-SPC-0007
cbef00f4-13e4-43a0-ab06-b06e7d94d2c9 | checkpoint | Cylinder sampling for compressive strength
4f9dcdd9-8608-56aa-9779-91aa503e0ed3 | note | Cylinder samples taken for 7, 14, 28-day tests
aa458440-88fb-5d19-9ccd-c373f588ec38 | note | Specifications/Drawings Reference - AS 1012, Sample Register
9c89d006-353b-4b03-a9d0-0e349082f97c | checkpoint | Concrete temperature monitoring (if required)
9c9b7cc3-8649-5432-bac4-7c1fc2068dc0 | note | Temperature recorded during pouring
5034577c-75fd-5b9a-a01f-7c7f43b924ac | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007, Pour record
cb0248b8-7935-4f72-acac-a4d9e30956fb | section | Part 5 – Post-pour inspection (photos where applicable)
8dd79ea6-2d6a-4930-b126-ebcb1dfb8bdd | checkpoint | Surface finish
c172d179-0ee6-59a9-8a30-235b99c7e65d | note | Class 5
0080eae1-8d54-53c0-ba2b-c064e1289a42 | note | Specifications/Drawings Reference - AS 3610, WBS-SS-CI-SPC-0007
9816562d-bf04-4d7b-af87-20601698a89d | checkpoint | Curing method
6996bae3-cb29-5afe-91bf-477db268632d | note | Curing compound or wet curing applied as per requirements
e32033a8-61db-5a30-aa7c-724100adeb72 | note | Specifications/Drawings Reference - AS 3799, WBS-SS-CI-SPC-0007
0829052d-8d7b-401c-b45a-01ca813e7a60 | checkpoint | Formwork stripping
d3d2f44c-7992-533a-a573-c87c42db00d7 | note | Formwork removed after concrete reaches required strength
5f253170-ccf2-50b0-bda7-2929d5b38e98 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007
2cb242af-f7e3-4121-85ca-36cdc298531e | checkpoint | Compressive strength testing
1967ef0e-d91b-5dd5-8173-974911f28732 | note | Compressive strength results meet >32 MPa at 28 days
42cb11ef-f217-5211-9f30-a97697c517e4 | note | Specifications/Drawings Reference - AS 1012, Test Results
4bd5be95-2a03-43ac-8b6f-f8c0a59b2f81 | checkpoint | Inspection of surface cracks and defects
69dddd49-846a-50eb-8d2a-ca0bc0f444dc | note | No major cracks or surface defects observed
529a90d9-ef9b-559d-b145-a44e84803cc6 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007
ef76c153-fbfe-4447-a327-59fdc66f2e11 | section | Part 5 – Final survey and as-built verification (photos where applicable)
5c8efa4d-70e9-4f6f-b93e-f44891faef76 | checkpoint | As-built survey verification
24980e66-de23-5e8f-9c58-b63f8522cb1d | note | As-built levels and layout match design
8bd0d860-ec64-59f6-8faf-1036219282e7 | note | Specifications/Drawings Reference - As-Built Drawings, Survey Report
881716bc-df4c-4021-ba8f-f34abfe9e3d5 | checkpoint | Final inspection sign-off
7e4c8a72-14b9-5c4d-960d-8a39407f9811 | note | Final approval of the slab surface, dimensions, and finish
76f72e52-62c6-5b50-9c2c-9425fb134d23 | note | Specifications/Drawings Reference - FIC sign-off
e593606c-8846-4fa9-840b-e18534959f34 | section | Document Sign-off
68d9bb92-f5ab-4ab0-98ef-37e5eafe834d | checkpoint | Prepared by:
7e60fb1e-903b-5255-8a80-ed5bad72b807 | textbox | SEPD (Engineer) - Name:
8201cdc3-2dc2-5660-9afc-c14933d03ce7 | date | SEPD (Engineer) - Date:
e9e1d579-f4fa-4c8e-9be2-12dc92d550ae | signoff | Add Signature
22ef4b64-570c-4f04-8ab8-77e2a18321b7 | checklist | RR-SEPD-BESS-FIC-004-01 - Proof roll | itp | RR-SEPD-BESS-FIC-004-01 - Proof roll
d1f978cf-bf8a-41fa-b95e-7a6bfd5fc925 | section | Part 1 – Proof roll (photos where applicable)
e9ad6f2f-ba11-4a5c-b9fc-5fc78869d5bc | checkpoint | 1.1 - Smooth Drum Roller – 12t
ac59aba5-2e75-50a6-9209-6d20680ecb62 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006
aaacc864-e29e-4e90-8060-52201efa1d48 | checkpoint | 1.2 - Plate compactor – 0.75t
15888de4-f925-5440-872a-3f93219a8d62 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006
ddda332a-7f42-401f-b435-eeb363a81efd | checkpoint | 1.3 - Single pass with smooth drum roller to cover the area for the proof roll. If any doubts remain after a single pass, any subsequent passes, yet no greater than four, further compaction works shall be carried out till SEPD supervisor and PE are satisfied that there are no visual subgrade defects.
38316a20-1dcd-528b-b3ce-c5aada29701e | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006
870a11af-e1d6-462f-9c97-5d81d3d5990b | checkpoint | 1.4 - The speed of the pass shall be constant and sufficient and no greater than walking speed.
3c31a49c-f68e-553c-9c69-714c74c8c562 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006
dd2bc782-5158-446a-ab08-abd29316511b | checkpoint | 1.5 - No proof rolling to be conducted within 2m of footings, foundations or retaining walls. Subject to a visual assessment and the principal’s approval, any compaction within this proximity of civil infrastructure shall be only achieved using hand compaction methods.
a6a44f92-8b19-581c-8171-32002b17b4f4 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006
889d9253-351f-4e5a-9227-ab14dc8fe01b | section | Part 2 – Comments
87dcc43d-c749-4468-a07d-b40228c5d4f7 | checkpoint-no-value | Comments:
afcac34c-0667-4528-9417-fcd26e73899e | section | Document Sign-off
3042148d-1bd7-4489-9246-82899ad354e3 | checkpoint | Prepared by:
d2c2cf7d-d312-5bc6-a7d4-4823c5e1dbfb | textbox | SEPD (Engineer) - Name:
cbdabcd8-6241-5219-b6de-61e69b3e695c | date | SEPD (Engineer) - Date:
6964c87b-a9d5-40c0-b334-7ec92f5e1b34 | signoff | Add Signature
4179c91d-7f59-466a-a726-0f1c39795541 | checklist | RR-SEPD-BESS-ITP-001-01 - Earthworks | itp | RR-SEPD-BESS-ITP-001-01 - Earthworks - Layer
32e5e86d-ff97-4af1-9c74-dc449e940113 | section | Section 1: Earthworks
409d1609-0995-45e8-9afc-4dfe337d8526 | checkpoint | 3.1 - Excavation to subgrade – verify lines, depth and dimensions
7d8e196f-d342-5157-acee-bcb07665f212 | note | Responsibility - SE/PE
9220892c-62d6-5d55-a764-a0bc84dedd42 | note | Specification Reference - WBS-SS-CI-SPC-0006
771e2794-58fc-573c-af02-f00d1ad8034c | note | Conformance Criteria Summary - Compliance with design drawings and subgrade preparation
1a540eed-1db3-5010-bed9-5580e3b46665 | note | Method - I
0de44e87-4ad8-5892-b07f-dc0cb38b5e6e | note | Frequency - PL
155b56dd-7411-5bf6-88d6-0246dbf17b99 | note | Hold/Witness Point Requirements: ROBAR - V
1c10a1c6-6aef-54f7-87a1-c6b6a8a6d61f | note | Hold/Witness Point Requirements: SEPD - V
e54b82d8-0ad8-5ea8-8df9-428153e385fd | note | Hold/Witness Point Requirements: Client - NA
55188513-fb90-5e33-bd48-243255745252 | note | Records or Checklist Document Number - IFC Drawings
a6f02a31-b623-497e-9200-2704507faf4a | checkpoint | 3.2 - Stockpiling of excavated material – manage and segregate by type
05858e3d-b25d-5637-af53-0de042c21db6 | note | Responsibility - SE/PE
6965bc3d-551b-5e8c-8447-160d2a0775d5 | note | Specification Reference - WBS-SS-CI-0006
df49beda-534d-5a07-a657-fb2a321bd3af | note | Conformance Criteria Summary - Material stockpiled appropriately, no cross contamination
3820134d-36b8-58b7-a1d5-40d26841339e | note | Method - I
9bd26fee-5b57-5beb-8b8e-dd854cdc0d88 | note | Frequency - PL
a5eb04c4-53ba-5bb1-9d73-fde2ddbe96b2 | note | Hold/Witness Point Requirements: ROBAR - V
1d3b5edb-a68d-58eb-8426-07732ec9e54a | note | Hold/Witness Point Requirements: SEPD - V
25fa1a3d-b5f5-529e-bcc2-b4747fec05a3 | note | Hold/Witness Point Requirements: Client - NA
4492186b-ac54-5047-b97c-2adbb9195039 | note | Records or Checklist Document Number - SEPD environment-al plan
a160b9ef-41bf-49db-9c8c-cc51009ac802 | checkpoint | 3.3 - Subgrade proof roll
4ad682db-fc7a-5f49-801a-aa663f84f2be | note | Responsibility - SE/PE
3a604f03-5344-5510-afdc-f3d5b8043377 | note | Specification Reference - WBS-SS-CI-SPC-0006
fd5db355-bff8-592f-9601-ad8223ca71ab | note | Conformance Criteria Summary - Subgrade meets stability requirements
3f1c8074-2558-50b8-9a88-843d04fd39a8 | note | ○ Subgrade proof roll shall be inspected by the Principal
762d0fb1-cf36-51c4-a7b8-c69fd7330a36 | note | Method - T
6feba1f9-7f04-5c46-af13-f9e458339008 | note | Frequency - PL
6f095dc4-a3a0-599d-b20b-e1e82ff9bb5a | note | Hold/Witness Point Requirements: ROBAR - HP
43060b07-e0ad-545e-ac15-d9d2710064f3 | note | Hold/Witness Point Requirements: SEPD - HP
cb3ad0a5-712d-5b60-9752-d7c887fe3b28 | note | Hold/Witness Point Requirements: Client - NA
83b4993e-59fb-5020-9589-2a4062116699 | note | Records or Checklist Document Number - WBS-SS-CI-ITP-910049
951bf58a-2653-47f9-af51-93cf05fda6be | signoff | HOLD POINT
c6837b5d-d3d6-4c95-846f-1c7f65629b70 | checkpoint | 3.4 - Backfill under slabs and compaction of lifts
87c1ab8f-c8cc-5973-b478-be2c82720aa5 | note | Responsibility - SE/PE
59f7e2f1-601e-51a9-a8b8-b17a07842ceb | note | Specification Reference - WBS-SS-CI-0006
4eee7b4c-20a0-58d1-8788-7262c74e1e76 | note | Conformance Criteria Summary - Backfill material compacted in layers to required thickness
c54e752e-29b0-5f9a-9b82-d70fba6a168f | note | Method - I
3b56e54c-25fe-532f-9ebc-fdff55c3348e | note | Frequency - PL
f766f266-2d19-5ec7-aa35-4542517b8334 | note | Hold/Witness Point Requirements: ROBAR - V
df5f7aaf-e852-50f9-96dc-a711318feed1 | note | Hold/Witness Point Requirements: SEPD - V
72afa0e3-c281-5f11-b3b8-4bb5d94f9d1a | note | Hold/Witness Point Requirements: Client - NA
dc18306d-0de8-5103-b6cf-895ac6181c47 | note | Records or Checklist Document Number - WBS-SS-CI-ITP-920049
3a4c7c05-33fc-4957-81ea-4ca3f54a7582 | checkpoint | 3.5 - Compaction density ratio for backfill
12c26bf3-2458-57c5-943f-3363fb47d834 | note | Responsibility - SE/PE
2cdca4dc-fbd2-56cd-af4e-c14fe1bab472 | note | Specification Reference - WBS-SS-CI-SPC-0006
fd6a8930-3a68-5699-8ed9-8a57aca97eee | note | Conformance Criteria Summary - Compaction test report showing >95% MMDD
28152ca1-4fef-5098-b55f-8b4c48be7747 | note | ○ WBS-SS-CI-ITP-920049
91d23bee-d4fe-53ff-800a-c0ba0cc2477c | note | Method - T
31411ae6-0dcd-5a80-80bd-654ce4b51a1b | note | Frequency - PL
3450dcc8-078c-5db2-a693-1c443a4cbf1c | note | Hold/Witness Point Requirements: ROBAR - HP
7e8fcd6c-770d-5619-b9b1-2a5e2b4d7052 | note | Hold/Witness Point Requirements: SEPD - HP
9fa5fedc-4a8a-5484-a2fc-60c01f46cba4 | note | Hold/Witness Point Requirements: Client - NA
663d39cb-671e-5075-80fd-71a8cae9e4b2 | note | Records or Checklist Document Number - Test results
8cd80d5c-fa6e-4967-9cb2-f6f9c0920732 | signoff | HOLD POINT
e8c16635-b45e-4c56-b607-215fdda7422c | checkpoint | 3.6 - As-built survey pick-up
84038a20-0ebf-5a6a-bcc9-e6671409f289 | note | Responsibility - SE/PE
600aa93c-6cb1-50a8-abe6-eadef4b38657 | note | Specification Reference - WBS-SS-CI-SPC-0006 PPR
91ca7949-02ca-5221-a7a0-92a7ae2161b0 | note | Conformance Criteria Summary - Survey records and as-built drawings
ffed2b1f-d1c1-5b16-b480-878b148447c9 | note | Method - S
5aa38fab-3f35-502b-a0c6-22d74d64c547 | note | Frequency - PL
2821ad7c-99c5-5d59-a4b6-f7b729cb83f1 | note | Hold/Witness Point Requirements: ROBAR - V
749dd50e-2c5d-5911-a7d3-f801eea12e80 | note | Hold/Witness Point Requirements: SEPD - V
b629a5db-ef6a-598d-986b-db669e5ef242 | note | Hold/Witness Point Requirements: Client - NA
5c90e751-34a1-5012-b36f-0c2a703c9d59 | note | Records or Checklist Document Number - As-built drawings
075f1a4a-f63b-43bc-911b-723f305bfdc3 | section | Section 2: Final Inspection
788ddbc0-7039-439f-9f41-ad358963467d | checkpoint | 4.1 - Finish level compliance with design drawings
e386080f-081c-50ce-b494-3cd619518c7c | note | Responsibility - SE/PE
d2b0c26e-d63b-546c-b71b-0a3d5e9ee86e | note | Specification Reference - WBS-SS-CI-SPC-0006
855711b9-a553-5ab2-bfc3-725abca6aa4e | note | Conformance Criteria Summary - As-built drawings
bfb22895-b1ed-5cf8-a7ee-2cffcaf72ac6 | note | Method - S
705dc6df-4a60-586d-aa4b-43463be36596 | note | Frequency - PL
1d3ea53c-79d0-535c-9d68-ebcee0276881 | note | Hold/Witness Point Requirements: ROBAR - V
1da04910-6ffe-561d-840b-6185a9118ea8 | note | Hold/Witness Point Requirements: SEPD - V
3f8df9ae-e57d-550a-8f49-6311889eca20 | note | Hold/Witness Point Requirements: Client - NA
dd35270e-b32d-513f-9f84-e5f52eecd9ba | note | Records or Checklist Document Number - WBS-SS-CI-ITP-920049
cdc440b9-82d9-43c9-aa73-8eb04a07f916 | checkpoint | 4.2 - Final Inspection Checklist (FIC) completion
c7678f25-ac04-5dc5-8825-d38e0d46eb5a | note | Responsibility - SE/PE
335bce92-3836-5391-8dbc-775d69dd3a06 | note | Specification Reference - WBS-SS-CI-SPC-0006
34d66d2a-c656-52a5-a0cf-844951e8c9de | note | Conformance Criteria Summary - Signed FIC
eeda8ddd-b33b-5518-8112-a64d9f4e1807 | note | Method - R
0a18ebe4-6d71-5c51-82e8-505ab375d691 | note | Frequency - PL
cdde9182-5ad2-5dcd-a80f-3cf36daf18bb | note | Hold/Witness Point Requirements: ROBAR - V
e258f138-f9b3-583c-95af-cfef8c27a64f | note | Hold/Witness Point Requirements: SEPD - V
f661ca9c-3783-5572-b04d-46a41cb36c94 | note | Hold/Witness Point Requirements: Client - NA
f093581e-cd19-51d4-a8d8-75bbb1203ff7 | note | Records or Checklist Document Number - WBS-SS-CI-ITP-920049
2f4854da-23dd-49ca-b3ad-ca005807721b | section | Document Sign-off
b15c39b8-fb46-4c77-a0d3-eb28e7b22a7b | checkpoint | Close-out
13697973-3d1d-5a34-927e-c5a62a2be058 | textbox | SEPD - Name:
ba49da7f-b716-55aa-9546-51b5b90672ce | textbox | SEPD - Position:
58cd4340-6fff-5a01-99cf-4e196282bc5c | date | SEPD - Date:
8e54f05a-187e-45df-b04b-22c418cd40d6 | signoff | Add Signature
0e0c6570-300a-4cb1-b687-6f511348f05b | checklist | RR-SEPD-BESS-ITP-002-02 - Concrete slabs | itp | RR-SEPD-BESS-ITP-002-02 - Concrete slabs - Layer
d91b75fb-2922-473f-b447-f2474fe0faaa | section | Section 1: Concrete placement
bd6ac0f9-b080-4d76-ab6c-ae288768079f | checkpoint | 3.1 - Pre-pour concrete delivery inspection
f8b39c44-4ca6-5951-a24c-4e95bb5acaa2 | note | Responsibility - SE/PE
2ad44689-d242-57ca-bf88-0fdd60acaa63 | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 1379
5a0c8737-c154-5718-b885-5d3edfc2f066 | note | Conformance Criteria Summary - Batch delivery dockets match approved mix
96668dfc-a4a4-51ab-902f-e39cbe7fa872 | note | Method - I
a7d0f23e-245c-52a7-b20b-a69242f8f994 | note | Frequency - PL
4c364b81-4828-5a82-bb16-92f7817fd615 | note | Hold/Witness Point Requirements: ROBAR - WP
fd79ace6-3972-5d6d-a2ba-1efefccb7f0b | note | Hold/Witness Point Requirements: SEPD - WP
40507f8e-ade4-56c1-8d97-c70018165e09 | note | Hold/Witness Point Requirements: Client - NA
2f7bc74b-64f2-54ab-a1ba-f18dee18f39a | note | Records or Checklist Document Number - Delivery dockets
b54d4119-444e-46cd-9d08-7d8085a9e8a8 | checkpoint | 3.2 - Slump test at site (conformance to mix design)
de747406-436f-5961-b5d3-03898932de2d | note | Responsibility - SE/PE
acab73ee-0f2a-56fd-9f88-6a9f48820eb9 | note | Specification Reference - AS 1012
65f4aa4d-bb0d-5e36-b2e5-23d2a0ff61d7 | note | Conformance Criteria Summary - Slump within specified range (e.g., 100mm +/- 20mm)
e3b4777a-ab47-5cc9-97bf-9fc82c411c65 | note | Method - I
0f9236f4-ab8d-5cc4-8466-931781f7227e | note | Frequency - PL
f6d2dcdf-79b8-5850-ad96-ab4faed025a5 | note | Hold/Witness Point Requirements: ROBAR - HP
575c12e3-6be4-5b22-b5ed-bb9e5190d577 | note | Hold/Witness Point Requirements: SEPD - HP
b2733ba8-4c79-5c48-878a-2e6e89d7dc56 | note | Hold/Witness Point Requirements: Client - NA
5a7aadc7-bc3e-5cbe-9705-3673a779d04f | note | Records or Checklist Document Number - Lab test report
975b30c2-101a-4c50-bc3e-a4fbd4e005d3 | signoff | HOLD POINT
6dd6541f-207a-4133-9ba5-70fc44199bb4 | checkpoint | 3.3 - Concrete placement and compaction
5e112f03-e68a-5392-a69f-843d62038f46 | note | Responsibility - SE/PE
633c403d-aa39-59d3-9941-f8a03d038de0 | note | Specification Reference - WBS-SS-CI-SPC-0007
d60c8780-e496-5f8f-b20d-61126272d58a | note | Conformance Criteria Summary - Concrete placed within formwork, no segregation, fully compacted
d79622da-dd58-5cbc-8cc0-02bb085789ec | note | Method - T
259d53e1-2863-5be4-a96a-1aa36cbba1b5 | note | Frequency - PL
0802b771-d0d9-51f7-8b1a-0edf01f9eb92 | note | Hold/Witness Point Requirements: ROBAR - V
8712583e-ad8b-5e4d-b4e2-22178fc8ac58 | note | Hold/Witness Point Requirements: SEPD - V
c8ac6499-6bf4-533f-8824-6ffc4172f071 | note | Hold/Witness Point Requirements: Client - NA
b6121063-047d-5cea-9f1d-46dca9e69676 | note | Records or Checklist Document Number - Pour record
e6345b64-520a-424a-b091-c788b42bdc35 | checkpoint | 3.4 - Cylinder samples for compressive strength testing
ec3bffc4-6faa-5fdb-b15e-c3741acfe2ab | note | Responsibility - SE/PE
1fe84b2e-9a29-509e-8244-45c9b206638e | note | Specification Reference - AS 1012
d806c331-c457-5b92-a4b4-ac8cc52f8f8a | note | Conformance Criteria Summary - Minimum of 12 cylinders in total for 7, 14, 28-day tests
10fa576a-ab3c-5d0a-aa83-178422deebf6 | note | Method - I
cbf8fbf2-3f93-59d6-ad0c-4c5673d32707 | note | Frequency - PL
7d2112ca-8f78-5c62-82da-01016756f6fd | note | Hold/Witness Point Requirements: ROBAR - HP
3b129134-a3ce-5fda-9a3c-e8aaac27c13c | note | Hold/Witness Point Requirements: SEPD - HP
3dd15563-7c26-5420-9da6-fa1d66c323f3 | note | Hold/Witness Point Requirements: Client - NA
5be6af63-e816-5180-8aed-d91c7bd54390 | note | Records or Checklist Document Number - Lab test report
45937ee0-755c-46ea-9c23-8eb4e1e503b8 | signoff | HOLD POINT
d0d4dba8-d687-4a86-a731-3a126e5fd88e | checkpoint | 3.5 - Concrete temperature monitoring
d9f21a2d-5674-5421-b25a-6bce74f67a18 | note | Responsibility - SE/PE
a741d70a-1192-5aed-987a-c396452fba6a | note | Specification Reference - WBS-SS-CI-SPC-0007
c8fe1e39-00cf-54c4-a719-21f5d1f92640 | note | Conformance Criteria Summary - Temperature within acceptable range
c8da645a-00eb-5c5b-bc3b-5cdd23f2dda3 | note | Method - T
94a81f5d-f277-59ba-bcf3-6eb407d6a6fc | note | Frequency - PL
96f7d7f5-5c21-5a9e-b8f1-a794f02f2122 | note | Hold/Witness Point Requirements: ROBAR - HP
a2d9899d-1b3e-551e-bb85-a2353b0f53a4 | note | Hold/Witness Point Requirements: SEPD - HP
2f32b917-27fe-5b79-bc87-07496f48e316 | note | Hold/Witness Point Requirements: Client - NA
06c39e7a-a7fd-5674-a2ec-ec667c188c7b | note | Records or Checklist Document Number - Pour record
1597b5b4-f875-45ee-bd88-31f21912e974 | signoff | HOLD POINT
9a9e8fdc-e71c-4cff-a15b-d3aa44109cae | checkpoint | 3.6 - Placement monitoring – free- fall limit
fdb4f8f4-b6e0-501d-a10e-40c1498024e3 | note | Responsibility - SE/PE
9d7ebeb1-516e-599f-924b-50bca72e4aec | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 3600
32768342-5af1-54f7-9839-1ba498bff81c | note | Conformance Criteria Summary - Concrete poured with a maximum free-fall height of 1.8m to avoid segregation
29a31854-290c-5b3a-a28f-3b06a9fd6d0a | note | Method - T
7429ed1e-3729-5119-8c8d-e0a783e9e0ca | note | Frequency - PL
f06dce4a-29ee-53e0-a5f6-1faf537bc855 | note | Hold/Witness Point Requirements: ROBAR - V
a2e26af6-b960-5726-af35-fa0a074a131a | note | Hold/Witness Point Requirements: SEPD - V
1c527c74-95bd-5f3e-a6a2-26b2a2ae94b9 | note | Hold/Witness Point Requirements: Client - NA
edaaa740-4f53-5d44-a1fa-1b5482b4bc86 | note | Records or Checklist Document Number - FIC
da2ba581-3222-4c25-8552-bef73aadeb3d | checkpoint | 3.7 - Vibration and compaction monitoring
a38f60c3-3c06-50b6-8a6d-cbdcf01a049d | note | Responsibility - SE/PE
d6d792a6-5244-5ddc-8510-1ec817bbe75b | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 3600
3f01d66d-2c45-5782-a4f6-646b4faf8923 | note | Conformance Criteria Summary - Concrete properly compacted with vibrators, no voids or segregation
6a6f1e14-6cbf-5d59-a107-ec428e9cbeb9 | note | Method - T
8d036460-884b-53b3-ae81-2afb3136ea04 | note | Frequency - PL
c10b337e-59b8-5fb4-9289-d82714ae0900 | note | Hold/Witness Point Requirements: ROBAR - V
51a06a0f-ab0c-5be9-9727-73671f3ed1c5 | note | Hold/Witness Point Requirements: SEPD - V
9af94fa9-57b2-5654-87ec-f67addf7c35a | note | Hold/Witness Point Requirements: Client - NA
0c57dcae-72e2-579c-a4d9-84f6330284dd | note | Records or Checklist Document Number - FIC
d4769162-d2ef-4fd9-9e09-a9307143cb02 | checkpoint | 3.8 - Concrete curing
142806cd-fa84-5c60-9471-0e675971c93f | note | Responsibility - SE/PE
7ef5e448-ccd8-537f-b14b-86d42ec8b4df | note | Specification Reference - WBS-SS-CI-SPC-0007 FRP section 4.25.11 AS 3600
0eb0dac7-945d-5a84-af83-70bd28c7e5c2 | note | Conformance Criteria Summary - Concrete curing per approved concrete curing method statement
e0202387-6819-5814-8c27-fa54c3b3e2e9 | note | Method - T
d61b9875-2362-553f-9bed-4dee2a73baf0 | note | Frequency - PL
1d5aab0f-f7af-5e59-8d6d-15b949e1b9b3 | note | Hold/Witness Point Requirements: ROBAR - V
749ef53d-2796-5065-892f-768ccb8a3b39 | note | Hold/Witness Point Requirements: SEPD - V
efb3b021-ba05-5aeb-abed-1158c47cdfab | note | Hold/Witness Point Requirements: Client - NA
bb0928a0-a8ca-53fa-8eef-9c1dd560be14 | note | Records or Checklist Document Number - FIC
0fce9922-410e-41e0-a522-9a56897c0359 | section | Section 2: Final Inspection
6b2c6b91-fc8b-4c8e-a5b0-c03093a9ddcd | checkpoint | 4.1 - Surface finishing (Class of finish per AS 3610)
b2376cea-e273-5516-8f2b-3b7030aca2e2 | note | Responsibility - SE/PE
2e98a060-20c4-5176-a964-c1b95bc736b8 | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 3610
7f4fb86f-d7b7-5260-92fd-17e07b055acf | note | Conformance Criteria Summary - Class 5 finish for surfaces that are not visible after construction
702156b3-9252-5d0c-af6e-b17cdba54a77 | note | Method - S
bc7aa6db-3887-5e47-80f1-69a1be526331 | note | Frequency - PL
314e0ad7-0575-5312-903b-8b6d5ee75d58 | note | Hold/Witness Point Requirements: ROBAR - V
6e5746de-2bf7-58df-bc1e-8cc1b8d7d3bf | note | Hold/Witness Point Requirements: SEPD - V
38a257e5-3454-5b27-a76f-9854e1c15220 | note | Hold/Witness Point Requirements: Client - NA
69a7d7b0-7b7b-5ebc-8cb6-9df4e160f0f8 | note | Records or Checklist Document Number - FIC
cacb5021-9b66-4488-9f88-34bc4a86c48a | checkpoint | 4.2 - Curing procedure inspection
b3da11f3-0c35-59b4-b6fc-2f8ab77c9b68 | note | Responsibility - SE/PE
857b04a7-1824-5448-8067-cee8f258261c | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 3799
4b6537f4-2943-5f7c-8395-aef3fe510149 | note | Conformance Criteria Summary - Curing compound applied or wet curing in place
c1114067-78a0-546a-ae10-fd462b26242c | note | Method - R
d1306182-775b-5179-8584-a01f83c17c0e | note | Frequency - PL
225cd55e-e7b3-58c8-8df2-88fd0b1f1fea | note | Hold/Witness Point Requirements: ROBAR - V
59736eb5-1de1-5547-a281-668ac8d43872 | note | Hold/Witness Point Requirements: SEPD - V
5cb32a25-57a8-5b2c-9079-8e56b1dff107 | note | Hold/Witness Point Requirements: Client - NA
d2f9a708-37da-5983-ba15-6c5f487550ab | note | Records or Checklist Document Number - FIC
8bd48a35-4dfd-460a-a80a-82b5b408feb4 | checkpoint | 4.3 - Formwork stripping and post-pour inspection
c7d43e7a-8f9d-5093-8a4b-4d52e321f13e | note | Responsibility - SE/PE
fe81a14f-24f1-55d9-8a00-bfd5bb8bcdca | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 3610
852b2853-72f6-506d-98fa-8577e69f3c53 | note | Conformance Criteria Summary - Formwork removed at required strength, surface defects repaired
b8b3d43e-c038-5c94-9648-4636c1a9e025 | note | Method - R
9891ca5e-7ccb-5095-9720-d0e3e92df07a | note | Frequency - PL
fda86d00-3400-5903-8bb8-fb82c43a4023 | note | Hold/Witness Point Requirements: ROBAR - WP
85e96d13-2f5d-5f17-9507-b0b3fece3847 | note | Hold/Witness Point Requirements: SEPD - WP
0a4bd7b1-f33e-5730-ac11-612d5da9ef9d | note | Hold/Witness Point Requirements: Client - NA
75b70505-10e2-5d9b-9e25-7904a5df9da6 | note | Records or Checklist Document Number - FIC
7a2a3f79-c721-4d1e-b947-dc18d1f5a776 | checkpoint | 4.4 - Compressive strength test results
d9424698-e6e0-5ff7-9bfd-0e2c53e547ae | note | Responsibility - SE/PE
6ec2627f-8a97-5c03-af5a-019c415a48bc | note | Specification Reference - AS 1012
78c43181-4c63-5d3f-b231-1f9d99b1a146 | note | Conformance Criteria Summary - Compressive strength >32 MPa at 28 days
cca553e5-00e7-5383-9d91-a6d653cf8fa1 | note | Method - R
607b4b93-1450-5001-be97-b35ea35a03dd | note | Frequency - PL
94eaf632-b594-5c0b-9f3a-a4812d66b815 | note | Hold/Witness Point Requirements: ROBAR - HP
63c0599b-0391-5eea-bdcf-a9597d2f9a5b | note | Hold/Witness Point Requirements: SEPD - HP
5b762ccb-2aeb-56dc-bd68-f471fa2a718f | note | Hold/Witness Point Requirements: Client - NA
60e482d8-15b7-539f-8e9c-c18a26028d0e | note | Records or Checklist Document Number - Lab test report
d0aef6d6-2150-4101-8e0f-81db433cde14 | signoff | HOLD POINT
754cee9b-6ff9-4082-a63a-38db378a303c | checkpoint | 4.5 - Final inspection and acceptance of slab
19e7fb18-214c-57e6-9909-296009cfac42 | note | Responsibility - SE/PE
e1c03586-ca07-51c8-b828-2db389458790 | note | Specification Reference - WBS-SS-CI-SPC-0007
ec7f5f5f-009a-5e4d-9e8c-52a7b8cf27a3 | note | Conformance Criteria Summary - Surface levels, dimensions, and finish within tolerances
15729b03-188a-57a0-9a63-bbef6f700186 | note | Method - R
ab13780c-6628-5fc8-9c78-2de7863d1a8a | note | Frequency - PL
3e70de93-b5bc-54c4-95b9-8d8bfafa920b | note | Hold/Witness Point Requirements: ROBAR - V
e715a105-9bef-5711-9bd2-d3a852abb44e | note | Hold/Witness Point Requirements: SEPD - V
b544548c-1ee1-5e14-8f80-4e4da6d3aa3f | note | Hold/Witness Point Requirements: Client - NA
d9af8fda-c33d-5797-9eef-2fc4ed471e18 | note | Records or Checklist Document Number - FIC
6a4b7727-c31f-4f3f-9ffc-65e3a23434d7 | checkpoint | 4.6 - Joint Inspections
68f77389-68f1-537d-be80-4aedb6198137 | note | Responsibility - SE/PE
292252d4-ba6b-57b1-8d88-9430546fea3e | note | Specification Reference - WBS-SS-CI-SPC-0007
05331d1f-0998-5aba-92bd-37d3797a0095 | note | Conformance Criteria Summary - Expansion and contraction joints installed per design drawings
a4e1f2bb-de84-52a6-bd68-3ff6303ad730 | note | Method - R
238f8c81-da40-5b76-9223-e37dfafd3e04 | note | Frequency - PL
de8ca190-b7fa-55e2-b8d7-459808244d8b | note | Hold/Witness Point Requirements: ROBAR - V
1061bf03-34d5-529c-958d-26d20acbef6e | note | Hold/Witness Point Requirements: SEPD - V
a87ebd78-a4e2-56a6-af7f-12fd6ef0f031 | note | Hold/Witness Point Requirements: Client - NA
ec114ab5-f914-5cf2-ae93-ff224ac08977 | note | Records or Checklist Document Number - FIC
1635f63b-0b62-4c92-b120-68538e3f2114 | checkpoint | 4.7 - Post-cure inspections for shrinkage and cracking
779eed81-666d-5aee-bdfd-430a6de3d917 | note | Responsibility - SE/PE
10f54d9a-f47d-5f34-acff-0622826d9618 | note | Specification Reference - WBS-SS-CI-SPC-0007
6a2dbdf8-eac5-5d22-990d-a8a92ed97afd | note | Conformance Criteria Summary - Inspection for early shrinkage cracks and proper curing continuation
9a17d4a9-6bd9-5867-b4dc-9f8c7e0062b0 | note | Method - R
b48d1dfe-fa23-5409-b831-6e65898162b6 | note | Frequency - R
dea41777-1402-52ed-bc59-67ac9d610e5e | note | Hold/Witness Point Requirements: ROBAR - V
51576a8f-309d-52af-8afe-cb6b4ec9bfa4 | note | Hold/Witness Point Requirements: SEPD - V
e32cfdcc-1195-5c4d-9b08-a8a1f39587e1 | note | Hold/Witness Point Requirements: Client - NA
8d7d55ce-d725-57e0-99af-c380d3d2e264 | note | Records or Checklist Document Number - FIC
0f77a9d0-91bf-4c50-974a-5e4b817153d4 | section | Document Sign-off
285b1dfd-1fcc-480c-9911-3619506cb373 | checkpoint | Close-out
3982596a-a761-59db-ad28-1c2aeac32f1d | textbox | SEPD - Name:
6447d541-e5a2-5787-a5da-be793cb495a1 | textbox | SEPD - Position:
7b0724fa-534e-540a-8353-8dfc35931028 | date | SEPD - Date:
ac70b828-d2fc-45d5-9f27-d38c654d3ce1 | signoff | Add Signature
4a83d5a5-d96e-4a80-9be0-8bfaae6214b5 | checklist | RR-SEPD-BESS-QA-ITR-001-01 - Concrete Pour Record |  | RR-SEPD-BESS-QA-ITR-001-01 - Concrete Pour Record
ea74b003-0606-4ae1-af6b-a214e55f4c37 | section | Concrete Details
4c8e57af-2f8b-4d4c-bb4f-f9cbfe22e578 | checkpoint | Details
f5825e3d-fd11-5299-bc63-48e3abcf9781 | date | Date:
82afeed2-ccd5-5651-8fc1-01089bf2b8af | textbox | Premix Supplier and Plant:
a6e7cdec-ff43-5b4a-a8fc-34e973d97bc7 | textbox | Concrete/Grout Grade:
325ce011-a686-5b5b-acde-70b288016fc6 | textbox | Nominal Slump:
a84abc7b-403f-45b8-87a3-36961d9b3600 | section-nested-checklists | Concrete Pour Record