## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | 7d167250-1103-408d-bd17-8ab59cd3a826 |  | checklist | Townhouse Plumbing QA |  |  |  |  | Yes | Townhouse Plumbing QA | 0b446f66-cb82-44c7-8ec3-63e20a6623ad
checkpoint-group | 7d64568f-d9d3-454f-975d-06d55076b1e4 |  | section | First fix
checkpoint-status | 8a6c1339-fd89-4472-b6d0-ce668c1ac43d |  | checkpoint | Correct version of plans and revisions.
checkpoint-status | bcd50bf5-c376-470f-ac06-0fd7d389f748 |  | checkpoint | Check for correct fixtures/ client changes.
checkpoint-status | 2e7d32b3-9888-465f-a81d-374dafa0cc65 |  | checkpoint | Correct pipe size, material, class, level, grades and joints as per specs.
checkpoint-status | 0c5a40c1-8787-4332-9beb-20a7924bc827 |  | checkpoint | Hot water pipes run the shortest way possible and thermally lagged.
checkpoint-status | 285ddc83-d6ec-4bc1-b0e1-5d29134ef3bf |  | checkpoint | Specified waste pipework is acoustically lagged.
checkpoint-status | 6263812e-352d-4495-ba10-4cefa46241d9 |  | checkpoint | All joist brackets or reinforcements installed if required.
checkpoint-status | 901f5e11-a916-4e32-b237-1cfae8f2b074 |  | checkpoint | All nogs/fixings are installed.
checkpoint-status | d579f388-6378-4f0c-80fe-60883769ae11 |  | checkpoint | Check all wingback and wastepipe heights against the plans.
checkpoint-status | 7380d09c-6af4-4650-92cc-91e3bd63c483 |  | checkpoint | All pipework is clipped neatly, tidy and silicone.
checkpoint-status | 5a5d8ba0-11a6-4a1a-bd87-a372fd8e872b |  | checkpoint | All inspections and tests are complete including water to 1500kpa and wastepipe flood test.
checkpoint-status | 00f23d55-49e7-49aa-b38c-fd85c213506b |  | checkpoint | Waterpipes are left under working pressure and test gauge has been removed.
checkpoint-status | c5ecd90f-2a88-4a7a-86c2-a742306b1d5d |  | checkpoint | Area has been left clean and tidy.
checkpoint-status | 891cb54a-ba26-4735-8613-98eb5c6a2986 |  | checkpoint | Inspection has been completed.
checkpoint-group | ecc12a1a-80de-44d4-ae7a-5ea56b242a95 |  | section | Second fix
checkpoint-status | 505fbe2e-2a53-416e-9594-06d0b7b38d87 |  | checkpoint | Fit off fixtures match plan.
checkpoint-status | 2b5012e4-1e9a-41f7-959b-5870ea2111fe |  | checkpoint | All pipework has been flushed post pressure testing (Plumbing and drainage pipework). All commissioning completed.
checkpoint-status | f6d4151a-2998-4bce-a73f-79a4566f86d9 |  | checkpoint | No debris in floor wastes or stubs.
checkpoint-status | e3dfe13d-f708-4f35-a6a1-f988fda7d128 |  | checkpoint | The correct pipework has been used for the high temperature HWC drain.
checkpoint-status | b5cb3386-bd41-44b1-ac13-f27c38ebc399 |  | checkpoint | Flanges installed on all pipework.
checkpoint-status | 145eda1f-bbfe-4ade-8c40-c8f633a1e842 |  | checkpoint | All soil pipes are connected to sanitary sewer.
checkpoint-status | b2356770-88e0-422e-b78a-d179cce89f0f |  | checkpoint | No cross overs, hot on left and cold on right.
checkpoint-status | 870fef65-3a14-45c8-889f-e6fa7627c02d |  | checkpoint | All fixtures are silicone down and splash sealed.
checkpoint-status | a845ba1d-88c6-4286-8822-57387aafc2a4 |  | checkpoint | Area left clean and tidy.
checkpoint-status | 3f03d350-73b0-4f09-b6ef-52060595d7cf |  | checkpoint | Inspection completed.
checklist-flat | 5585ea3f-1185-4021-87fa-cb35a6d0834d |  | checklist | QA - Deck drains |  |  |  |  | Yes | QA - Deck drains | 0b91426b-f394-4999-bcd4-c908c21504bc
checkpoint-status | 95e6bbbb-1a65-42a3-a058-4b68222b1c5e |  | checkpoint | Pipework complete and connected to outlets
checkpoint-status | 0148da88-d6cf-4a87-b6c8-d0bb41b93759 |  | checkpoint | Flood test complete
checkpoint-status | cadf8906-c698-41f9-93ee-f66388ebe8da |  | checkpoint | Inspection passed
checkpoint-status | 44c15780-576e-423b-a7e4-62490599f4eb |  | checkpoint | Correct Pipe
checkpoint-status | bf4316dd-50b3-46a9-a534-696c93e992d1 |  | checkpoint | Correct Gradient
checkpoint-status | 277c461e-6b81-4283-a6c1-f44e9cce484a |  | checkpoint | Correct Brackets
checkpoint-status | 3141751c-3cee-4e3e-a80c-eebae2f7ac60 |  | checkpoint | Overflows moved into correct location
checklist-sectioned | 4de64a6d-a394-4e77-b936-8b8e147ead73 |  | checklist | Stormwater (Main Line) |  |  |  |  | Yes | Add Stormwater Mainline | 20a62461-a8bc-40f6-80b7-5b8485bc3d70
checkpoint-group | c29e82db-5e6e-42fb-8312-adaab8433f9d |  | section | Pipe Laying
checkpoint-status | c555e057-3f00-4ce6-8a24-1d790ebc2029 |  | checkpoint | Latest construction drawings referenced and followed
text | 5779bd30-d78a-4f5b-b70f-0df580ae4d89 |  | textbox | Drawing & Revision Number
checkpoint-status | 69f5badd-d755-4822-a31b-f0d8149116d5 |  | checkpoint | Setout & Excavation completed checked and accurate
checkpoint-status | 72639b77-ae08-411e-976d-a964ecfaf0bb |  | checkpoint | Ground conditions checked & acceptable
boolean | ba86ec5d-fd75-4f3a-b062-b9665e5910fc |  | tickbox | If ground is soft or uncertain - Notify Contractor
checkpoint-status | 8313c17a-bf79-487a-bce6-e2759f3d0348 |  | checkpoint | Bedding depth and material correct (photos & any relevant testing attached)
checkpoint-status | 0680da1f-bb61-421a-a31a-54ff28cab98f |  | checkpoint | Correct pipe (size, material & class) laid to specified level, grade and jointed as specified
text | 1d5d8ca2-0d90-4ca8-a258-a457c99d44fa |  | textbox | Start Invert Level
text | 10baae80-7cde-4468-82a7-2d94fa1767cb |  | textbox | Finish Invert Level
text | 58edff30-4c4c-47b3-88e7-fc9e8c34aaaa |  | textbox | length of pipe (m)
text | e5a03c88-0b91-49db-9d85-8eb876be37a5 |  | textbox | Grade of Pipe-Line %
checkpoint-status | 5d53e5c0-d037-4295-af6e-a790fe189546 |  | checkpoint | Connections to manholes complete, correct and approved
checkpoint-status | 58b0a68c-cb45-4a8c-b14c-eacd041ec188 |  | checkpoint | Relevant tests, photos & as-built information provided
checkpoint-group | c84db9ef-b5d1-464d-8e46-98480c033f75 |  | section | Backfill
checkpoint-status | 1df7dbfd-de63-45d5-a509-6f073adcbb64 |  | checkpoint | Backfill completed & compacted as specified
checklist-sectioned | c880ad41-0bd2-4d11-b01f-214abaf57b97 |  | checklist | Waste Water (Main Line) |  |  |  |  | Yes | Add Waster Water Mainline | 50cb3d21-fb63-43b1-8ba5-ca41d08ef05c
checkpoint-group | e8ca86b6-b62d-419e-8dfd-3c4aff0af2da |  | section | Pipe Laying
checkpoint-status | bf77c808-69f1-4b4c-9011-e6bf2314c17f |  | checkpoint | Latest construction drawings referenced and followed
text | 297e98e9-eb71-4dc1-85c5-7cb7ec256f2c |  | textbox | Drawing & Revision Number
checkpoint-status | 4bcb3e9b-1cbb-45e3-999b-0fdfaae15e3c |  | checkpoint | Setout & Excavation completed checked and accurate
checkpoint-status | 47a6d050-3800-48e9-9326-a54a12f24da9 |  | checkpoint | Ground Conditions Checked & Acceptable
boolean | 189075fe-d16f-46eb-bbc1-3ba3e4b95b04 |  | tickbox | If ground is soft or uncertain - Notify Contractor
checkpoint-status | 7f7a4b17-3d41-4ea7-aa22-4f8d84c7c76f |  | checkpoint | Bedding depth and material correct (photos & any relevant testing attached)
checkpoint-status | a289760c-f0f5-4f93-89f8-b94c8eaee033 |  | checkpoint | Correct pipe (size, material & class) laid to specified level, grade and jointed as specified
text | 3c6f48d6-aadd-44b1-abf4-6a5cf330c82f |  | textbox | Start Invert Level
text | af2d3333-7e37-4a51-a332-8c3b2bf78cc5 |  | textbox | Finish Invert Level
text | f4d73dc0-e286-4a25-aead-2d60e072becd |  | textbox | length of pipe (m)
text | 1ebf5efd-b32e-4f3f-a272-ab935f4e7a5f |  | textbox | Grade of Pipe-Line %
checkpoint-status | a7f8c7f4-9f0c-4882-8a18-dd24382f868d |  | checkpoint | Connections to manholes complete, correct and approved
checkpoint-status | 03deb6d2-9158-4ea9-97a6-495cea2e05eb |  | checkpoint | Relevant tests, photos & as-built information provided
boolean | c3deb9ca-a836-4833-bd1b-0993328d701f |  | tickbox | air/water test completed (photo of pressure gauge taken at START & FINISH)
checkpoint-group | 54f8daa8-d9bb-4add-954a-d95d6a9155c3 |  | section | Backfill
checkpoint-status | 21583bec-a3a3-47ab-9dc5-05f536f3da66 |  | checkpoint | Backfill completed & compacted as specified
checklist-sectioned | 07426c35-4b18-4951-b375-eca689177d72 |  | checklist | Manhole installation |  |  |  |  | Yes | Add Manhole | 5991d2f0-2c67-4c7c-92e0-cd57e6245972
checkpoint-group | c4d5d258-701f-48b0-b2c5-0bb5a1a68f13 |  | section | Manhole Install
checkpoint-status | 1877ba70-6e3a-470d-83a1-3eefb1da3f57 |  | checkpoint | Latest construction drawings referenced and followed
text | 318266e2-6cfe-4441-8fdf-2e507f0b4558 |  | textbox | Drawing & Revision Number
checkpoint-status | 13578ec3-b3ed-470a-a6c6-c179f6808698 |  | checkpoint | Setout & Excavation completed checked and accurate
checkpoint-status | 0700b786-79b7-408a-a252-5af95f655b30 |  | checkpoint | Ground Conditions Checked & Acceptable
boolean | d06c3b6a-edaf-43e4-99c7-e38033ed4364 |  | tickbox | If ground is soft or uncertain - Notify Contractor
checkpoint-status | bd0bad0a-4785-4bab-8ab7-ec5036815846 |  | checkpoint | Bedding depth and material correct (photos & any relevant testing attached)
checkpoint-status | a04b2fc1-8ec2-4b27-ab23-9c7c674557c5 |  | checkpoint | Correct manhole size installed to specified Invert Level
checkpoint-status | d994fc38-ad8d-45d0-99a9-484dd2807a7f |  | checkpoint | Manhole risers & steps installed and joints sealed as specified
checkpoint-status | be69ab0c-2930-4ab6-a7c1-95a5209cd296 |  | checkpoint | Manhole benching completed and acceptable
checkpoint-status | 2d882816-b285-4574-a741-4ecfc79dfb07 |  | checkpoint | Concrete manhole cover installed and sitting correctly (hole covered if required)
checkpoint-status | a639489b-af9f-4435-947e-167017d71765 |  | checkpoint | Cast Iron Lid installed and fixed at correct height
checkpoint-status | 148f7c79-a931-4974-9f4d-06b59b0d369f |  | checkpoint | Manhole Installation reviewed and approved (photos required)
checkpoint-group | 8172a6a6-e3e1-4ace-a699-efb2bb5118b3 |  | section | Backfill
checkpoint-status | d52c493d-f161-4829-862c-63ba17284ecd |  | checkpoint | Backfill completed & compacted as specified
checklist-flat | c70c2b8e-d1dc-4228-9daa-5113fdefbab9 |  | checklist | QA - Corridors |  |  |  |  | Yes | QA - Corridors | 76252b62-cb8b-48ba-831e-36abb221cd66
checkpoint-status | 570078ef-93db-4aca-a0a1-d92cef6a99af |  | checkpoint | Copper and Ke-kelit runs
checkpoint-status | 56449ce0-a7b8-4e7a-892b-2aa3f768abca |  | checkpoint | Correct version of plans and revisions
checkpoint-status | 310d7cb1-314b-455c-8221-3a1781151026 |  | checkpoint | Measurement of the way/grid line
checkpoint-status | a34da28c-e86e-4d2f-9377-f10389b1a246 |  | checkpoint | Height off floor level
checkpoint-status | 11716f41-26ef-45da-914c-342d0dc72d1e |  | checkpoint | Water meter position
checkpoint-status | db241687-3889-497c-a077-a454934bca66 |  | checkpoint | Seismic restraints fitted where needed
checkpoint-status | 8189acab-8820-4932-9cb7-c0477e668a92 |  | checkpoint | Check for fireproof paint on pipework
checkpoint-status | e8842e6f-7e2c-461a-be62-2b72ac34c73c |  | checkpoint | Pressure test complete
checklist-sectioned | f8c56a92-2d3d-40bc-80cc-cd7d0444e2ba |  | checklist | Basement |  |  |  |  | Yes | Basement checklist | 76721564-2be6-4ac4-83ce-b257402e6b66
checkpoint-group | 47de3db5-cb2f-4985-849e-f74fa852c648 |  | section | Stormwater
checkpoint-status | 66f4ce3d-1897-4304-9cf5-bdf345200fc2 |  | checkpoint | Correct drawings and revision
checkpoint-status | 11c70670-8bb6-4175-a6d7-dfe7ab9c90d7 |  | checkpoint | Setout completed, checked and accurate
checkpoint-status | 72037394-d3a5-4b78-8bc3-dd34777eb630 |  | checkpoint | Correct pipe size, material, class, level, grades and joints as per spec
checkpoint-status | bd155f7c-122d-479f-aa68-2aec7e2f06c2 |  | checkpoint | Correct support and brackets
checkpoint-status | e3dce7fb-bedf-4060-af71-c4fd2ee98ab9 |  | checkpoint | Correct Seismic bracing as per spec
checkpoint-status | a31c2ac1-aa8d-44fb-ba3f-0aadf2878c4f |  | checkpoint | Testing completed as per specs
checkpoint-status | a38ba9b5-debb-479f-9e95-dbd8ab73b233 |  | checkpoint | All open end of pipes protected and covered
checkpoint-status | 5be69d78-1a73-46af-bb50-490244ced891 |  | checkpoint | Any clashes with other services checked
checkpoint-status | 6f53d427-eb7c-42c6-a98a-ee603b5c5834 |  | checkpoint | Pipework identification and labels applied
checkpoint-status | 3976ea0c-01a0-4669-88ed-00420c604e99 |  | checkpoint | Area left clean and tidy
checkpoint-group | e9f7a7ad-c325-452e-89f7-bd19b93fea1b |  | section | Sewer
checkpoint-status | 5cee44fb-92b0-4f08-9856-1fe912bcbc3d |  | checkpoint | Correct drawings and revision
checkpoint-status | 5de11d90-f5e0-46a1-90a0-eac4431b5e36 |  | checkpoint | Setout completed, checked and accurate
checkpoint-status | 83e98673-e369-490b-95a8-55fdec2cf7e5 |  | checkpoint | Correct pipe size, material, class, level, grades and joints as per spec
checkpoint-status | 1643030a-bb43-40ff-b257-c0c382fb1f64 |  | checkpoint | Correct support and brackets
checkpoint-status | 7634f14e-aa38-4e1b-ab6a-14fb847d5ca9 |  | checkpoint | Correct Seismic bracing as per spec
checkpoint-status | f85b0554-5763-4c27-b1c5-edd96e9be9b0 |  | checkpoint | Testing completed as per specs
checkpoint-status | 4dc67e80-d59d-4efe-bc11-a31aa3547910 |  | checkpoint | All open end of pipes protected and covered
checkpoint-status | 13bba1fe-6f95-4301-8844-862cbe4b1e81 |  | checkpoint | Any clashes with other services checked
checkpoint-status | f41104ec-8857-4489-9726-076c9f636b88 |  | checkpoint | Pipework identification and labels applied
checkpoint-status | 933b2917-29c9-4674-8d3b-53e40f576d50 |  | checkpoint | Area left clean and tidy
checkpoint-group | cdeef541-644f-4d01-b1a9-fd752d628708 |  | section | Watermain
checkpoint-status | a58b9d00-5b17-41b4-8a7a-a222c3415778 |  | checkpoint | Correct drawings and revision
checkpoint-status | 4a06adfb-c571-460a-8a4b-2b3901f378e2 |  | checkpoint | Setout completed, checked and accurate
checkpoint-status | 4ceef594-5ae5-4fc8-9cc7-d7d11c21275b |  | checkpoint | Correct pipe size, material, class, level, grades and joints as per spec
checkpoint-status | 70f4aafa-ccff-4f77-90e8-48322e6ec99f |  | checkpoint | Correct support and brackets
checkpoint-status | c2330d47-8de0-408e-957b-112d4f0614fa |  | checkpoint | Correct Seismic bracing as per spec
checkpoint-status | 33cc105f-d478-4c38-9349-8affdd88f07f |  | checkpoint | Testing completed as per specs
checkpoint-status | aafcd082-26a9-4174-99e8-3f247faec00d |  | checkpoint | All open end of pipes protected and covered
checkpoint-status | a0f40fa5-6898-4623-88c3-877e2f3f69dc |  | checkpoint | Any clashes with other services checked
checkpoint-status | 2d77f714-a700-43a3-b7be-d8ae2bedff99 |  | checkpoint | Pipework identification and labels applied
checkpoint-status | a0a68faf-5f8e-449b-8065-2b8b17c34df4 |  | checkpoint | Area left clean and tidy
checkpoint-group | 653e24c4-0ba8-4c1d-b7f9-bcde481a6558 |  | section | Inspection
checkpoint-status | 3a4141ca-3ec3-44a9-bdf7-2f48a7286d55 |  | checkpoint | Council Inspection completed
checklist-sectioned | 4f712004-f2a9-460e-aaf3-b393062bbca2 |  | checklist | Townhouse Plumbing QA |  |  |  |  | Yes | Townhouse Plumbing QA | 79baeed9-c828-4623-a7de-33baafb0c967
checkpoint-group | 86a98804-ae55-41d6-a5ae-5796e6a0c239 |  | section | First fix
checkpoint-status | bd3e7153-f489-4788-a50a-712d3f830159 |  | checkpoint | Correct version of plans and revisions.
checkpoint-status | f84d9bc7-5abb-441f-a942-d68d79dc48d7 |  | checkpoint | Check for correct fixtures/ client changes.
checkpoint-status | c93e0bc6-b29e-41f7-8169-083f140f9abf |  | checkpoint | Correct pipe size, material, class, level, grades and joints as per specs.
checkpoint-status | 27b85fa7-3855-492a-9def-b23ed61f7ea8 |  | checkpoint | Hot water pipes run the shortest way possible and thermally lagged.
checkpoint-status | e3334851-d0ce-4b9f-be89-8b2820086bb2 |  | checkpoint | Specified waste pipework is acoustically lagged.
checkpoint-status | ff90f03f-c60c-43ea-808c-50dc9a408dab |  | checkpoint | All joist brackets or reinforcements installed if required.
checkpoint-status | cdddb161-7950-4d4d-8eb4-62681a879c11 |  | checkpoint | All nogs/fixings are installed.
checkpoint-status | 008526e6-2e0a-413f-8595-1a073d09ab46 |  | checkpoint | Check all wingback and wastepipe heights against the plans.
checkpoint-status | eba2775f-7cf6-499e-81c4-f172df159e05 |  | checkpoint | All pipework is clipped neatly, tidy and silicone.
checkpoint-status | d9f0fb66-8aa6-4fe1-b532-b9e8c7098f21 |  | checkpoint | All inspections and tests are complete including water to 1500kpa and wastepipe flood test.
checkpoint-status | aa6f0e92-3f1c-48db-b747-2d7f3c57e8cd |  | checkpoint | Waterpipes are left under working pressure and test gauge has been removed.
checkpoint-status | ec971af1-fcc9-424f-8a92-2157a7ba5ac8 |  | checkpoint | Area has been left clean and tidy.
checkpoint-status | 8fba847a-54cb-49ec-96c0-54632b8c0e1e |  | checkpoint | Inspection has been completed.
checkpoint-group | fd6d573e-199a-450e-906b-8b97b242fe70 |  | section | Second fix
checkpoint-status | 844a3e46-c912-4f08-8e7f-cfc3ef010acf |  | checkpoint | Fit off fixtures match plan.
checkpoint-status | a0a323f7-3486-4312-84e0-8360be02b882 |  | checkpoint | All pipework has been flushed post pressure testing (Plumbing and drainage pipework). All commissioning completed.
checkpoint-status | 1cb295d3-e260-4913-b364-7636fb3a38e0 |  | checkpoint | No debris in floor wastes or stubs.
checkpoint-status | 105fe1f9-b84f-4764-9f9e-472cc6d143d6 |  | checkpoint | The correct pipework has been used for the high temperature HWC drain.
checkpoint-status | cdbba5ef-1b54-4d56-b69d-99a4fc2445d9 |  | checkpoint | Flanges installed on all pipework.
checkpoint-status | b4c33dff-c219-4103-abbb-e5d6d681ecf9 |  | checkpoint | All soil pipes are connected to sanitary sewer.
checkpoint-status | 5732278d-cfc6-4f92-99db-d3cca8a0c915 |  | checkpoint | No cross overs, hot on left and cold on right.
checkpoint-status | b482fc74-8704-4246-8a71-2e3cda3af797 |  | checkpoint | All fixtures are silicone down and splash sealed.
checkpoint-status | 7291ee2a-4034-42c3-af18-099cf06d1c54 |  | checkpoint | Area left clean and tidy.
checkpoint-status | c360b490-e7e1-4c41-ac62-bec4bb4c08ec |  | checkpoint | Inspection completed.
checklist-flat | 98fdde99-1769-429b-aa3f-03652d9732ed |  | checklist | First fix - Apartments |  |  |  |  | Yes | First fix - Apartments | a05f4668-2ee5-4d04-b114-cd0cc4cd09d7
checkpoint-status | b5761464-0c41-4220-a7c0-5e7a2c761247 |  | checkpoint | Correct version of plans and revisions.
checkpoint-status | a9ff91ed-a646-44e2-97bb-474f73c06d47 |  | checkpoint | Unit type and unit location.
checkpoint-status | 8f843f8f-efda-4e3e-97d9-19bf13aa1181 |  | checkpoint | Inside - 2m blue cable, 600mm copper, 1m clear tube.
checkpoint-status | 50134a5b-d80c-4d89-ab88-f69fb7dde7f5 |  | checkpoint | Outside - 3m blue cable, 2m copper twin.
checkpoint-status | ffea407e-22c7-44ad-bcc5-056ccb416c85 |  | checkpoint | Check measurements off the plan for high wall location of unit and copper.
checkpoint-status | 164a581d-8897-487c-9000-d7a237a84864 |  | checkpoint | Condensate line complete and sturdy and has fall.
checkpoint-status | ae09f99f-f696-4822-bb47-b29be5217942 |  | checkpoint | Lagging of condensate line, minimum of first 1m.
checkpoint-status | 451af1bc-9ec1-449c-926d-bf4fceffdbd6 |  | checkpoint | Check correct copper pipe size.
checkpoint-status | a7105d87-b9b7-4621-a16e-63b192f6c07c |  | checkpoint | Check connection of the clear tubing.
checkpoint-status | fb13e54f-df1f-42c8-82d6-5982553a1a98 |  | checkpoint | Check the line is under pressure and on test.
checklist-flat | bb679ef2-0bf5-4def-af70-ce41dd122ba2 |  | checklist | Inspection Reports |  |  |  |  | Yes | Inspection Reports | aecbbf6a-a509-48a7-b500-40e65503e3fc
checkpoint-no-status | 99d68970-f356-4bf9-9762-4302c4a6b84e |  | checkpoint | Inspection Reports
checklist-flat | 36481e1d-ba40-41aa-a0bb-7be224be4ef5 |  | checklist | First fix - Townhouses |  |  |  |  | Yes | First fix - Townhouses | b424053f-eadc-4a1d-bceb-90befa15c048
checkpoint-status | e644a670-0002-4c96-93dc-c383d0b0bf67 |  | checkpoint | Correct version of plans and revisions.
checkpoint-status | 572ab0a3-454f-4ffb-8348-8cb5d88880b4 |  | checkpoint | Unit type and unit location.
checkpoint-status | d1287f63-b9fa-4832-a907-2c002b3f73a0 |  | checkpoint | Inside - 2m blue cable, 600mm copper, 1m clear tube.
checkpoint-status | db515f38-eefc-4c01-95ab-d2ffbfe41aba |  | checkpoint | Outside - 3m blue cable, 2m copper twin.
checkpoint-status | 1936faa6-0ea3-4f31-b1cc-3933afdbc1b2 |  | checkpoint | Check measurements off the plan for high wall location of unit.
checkpoint-status | 1155ed3c-8c7e-41b8-aa52-a802c09631f0 |  | checkpoint | Check correct copper pipe size.
checkpoint-status | c325fe70-a174-42cb-9a4e-6b6a92965976 |  | checkpoint | Check connection of the clear tubing.
checkpoint-status | 43986e38-0505-429f-8821-ca02f2545ac9 |  | checkpoint | Check the line is under pressure and on test.
checkpoint-status | 2eb3232a-bdf7-4c82-a7c4-0af0715b0bd5 |  | checkpoint | Ducting all installed and correct location and clear of obstacles for grill install.
checkpoint-status | 5b3ca0f6-5d67-4fd7-88b7-a6d82df85e9e |  | checkpoint | Check the condensated line discharges outside and to the correct location.
checklist-flat | d66d2787-28bb-4f9d-96dd-e4b1654176f1 |  | checklist | Issues/Clashes |  |  |  |  | Yes | Issues/Clashes | b558837f-0cda-409b-80d6-5ae7e628bf8c
checkpoint-no-status | 7dc18c40-e196-4cd4-bda7-4730e79f57c4 |  | checkpoint | Issues/Clashes
checklist-sectioned | e0d3dc4d-7041-42c0-8118-b866b5e29b1e |  | checklist | Plumbing checks Area: |  |  |  |  | Yes | Plumbing QA | be4abe98-1493-4b7f-abb1-0f26aedd9c30
checkpoint-group | 43258d31-d75e-4c8f-af55-c440049aee81 |  | section | First Fix
checkpoint-status | c80feee1-5f87-4be2-a591-6bf062d4e41b |  | checkpoint | Area acceptable to begin work
checkpoint-status | ff4dc195-1275-425e-abf7-dbed2ca905a4 |  | checkpoint | Check correct version of plans/shop drawings
checkpoint-status | 704a47eb-d0a3-4774-b9c1-f6ca51d95201 |  | checkpoint | Check for correct fittings/client changes
checkpoint-status | 668862c2-e80c-40c4-b13f-5c2353306d92 |  | checkpoint | Fiot water supply lines run the shortest
checkpoint-status | ba84023b-c7c0-4047-ac59-5f261b8dd3d7 |  | checkpoint | Specified Waste pipework is Acoustic Lagged
checkpoint-status | d508dc1f-e31f-427e-89cb-dc6306679f2f |  | checkpoint | Penetrations through fire cells are fire protected
checkpoint-status | ad7e2c3d-96f7-4e34-81bf-1aac11be2947 |  | checkpoint | All joist Brackets or Reinforcement installed if required
checkpoint-status | b2111410-fd55-491a-9e94-4988b7202379 |  | checkpoint | Nog's and fixings are installed for WC, WHB, SFIW, FIWC?
checkpoint-status | 775cf627-8a16-40da-8f16-fa06e62a239b |  | checkpoint | Penetrations through building paper are trade sealed
checkpoint-status | a002ac77-c5b4-4cc3-af0c-16ba2056af9d |  | checkpoint | Hot Water Ring main is thermally lagged
checkpoint-status | f2dc2f9b-d09a-4203-8f4b-5127523cdd7e |  | checkpoint | Check wingback heights against schedule including FIWC
checkpoint-status | ccae6912-6c77-44e1-9d3f-c490e45b2458 |  | checkpoint | All Pipework clipped neatly and tidy
checkpoint-status | a07fb237-a1c0-4310-b3c0-623542ea6480 |  | checkpoint | All pipework secured/ siliconed
checkpoint-status | 2e2d7ae3-3f07-4a70-8d9c-3b3dbb861595 |  | checkpoint | FWG Flange is recessed into flooring and installed
checkpoint-status | 0eb454ca-af93-4461-be42-52b03ac09ac8 |  | checkpoint | Check waste pipes for height and position (flush pipe)
checkpoint-status | fde93b10-f969-478e-9b9a-f5bfe6b2852c |  | checkpoint | Water tested to 1500kpa and loop not effect lining
checkpoint-status | 6a2f5da5-9ec6-4061-90ec-7da96cc51a3d |  | checkpoint | Checked for drips on water and waste piping
checkpoint-status | fc1ef5cf-9ffa-4abe-be37-8daf99a71969 |  | checkpoint | Picked up all left over material and removed from site
checkpoint-status | 5a655262-311e-4e81-931d-2de83aa316f3 |  | checkpoint | Soil and waste piping hydrostatic test ( Flood test )
checkpoint-status | 42999b71-5e91-4e87-bd4d-ac1f2213c066 |  | checkpoint | Test plug & Guage removed from pipe system
checkpoint-status | 9fdc25ae-0949-4307-a3cf-59a7686db007 |  | checkpoint | Fire penetration Schedule is completed
checkpoint-status | c7775ab8-c1b0-42b3-80d2-63e7d9500fa8 |  | checkpoint | First Fix completed as required (photos attached)
checkpoint-group | 81a5969b-339a-4593-8847-8046b2864e64 |  | section | Second Fix
checkpoint-status | 335728c6-561d-493d-ab52-398eb615719a |  | checkpoint | Area acceptable to begin work
checkpoint-status | 72a69caa-01ea-4a52-aa42-c22abc5991cd |  | checkpoint | Fit-off Materials match schedule on plans
checkpoint-status | d1fec1d3-9bdf-4ef1-8841-4830ee49366b |  | checkpoint | Setouts/min clearances as per plan
checkpoint-status | 85a375a9-ebf6-4814-a953-a58dfb23044a |  | checkpoint | Water pipework maintained test throughout
checkpoint-status | 505add7e-67f8-4b87-8e3e-d349fdbfe2e2 |  | checkpoint | No debris in floor wastes or stubs
checkpoint-status | f0a7eebe-b275-4e6f-ae8a-2568abfda3d2 |  | checkpoint | HWC Tempered to required outlet temp
checkpoint-status | 11ba77ab-63bd-41fc-a2b4-864e2f57292d |  | checkpoint | Flanges installed on all pipework to vermin proof
checkpoint-status | eb0b1b9f-e008-49e8-8995-75705226390d |  | checkpoint | All soil pipes are connected to sanitary sewer
checkpoint-status | 06cff9fe-56c4-480c-ba09-86f6092b0991 |  | checkpoint | No crossovers, Flot on left and Cold on Right
checkpoint-status | 93332284-ef06-4c9d-a1cb-8fb2409162be |  | checkpoint | All fixtures are silicon-ed down and splash sealed
checkpoint-status | ed72b5ad-388b-4adb-b154-b18c2e5052da |  | checkpoint | Shower Floses are fitted with non returns
checkpoint-status | 287220ab-5e5f-45ff-be71-549201df84fc |  | checkpoint | Second Fix completed as required (photos attached)
checklist-flat | cd5e73b1-b24f-4e93-930e-8cfadfff2df0 |  | checklist | Gas Line |  |  |  |  | Yes | Gas Line | bf330cb1-403a-47bc-88a7-5b4e39cef112
checkpoint-status | 601da57f-5592-4f0f-8b9e-6375ef903d9b |  | checkpoint | Correct drawings and revision
checkpoint-status | 391543a6-c0e2-407c-8aca-3eb72151911a |  | checkpoint | Setout completed, checked and accurate
checkpoint-status | a0f199c7-cd01-4f1e-9878-1018ec7ef718 |  | checkpoint | Correct pipe size, material, class, level, grades and joints as per spec
checkpoint-status | c6b54817-f8db-433e-8640-a568b3440631 |  | checkpoint | Correct support and brackets
checkpoint-status | 20bbd7f7-cc81-4d40-827f-a7faf6555b00 |  | checkpoint | Correct Seismic bracing as per spec
checkpoint-status | 01dee395-3559-41b0-8c13-3c9dfe54aa5f |  | checkpoint | Testing completed as per specs
checkpoint-status | 755122ba-2ecb-49bd-8a47-549488c99b0c |  | checkpoint | All open end of pipes protected and covered
checkpoint-status | 02b49fd8-c065-4766-a058-9760bda17959 |  | checkpoint | Any clashes with other services checked
checkpoint-status | 663fd275-6433-43fc-b976-d19de4c26430 |  | checkpoint | Pipework identification and labels applied
checkpoint-status | dbb2e4b9-bced-48a5-8d7f-cb9744671a0d |  | checkpoint | Area left clean and tidy
checklist-flat | a81eb96e-de23-4c98-bf5a-9fff99ba4c2a |  | checklist | Name: |  |  |  |  | Yes | Install Specs | c4d2cf29-da68-46e0-b29c-4112bbdec47c
checkpoint-no-status | 3854df91-6ab8-458b-a302-ecb349b6db6c |  | checkpoint | Attach install specifications here
checklist-flat | 5f30b656-62a3-4d5b-834e-ed5bac4c3ee9 |  | checklist | Second fix townhouses |  |  |  |  | Yes | Second fix townhouses | c564a21c-630a-429a-bec3-d4c65b52fea7
checkpoint-status | 8ca75085-8b23-4d4b-a7bc-4cc44c67d49b |  | checkpoint | Check the grills on the vents are installed and finished.
checklist-sectioned | 4df2b293-e4e9-4d52-812a-d4463a3b7a87 |  | checklist | Water Main |  |  |  |  | Yes | Add Water Main | fc30b860-440b-4110-972b-b0c5bced7ec0
checkpoint-group | 10a9d1a7-da0f-4f4d-b907-01a8c6a0347f |  | section | Pipe Laying
checkpoint-status | 92bcef2b-ec6d-41b8-82a1-ef85fa7dfd25 |  | checkpoint | Latest construction drawings referenced and followed
text | 0f138cd7-12bd-4b7d-914a-f5f5dbbafb3e |  | textbox | Drawing & Revision Number
checkpoint-status | d5421fba-d7dd-48bb-b90a-4ac9b718ed7a |  | checkpoint | Setout & Excavation completed checked and accurate (minimum cover considered)
checkpoint-status | 1eccad3e-69f7-47ea-babe-e93c51178550 |  | checkpoint | Ground Conditions Checked & Acceptable
boolean | 04500950-f19d-4d68-a282-7f7021397a5f |  | tickbox | If ground is soft or uncertain - Notify Contractor
checkpoint-status | e565f854-8233-4e1f-b41d-6e581f6fcf52 |  | checkpoint | Bedding depth and material correct (photos & any relevant testing attached)
checkpoint-status | 5097e76f-7815-4b23-8fae-2a8b4152d3ab |  | checkpoint | Correct pipe (size, material & class) laid to specified level, grade and jointed as specified
text | 2c861f10-eb95-43ab-b0c6-3abef57259f3 |  | textbox | Length of pipe section (m)
checkpoint-status | 64be2f60-6442-4bc8-8036-e9ef37e49144 |  | checkpoint | All connections complete, correct and approved (photograph of each connection required)
checkpoint-status | e6b07ea4-bdd7-41d0-aa1f-4e5ea5814f87 |  | checkpoint | Relevant tests, photos & as-built information provided
checkpoint-group | 704b5ac4-ad31-4e87-bcb4-23462df9d8ce |  | section | Backfill
checkpoint-status | 26365925-b8d2-4549-bb21-239d08ad728e |  | checkpoint | Backfill completed & compacted as specified