## Street Light
|  |  |  | Construction Process: Installation of 2 streetlights | Start RP |  | INSPECTION AND TEST PLAN - VERSION CONTROL |  |  | A | B | C | 0 - IFC
[5 empty] | Finish RP |  | Prepared by Pavement Designer: |  | PE name | dd/mm/yy
|  |  |  | Project Name: Pakira Place and SH1 Streetlight installs |  |  | Reviewed by Construction Manager: |  | PM name | dd/mm/yy
[7 empty] | Reviewed by Surf./ Pavmt Manager: |  | Surfacing or Pavement Manager | dd/mm/yy
Client's Rep. : Neil Payne / Deena Tapara (Stellar Projects Ltd. (SPL) |  | Contractor's Rep. : Wayne Bowden (CM) / Sid Rudani (PM) |  | Specifications: Project Specification Activity: Street Light |  |  | Approved Quality Manager.: |  | Nominated by Group Quality Manager | dd/mm/yy
[7 empty] | Approved by: Pavements SME.: |  | Responsible Group SME | dd/mm/yy
[7 empty] | Issued by: Project Director |  | PE name | dd/mm/yy
Item | Task/Activity/Description | Inspection/Test |  |  |  | Acceptance Criteria | Record documents (QCP - Quality Control Portal | Responsibility | Project Specific Notes / Instructions | Checked by R = Responsible, I, Informed, A = Approve
|  | Detail of Activity / Test | Action (Hold, Monitor, Witness) | Minimum Test Frequency | Inspection / Test method |  |  |  |  | Designer | Eng. Rep / NZTA | Contractor | Date
1.0 Setout and Preparation
1.01 | Job Safety & Environmental Analysis | Install 2 streetlight and upgrade 2 Luminaires on exsisting streetlights. | H | Daily | NA | Method Statement and JSEA Completed and signed by relevant authority. | JSEA | Contractor | Job Safety & Environmental Analysis to be provided to Engineer for review prior to commencing excavation on site. | I | I | A | dd/mm/yy
1.02 | Method Statement Development | Supplyn and Install 2 new streetligh coloums and Cables as per Lighting design. | H | Once | NA | Method Statement completed and signed by relevant authority. | MS | Contractor | Method Statement provided to Engineer for review prior to commencing excavation on site. | I | I | A | dd/mm/yy
1.03 | Drawings and Specifications | Check drawings are for construction and latest revision. Check Specification is for construction and latest revision | H | As per lighting design | NA | Drawings and Specification are the latest revision. | IFC Drawings and Specification | Contractor | Up to date drawings and specification to be reviewed before construction. | I | I | A | dd/mm/yy
1.04 | Power Connection | Ensure power supply is organised and is undertaken by an experience and competent contractor. | M | Power supply to the new lights will be installed by Direct earth and conected to the existing streetlight circuit. Conections will be carried out by an Diret Earth OS1010 agent. | Visual Inspection | Unison to supply power to streetlight bases, contractor connecting streetlights to the network to be "approved" by the local electricity network company. | increase in load Documents. | Contractor | This will be submited to NZTA and the network provider. | I | I | A | dd/mm/yy
1.05 | Survey Set Out | GPS Setout of the shared services trench location as per the construction drawings. | M | Setout location prior to commencing works | Visual Inspection | Streetlight set out locations do not clash with other features (i.e. existing/new services etc) | Contractor's site diary and/or photos | Contractor | Post Installation SAT report will be submitted to downer and Ramm update will be subimtted to NZTA for this work. DEL will submit update drawing to surveyor for construction drawings. | I | I | A | dd/mm/yy
2.0 Construction and Finshing
2.01 | Pole | Assembly - Poles will be spliced togeather on site prior to installtion. | M | each pole | Visual Inspection | Confirmation by contractor/installer of correct assembly per manufacturers instructions. | Photo | Contractor | the poles arrive in section and will be built on site by Direct Earth | I | I | A | dd/mm/yy
2.02 |  | Installation - this will be installed once ground stubs are set | M | each pole | Visual Inspection | Ensure poles are plumbed vertical. Confirmation by contractor/installer of correct installation to manufacturers specification by contractor/installer. | QC - SAT and Photos | Contractor | Installation to be done by Direct earth LTD using Manufactures specifications. | I | I | A | dd/mm/yy
2.03 |  | Type - elliptical with 2.5meter outreaches | M | each pole | Visual Inspection | Ensure the correct pole type is installed per the latest IFC drawings. | Check sheet | Contractor | pole ordered as per specification | I | I | A | dd/mm/yy
2.04 |  | Footings - 2.4meter shear base | M | each pole | Visual Inspection | Ensure poles are founded securely and have are adequatley backfilled to suit site conditions. Confirmation by contractor/installer of correct installation to manufacturers specification by contractor/installer. | Check sheet and Photos | Contractor | As per Installation Specifications. | I | I | A | dd/mm/yy
2.05 |  | Earthing - earthing to be installed by direct earth. | M | each pole | Visual Inspection - Electrical test | Confirmation by contractor/installer that all streetlights are earthed per installation requirements. | COC Sheet | Contractor | earthing to be installed during installation, new earth electrode and MEN link at each location. | I | I | A | dd/mm/yy
2.06 | Luminaire | Type - ITALo 2 LED | M | each luminaire | Visual Inspection | Ensure the correct luminaire type is installed per the latest IFC drawings. | Check sheet | Contractor | these luminaires are as per NZTA specifications | I | I | A | dd/mm/yy
2.07 |  | Tilt Angle - 0deg | M | each luminaire | Visual Inspection | Ensure the correct luminaire tilt angle is installed per the latest IFC drawings. +/-1O | Check sheet | Contractor |  | I | I | A | dd/mm/yy
2.08 | Electrical Testing | Test relevant - ESC / COC and ROI required | H | each pole | Electrical Testing | Confirmation by contractor/installer that streetlights and circuits have been satisfactorily tested in accordance with Electrical (Safety) Regulations 2010. | COC Sheet/ ROI | Contractor | test to be completed prior to hand over by a qualified electrician with OS1010 certification. | I | I | A | dd/mm/yy
2.09 | Electrical certificate of compliance and electrical safety certificate | Complete COC | H | minimum once per Zone | Inspection / Audit | Submit COC. | COC Sheet / ROI | Contractor | To be submitted once works complete | I | I | A | dd/mm/yy
3.0 Post Construction
3.01 | Collate above documentation | Document review | H | Each ITP | Review | All above documentation is shown as attached to this work pack. | Review | Contractor |  | I | I | A | dd/mm/yy
3.02 | As-built drawings | Survey | H | At completion of construction | Asbuilts to be submitted at the completion of construction, information to be captured regularly. | Asbuilts reviewed and submitted (i.e. showing final location of all poles). | In Eight record | Contractor | All As builts to be submitted from DEL | I | I | A | dd/mm/yy
Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance. | [6 empty] | H | Hold Point | Work Shall not proceed past the HP until released by the Eng. Rep.
Contractor's Rep Name:__Dylan Baxter___________________________________________ |  |  | Signature:__Dylan Baxter__________________________________ |  |  | Date: _26-09-2025____________________________ | W | Witness Point | An Inspection which must be witnessed by the Eng. Rep.
Engineer's Rep. Name:____________________________________ |  |  | Signature:____________________________________ |  |  | Date: _____________________________ | M | Monitor Point | Intermittent monitoring of any stage of the work in progress by the Eng. Rep.

## Sheet1
1. Pre-Construction Design Approval: Confirm approved drawings and specifications. Product Acceptance: Ensure all materials (precast units, pipes, grates) are on the Acceptable Products List. 2. Excavation & Base Preparation Excavation: Check excavation is to correct line, level, and dimensions. Foundation: Inspect for suitable subgrade; if unsuitable, ensure remedial works are completed. Base: Confirm correct bedding material and compaction. 3. Catchpit Installation Placement: Ensure catchpit is placed at correct location, orientation, and level. Alignment: Check inlet/outlet pipe connections for correct alignment and seal. Jointing: Inspect all joints for watertightness. 4. Backfilling Material: Use approved backfill material. Compaction: Backfill in layers and compact to specified density. Protection: Protect catchpit from damage during backfilling. 5. Surface Works Grate & Frame: Install to correct level (flush with finished surface or as specified). Surround: Ensure concrete surround (if required) is to specification. 6. Final Inspection Cleaning: Remove debris from inside catchpit. Functionality: Confirm free flow of water through catchpit and pipes. Finish: Check for damage, correct installation, and compliance with drawings. 7. Documentation As-Built Records: Submit as-built plans and inspection records. Checklist: Complete and sign the RITS Stormwater Catchpit Checklist.