## SSMH Installation
Sewer Manhole Installation
1 | Pre-Establishment | Select One | Inspection Type | Comments
1.1 | If the work is under a consent, has the pre-commencement meeting with the relative council been completed and approval to start works issued? | Y/N/NA | HP
1.2 | Has the site Geotech report been reviewed to identify soil types and ground water level? | Y/N/NA | IP
1.3 | Has the trenching and installation methodology been confirmed to cater for the ground conditions? | Y/N/NA | IP
1.4 | Is the SSSP been witnessed by the client | Y/N/NA | WP
1.5 | Has the JSEA been completed and witnessed? | Y/N | WP
1.6 | Have the IFC drawings been issued | Y/N/NA | HP
1.7 | Send all IFC drawings and design files to the surveyor for site set-out requirements | Y/N/NA | HP
2 | Pre-Excavation | Select One | Inspection Type | Evidence
2.1 | Site is set-up and work area is fenced off before excavations start | Y/N | IP | Attach Photos
2.2 | Check service plans for any underground assets that may come in contact with trenching operations and all plans are on site. | Y/N | HP | Attach Photos
2.3 | Are there any services within your excavation area? | Y/N | IP | Attach Photos
2.4 | If 'Yes' to the above; have the services been marked out and located? | Y/N | IP | Attach Photos
2.5 | If there is a high-value or high-risk service (Power/Gas/Stategic Fibre), has the asset been located by hand digging or hydrovac excavation? | Y/N | HP | Attach Photos
2.6 | Have all required materials been delivered to site and inspected for damage prior to installation? | Y/N | IP | Attach Photos
2.7 | Has survey set-out been completed? | Y/N | IP | Attach Photos
2.8 | Have all persons involved in the work been inducted onto the site? | Y/N | IP | Attach Photos
2.9 | Has the JSEA been signed by all persons involved in the works? | Y/N | IP | Attach Photos
2.1 | Has all plant and machinery been established to site? | Y/N | IP | Attach Photos
2.11 | Have all pre-start checks been completed on the plant and machinery being used for the job? | Y/N | IP | Attach Photos
3 | Excavation & Foundation | Select One | Inspection Type | Evidence
3.1 | Excavation completed to line and level as per survey set-out | Y/N | IP | Attach Photos
3.2 | Ground conditions checked and subgrade tested to ensure competent substrate before laying. Soft sports to be raised with PM for further instruction. | Y/N | HP | Attach scala sheet
3.3 | If required, complete undercut as per engineers' instruction and take photos. | Y/N/NA | IP | Attach Photos
3.4 | Place and compact granular foundation as per drawings | Y/N | IP | Attach Photos
4 | Sewer Manhole Install | Select One | Inspection Type | Evidence
4.1 | Install MH structure to the line and level as indicated by the design making allowances for benching thickness and internal inverts. | Y/N | IP | Attach Photos
4.2 | Make pipe connections to manhole to line and invert level detailed on the approved drawings and record as-built invert levels. | Y/N | IP | Attach Photos and record invert levels
4.3 | Remove burs on cut pipe
4.4 | Complete concrete corbel connections to outside of MH on all main connections | Y/N | IP | Attach Photos
4.5 | Form concrete benching inside manhole and ensure that benching is not flatter than 1 in 3 and haunching of intersecting pipes provide curved channel to ensure streamlined flow. | Y/N | IP | Attach Photos
4.6 | Install stainless steel manhole safety steps and epoxy the back of the bolts and around the base of the step penetrations. | Y/N | IP | Attach Photos | Install manhole steps
4.7 | Install MH riser rigns, additional steps, mahole sealing strip and seal each riser with epoxy on both sides of the manhole riser joint. | Y/N | IP | Attach Photos
4.8 | Leak test manhole and confirm that the structure of the manhole is not leaking. | Y/N | IP | Attach Photos Record leak test results and attach
4.9 | Backfill manhole excavation and compact in layers and test | Y/N | IP | Attach Photos & Scala Sheet
4.1 | Install concrete manhole lid and casting | Y/N | IP | Attach Photos
4.11 | Once pavement layers have been placed to height, raise steel castings and throats to height and check throat depth is no more than 350mm.
4.12 | Once pavement has been constructed and all vibratory activities completed; complete all sealing work around manhole lid with expoxy | Y/N | IP | Attach Photos
4.13 | Complete all internal plastering work and expoxy sealing on the benching, pipe penetrations and riser rings to ensure that the manhole is leak proof. | Y/N | IP | Attach Photos
4.14 | Install bungs on all pipe inlets and outlets and perform preliminary leak test on manhole. | Y/N | IP | Attach Photos Record leak test results and attach
4.15 | Complete leak test under witness from a council inspection engineer. | Y/N | WP | Attach Photos Record leak test results and attach
4.16 | Paint steel casting 'white' as per TCC requirements | Y/N | IP | Attach Photos
4.17 | Complete final visual inspection with Engineer & Council Inspector | Y/N | WP | Attach Photos
4.18 | Complete as-builts and submit to engineer | Y/N | IP | Submit electronic as-built
4.19 | If connecting to existing line; complete council connection application form and have the responsible drainlayer sign the form | Y/N | HP | Submit completed form to the engineer