## Table 1
Item # | Activity Descrption |  | Inspection / Test Method |  | Acceptance Criteria |  | Frequency |  |  | Verifying Documents |  |  | Inspection Point | [8 empty] | Comments
[13 empty] | Sub Contractor |  |  | Head Contractor |  |  | Engineer / Client
1 |  |  |  |  | PRELIMINARY / GENERAL
1.1 | Subgrade testing |  | Beam testing / proof rolling or scala |  | Consistent with design assuptions. |  | Prior to construction |  |  | Test results |  |  | H |  |  | H |  |  | R |  |  | Required to confirm assumed CBR.
2 | [6 empty] | MATERIALS
2.1 | Sub Base |  | Production testing to NZS 4407 |  | Max particle size lesser of 65mm or 40% of layer depth. and no more than 8% by mass of material shall pass the 150 micron sieve. The CBR value should not be less than 60 - and minimum crushing resistance of 100kN. |  | 1 test prior to placement |  |  | IANZ Lab report |  |  | H |  |  | — |  |  | R |  |  | —
2.2 | Base Course |  | TNZ M/4 |  | Compliance with TNZ M/4. Refer to Table 5 in the M/2 specification for detailsfor "Napier River Run". |  | 1 test per 500m3 prior to placement |  |  | IANZ Lab report |  |  | H |  |  | — |  |  | R |  |  | —
2.3 | Ashphaltic concrete surfaceing |  | TNZ M/10 |  | Job mix formula |  | Prior to placement |  |  | Mix design |  |  | H |  |  | H |  |  | R |  |  | —
2.4 | Chip seal |  | TNZ M/01, P/3 & M/06 |  | Job mix formula |  | Prior to placement |  |  | Mix design |  |  | H |  |  | H |  |  | R |  |  | —
2.5 | Concrete |  | NZS 3109 |  | 25MPa concrete at 28 days. |  | — |  |  | — |  |  | H |  |  | H |  |  | R |  |  | —
2.6 | Vehicle crossings |  | NZS 3109 |  | 30MPa concrete at 28 days |  | — |  |  | — |  |  | — |  |  | — |  |  | R |  |  | —
2.7 | Kerb and channel, nibs and dish channels |  | NZS 3109 |  | 20MPa concrete at 28 days |  | — |  |  | — |  |  | — |  |  | — |  |  | R |  |  | —
2.8 | Traffic signs and name plates |  | "Standard for the manuafacture and maintenace of traffic signs, post and fittings" - NZTA |  | Compliance with the standard. |  | — |  |  | — |  |  | — |  |  | — |  |  | R |  |  | —
2.9 | Road marking paint |  | TNZ M/7 |  | Compliance with the standard. |  | — |  |  | — |  |  | — |  |  | — |  |  | R |  |  | —
3 |  |  |  |  | SUB BASE CONSTRUCTION
3.1 | Topsoil stripping |  | Inspection |  | Prior to any fill, all organic topsoil mterials are removed. |  | Prior to fill. |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  | —
3.2 | Surface finish and levels. |  | Survey / string lines at 10m centres. |  | Surface finish in accordance with TNZ F/1, section 11 |  | Prior to fill. |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  | —
3.3 | Density testing |  | Nuclear densometer to NZS 4407 Test 3.7 - 20m intervals staggered between lanes. |  | 95% SMDD mean, 92% minimum |  | Prior to basecourse placement. |  |  | IANZ Lab report |  |  | H |  |  | H |  |  | R |  |  | —
3.4 | Sub base surface finish |  | TNZ B/2 |  | Visual inspection - tight mosaic finish. |  | Prior to placement of bascourse |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  | —
4 |  |  |  |  | BASECOURSE CONSTRUCTION
4.1 | Basecourse finished level setout |  | Survey / string lines at 10m centres |  | +15mm / -5mm vertical from sub base design surface. |  | Prior to basecourse placement. |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  | —
4.2 | Density testing |  | Nuclear densometer to NZS 4407 Test 3.7 - 20m intervals staggered between lanes. |  | 98% SMDD mean, 95% minimum |  | Prior to surfacing. |  |  | IANZ Lab report |  |  | H |  |  | H |  |  | R |  |  | —
4.3 | Beam testing |  | TNZ T/1 |  | Average: 1.5mm, Maximum 1.8mm |  | Prior to surfacing. |  |  | Test results. |  |  | H |  |  | H |  |  | R |  |  | —
4.4 | Surface finish |  | TNZ M/4 |  | Visual inspection |  | Prior to surfacing. |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  | —
5 | [6 empty] | ASHPHALT SURFACING
5.1 | Ashphaltic concrete finished level setout |  | Survey / string lines |  | 10m centres, 3m straight edge. |  | Prior to surfacing |  |  | +10mm / -0mm from finished design. |  |  | H |  |  | H |  |  | W |  |  | —
6 | [6 empty] | CHIP SEAL SURFACING
6.1 | Chip Seal finished level setout |  | Survey / string lines |  | 10m centres, 3m straight edge. |  | Prior to surfacing |  |  | +10mm / -0mm from finished design. |  |  | H |  |  | H |  |  | W |  |  | —
7 |  |  |  |  | FOOTPATH AND VEHICLE CROSSINGS
7.1 | Setout |  | Survey / string lines |  | +15mm / -5mm vertical from sub base design surface. |  | Prior to pour. |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  | —
7.2 | Basecourse compaction |  | Clegg |  | Mimimum 25. |  | Prior to pour. |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  | —
8 | KERB AND CHANNEL, NIB, DISH CHANEL
8.1 | Setout |  | Survey / string lines |  | +15mm / -5mm vertical from sub base design surface. |  | Prior to pour. |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  | —
8.2 | Basecourse compaction |  | Clegg |  | Mimimum 35. |  | Prior to pour. |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  | —
9 | [6 empty] | ROAD MARKING
9.1 | Road marking paint |  | Mark out on site |  | Mark out dimensionally in conformance with the design. |  | Prior to application of paint |  |  | Engineer approval. |  |  | H |  |  | H |  |  | S |  |  | —
10 | [6 empty] | CLOSEOUT
10.1 | Collate and supply Producer Statements / Waranty Schedules |  | Document review |  | Collate and supply producer statements |  | Upon completion of bulk roadworks |  |  | Producer statements |  |  | H |  |  | H |  |  | H |  |  | —
10.2 | Collate and supply as builts |  | Documate review / as builts |  | Collate and supply as-builts. |  | Upon completion of roadworks |  |  | As-builts |  |  | — |  |  | H |  |  | S |  |  | —
Inspec ion and Test Plan STORMWATER
Item # | Activity Descrption |  | Inspection / Test Method |  |  | Acceptance Criteria | Frequency |  |  |  | Verifying Documents |  |  | Inspection Point | [9 empty] | Comments
[14 empty] | Sub Contractor |  |  | Head Contractor |  |  | Engineer / Client
1 | [6 empty] | PRELIMINARY / GENERAL
1.1 | Consents and trench opening notices |  | Document review |  |  | Authority approvals. | Prior to excavation |  |  |  | Approval from relevant authorities. |  |  | — |  |  | — |  |  | R |  |  |  | —
1.2 | Drainlayer registration |  | Document review |  |  | Certification | Prior to drain laying works. |  |  |  | Scanned copy |  |  | — |  |  | — |  |  | R |  |  |  | —
2 | [6 empty] | MATERIALS
2.1 | Concrete pipes |  | Document review |  |  | New and in good condition and compliant with AS/NZS4058 reinforced cast rubber ring jointed, class 2 uless otherwise noted. | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.2 | PVC pipes |  | Document review |  |  | New and in good condition and compliant with AS/NZS1254 or AS/NZS1260 rubber ring jointed, minimum SN8, (unless noted otherwise) | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.3 | Precast chambers |  | Document review |  |  | Compliant to AS/NZS4058, with concrete lids designed to HN- HO-72 traffic loadings in roads. | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.4 | Access covers and frames |  | Document review |  |  | Removable with a clear opening >600mm (except for non-access MHs). Designed to minimum AS 3996 Class D or better. | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.5 | Sump grates |  | Document review |  |  | Complaince with HDC ECoP. | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.6 | Concrete Wing wall |  | Document review |  |  | Compliance with NZS 3109 with surface finishes to | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.7 | Backfill material |  | — |  |  | — | — |  |  |  | — |  |  | — |  |  | — |  |  | — |  |  |  | —
2.7.1 | Bedding haunching and overlay. |  | Inspection |  |  | 5-14mm clean washed granualr mix. | Prior to placement. |  |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  |  | —
2.7.2 | Fill to subbase |  | Inspection |  |  | AP65 of other approved imported material. | Prior to placement. |  |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  |  | —
3 | [6 empty] | CONSTRUCTION
3.1 | Set out |  | Document review. |  |  | Survey setout information in accordance with the design. | Prior to excavation. |  |  |  | Survey file. |  |  | — |  |  | — |  |  | R |  |  |  | —
3.2 | Trenching |  | Site inspection. |  |  | Trench widths ok and no unsuitable materials present. Min widths: pipe dia DN75 - DN150 = 350mm width, pipe dia DN150 - DN300 = 450 - 600mm width, pipe dia DN300 - DN400mm = 700 - 850mm width. | Prior to pipe laying |  |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  |  | —
3.3 | Pipe laying |  | Survey |  |  | Record level of main upstream and downstream of each chamber. Maximum discrepancy +- 10% of design gradient, and maximum +-15mm from design level. | Prior to backfill. |  |  |  | Survey as builts |  |  | — |  |  | — |  |  | R |  |  |  | —
3.4 | Chambers / sumps / wingwalls |  | Survey / site inspection. |  |  | Benching in accordance with specifcations and drawings. Position in accordance with the design | Prior to backfill. |  |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  |  | —
3.5 | Pipe bedding / haunching /overlay |  | Document review site inspection. |  |  | In accordance with AS/NZS 2566 for PVC pipelines and AS/NZS 3725 for concrete pipelines. Bedding minimum 100mm up to 450 diamter pipe and 150mm pipes > 450mm. For PVC overlay >100mm over pipe and for concrete 1/3 diamter of pipe. | Prior to backfill. |  |  |  | Photos or site inspection. |  |  | H |  |  | H |  |  | W |  |  |  | —
3.6 | Backfill |  | Clegg every 10m alignment for each layer of backfill (not exceeding 200mm) |  |  | Minimum 20 Clegg reading | Prior to placement of each layer of backfill. |  |  |  | Test records. |  |  | H |  |  | H |  |  | W |  |  |  | —
3.7 | Hydrostatic testing |  | Document review site inspection. |  |  | In accordance with NCC CoP and Engineer specification | After backfill/prior to road seal. |  |  |  | Test records and Council inspection records. |  |  | H |  |  | H |  |  | H |  |  |  | —
3.8 | CCTV |  | Document/video review |  |  | In accordance with NCC CoP and Engineer specification | After backfill/prior to road seal. |  |  |  | Test records and Council inspection records. |  |  | H |  |  | H |  |  | H |  |  |  | —
4 | [6 empty] | CLOSEOUT
4.1 | Collate and supply Producer Statements / Waranty Schedules |  | Document review |  |  | Collate and supply producer statements | Upon completion of stormwater works. |  |  |  | Producer statements |  |  | H |  |  | H |  |  | H |  |  |  | —
4.2 | Collate and supply Council inspection reports. |  | Document review. |  |  | Collate and supply Council inspection reports. | Upon completion of stormwater works. |  |  |  | Inspection records. |  |  | H |  |  | H |  |  | S |  |  |  | —
4.3 | Collate and supply compaction records. |  | Document review. |  |  | Collate and supply compaction records. | Upon completion of stormwater works. |  |  |  | Inspection records. |  |  | H |  |  | H |  |  | S |  |  |  | —
4.4 | Collate and supply as builts / CCTV inspections / water tests |  | Document review / as builts |  |  | Collate and supply as-builts and inspection records. | Upon completion of stormwater works. |  |  |  | As-builts |  |  | H |  |  | H |  |  | S |  |  |  | —
1 | [5 empty] | PRELIMINARY / GENERAL
1.1 | Consents and trench opening notices |  | Document review |  |  | Authority approvals. | Prior to excavation |  |  |  | Approval from relevant authorities. |  |  | — |  |  | — |  |  | R |  |  |  | —
1.2 | Drainlayer registration |  | Document review |  |  | Certification | Prior to drain laying works. |  |  |  | Scanned copy |  |  | — |  |  | — |  |  | R |  |  |  | —
2 | [6 empty] | MATERIALS
2.1 | PVC pipes |  | Document review |  |  | New and in good condition and compliant with AS/NZS1254 or AS/NZS1260 rubber ring jointed, minimum SN8, (unless noted otherwise) | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.2 | Precast chambers |  | Document review |  |  | Compliant to AS/NZS4058, with concrete lids designed to HN-HO-72 traffic loadings in roads. | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.3 | Access covers and frames |  | Document review |  |  | Removable with a clear opening >600mm (except for non-access MHs). Designed to minimum AS 3996 Class D or better. | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.7 | Backfill material |  | — |  |  | — | — |  |  |  | — |  |  | — |  |  | — |  |  | — |  |  |  | —
2.7.1 | Bedding haunching and overlay. |  | Inspection |  |  | 5-14mm clean washed granualr mix. | Prior to placement. |  |  |  | — |  |  | H |  |  | H |  |  | W |  |  |  | —
2.7.2 | Fill to subbase |  | Inspection |  |  | AP65 of other approved imported material. | Prior to placement. |  |  |  | — |  |  | H |  |  | H |  |  | W |  |  |  | —
3 | [6 empty] | CONSTRUCTION
3.1 | Set out |  | Document review. |  |  | Survey setout information in accordance with the design. | Prior to excavation. |  |  |  | Survey file. |  |  | — |  |  | — |  |  | R |  |  |  | —
3.2 | Trenching |  | Site inspection. |  |  | Trench widths ok and no unsuitable materials present. Min widths: pipe dia DN75 - DN150 = 350mm width. | Prior to pipe laying |  |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  |  | —
3.3 | Pipe laying |  | Survey |  |  | Record level of main upstream and downstream of each chamber. Maximum discrepancy +- 10% of design gradient, and maximum +-15mm from design level. | Prior to backfill. |  |  |  | Survey as builts |  |  | — |  |  | — |  |  | R |  |  |  | —
3.4 | Pipe bedding / haunching /overlay |  | Document review site inspection. |  |  | In accordance with AS/NZS 2566 for PVC pipelines. For PVC overlay >100mm over pipe. | Prior to backfill. |  |  |  | Photos or site inspection. |  |  | H |  |  | H |  |  | W |  |  |  | —
3.5 | Backfill |  | Clegg every 10m alignment for each layer of backfill (not exceeding 200mm) |  |  | Minimum 20 Clegg reading | Prior to placement of each layer of backfill. |  |  |  | Test records. |  |  | H |  |  | H |  |  | W |  |  |  | —
3.6 | Hydrostatic testing |  | Document review |  |  | In accordance with AS/NZS 3500.2 section 15.2 | Prior to backfill. |  |  |  | Test records and Council inspection records. |  |  | H |  |  | H |  |  | H |  |  |  | —
3.7 | CCTV |  | Document/video review |  |  | In accordance with AS/NZS 3500.2 2018 section D1 | After backfill/prior to road seal. |  |  |  | Test records and Council inspection records. |  |  | H |  |  | H |  |  | H |  |  |  | —
4 | [6 empty] | CLOSEOUT
4.1 | Collate and supply Producer Statements / Waranty Schedules |  | Document review |  |  | Collate and supply producer statements | Upon completion of wastewater works. |  |  |  | Producer statements |  |  | H |  |  | H |  |  | H |  |  |  | —
4.2 | Collate and supply Council inspection reports. |  | Document review. |  |  | Collate and supply Council inspection reports. | Upon completion of wastewater works. |  |  |  | Inspection records. |  |  | H |  |  | H |  |  | S |  |  |  | —
4.3 | Collate and supply compaction records. |  | Document review. |  |  | Collate and supply compaction records. | Upon completion of wastewater works. |  |  |  | Inspection records. |  |  | H |  |  | H |  |  | S |  |  |  | —
4.4 | Collate and supply as builts / CCTV inspections / water tests |  | Document review / as builts |  |  | Collate and supply as-builts and inspection records. | Upon completion of wastewater works. |  |  |  | As-builts / test records. |  |  | H |  |  | H |  |  | S |  |  |  | —
WATER SUPPLY Project: Parklands Subdivision Revision: 0 Job number: Date: 25/08/2025 Client: Napier City Council
Item # | Activity Descrption |  | Inspection / Test Method |  |  | Acceptance Criteria |  | Frequency |  |  |  | Verifying Documents |  |  | Inspection Point | [9 empty] | Comments
[15 empty] | Sub Contractor |  |  | Head Contractor |  |  | Engineer / Client
1 | [7 empty] | PRELIMINARY / GENERAL
1.1 | Consents and trench opening notices |  | Document review |  |  | Authority approvals. |  | Prior to excavation |  |  |  | Approval from relevant authorities. |  |  | — |  |  | — |  |  | R |  |  |  | —
1.2 | Installer registration |  | Document review |  |  | Certification |  | Prior to drain laying works. |  |  |  | Scanned copy |  |  | — |  |  | — |  |  | R |  |  |  | —
2 | [7 empty] | MATERIALS
2.1 | PVC pipes |  | Document review |  |  | New and in good condition and compliant with AS/NZS1477 (min PN9) |  | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.2 | PE pipes |  | Document review |  |  | New and in good condition and compliant with AS/NZS1430 (min PN12.5) |  | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.3 | Precast chambers |  | Document review |  |  | Compliant to AS/NZS4058, with concrete lids designed to HN- HO-72 traffic loadings in roads. |  | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.4 | Access covers and frames |  | Document review |  |  | Removable with a clear opening >600mm (except for non-access MHs). Designed to minimum AS 3996 Class D or better. |  | Prior to order |  |  |  | Technical documents. |  |  | — |  |  | — |  |  | R |  |  |  | —
2.5 | Backfill material |  | — |  |  | — |  | — |  |  |  | — |  |  | — |  |  | — |  |  | — |  |  |  | —
2.5.1 | Bedding haunching and overlay. |  | Inspection |  |  | 5-14mm clean washed granualr mix. |  | Prior to placement. |  |  |  | — |  |  | H |  |  | H |  |  | W |  |  |  | —
2.5.2 | Fill to subbase |  | Inspection |  |  | AP65 of other approved imported material. |  | Prior top placement. |  |  |  | — |  |  | H |  |  | H |  |  | W |  |  |  | —
3 | [7 empty] | CONSTRUCTION
3.1 | Set out |  | Document review. |  |  | Survey setout information in accordance with the design. |  | Prior to excavation. |  |  |  | Survey file. |  |  | — |  |  | — |  |  | R |  |  |  | —
3.2 | Trenching |  | Site inspection. |  |  | Trench widths ok and no unsuitable materials present. Min widths: pipe dia DN75 - DN150 = 350mm width. |  | Prior to pipe laying |  |  |  | Engineer approval. |  |  | H |  |  | H |  |  | W |  |  |  | —
3.3 | Pipe laying |  | Survey |  |  | Alignment +-50mm from design, surface cover in accordance with HDC ECoP. |  | Prior to backfill. |  |  |  | Survey as builts |  |  | — |  |  | — |  |  | R |  |  |  | —
3.4 | Pipe bedding / haunching /overlay |  | Document review site inspection. |  |  | In accordance with AS/NZS 2566 for PVC pipelines. For PVC overlay >100mm over pipe. |  | Prior to backfill. |  |  |  | Photos or site inspection. |  |  | H |  |  | H |  |  | W |  |  |  | —
3.5 | Pressure test |  | Inspection. |  |  | In accordance with section C3 of NZS4404 and AS/NZS 2556. To a pressure no less than 800kPa and no greater than 25% above the rated pressure of the pipeline. |  | Prior to backfill over joints and fittings wherever possible. |  |  |  | Test records. |  |  | H |  |  | H |  |  | W |  |  |  | —
3.6 | Backfill |  | Clegg every 10m alignment for each layer of backfill (not exceeding 200mm) |  |  | Minimum 20 Clegg reading |  | Prior to placement of each layer of backfill. |  |  |  | Test records. |  |  | H |  |  | H |  |  | W |  |  |  | —
3.7 | Disinfection |  | Inspection. |  |  | Carried out in accordance with NCC ECoP (amended appendix D of NZS4404:2010. |  | Prior to connectioun to mains supply |  |  |  | Test records. |  |  | H |  |  | H |  |  | W |  |  |  | —
4 | [7 empty] | CLOSEOUT
4.1 | Collate and supply Producer Statements / Waranty Schedules |  | Document review |  |  | Collate and supply producer statements |  | Upon completion of Water supply works. |  |  |  | Producer statements |  |  | H |  |  | H |  |  | H |  |  |  | —
4.2 | Collate and supply Council inspection reports. |  | Document review. |  |  | Collate and supply Council inspection reports. |  | Upon completion of water supply works. |  |  |  | Inspection records. |  |  | H |  |  | H |  |  | S |  |  |  | —
4.3 | Collate and supply compaction records. |  | Document review. |  |  | Collate and supply compaction records. |  | Upon completion of water supply works. |  |  |  | Inspection records. |  |  | H |  |  | H |  |  | S |  |  |  | —
4.4 | Collate and supply as builts / CCTV inspections / water tests |  | Document review / as builts |  |  | Collate and supply as-builts and inspection records. |  | Upon completion of water supply works. |  |  |  | As-builts / test records. |  |  | H |  |  | H |  |  | S |  |  |  | —
Inspection and Test Plan SERVICE TRENCHING AND DUCTING
Item # | Activity Descrption | Inspection / Test Method |  | Acceptance Criteria |  |  |  |  | Frequency | Verifying Documents |  |  |  |  | Inspection Point | [7 empty] | Comments
[15 empty] | Sub Contractor |  | Head Contractor |  | Engineer / Client
1 |  |  |  | PRELIMINARY / GENERAL
1.1 | Consents and trench opening notices | Document review |  | Authority approvals. |  |  |  |  | Prior to excavation | Approval from relevant authorities. |  |  |  |  | — |  | — |  | R |  |  |  | —
2 | [8 empty] | MATERIALS
2.1 | PVC ducts | Document review |  | New and in good condition and compliant. |  |  |  |  | Prior to order | Technical documents. |  |  |  |  | — |  | — |  | R |  |  |  | —
2.2 | Chambers / pits | Document review |  | ACO type pits with class D covers in accordance with the specifications. |  |  |  |  | Prior to order | Technical documents. |  |  |  |  | — |  | — |  | R |  |  |  | —
2.3 | Backfill material | — |  | — |  |  |  |  | — | — |  |  |  |  | — |  | — |  | — |  |  |  | —
2.3.1 | Bedding haunching and overlay. | Inspection |  | 5-14mm clean washed granualr mix. |  |  |  |  | Prior to placement. | — |  |  |  |  | H |  | H |  | — |  |  |  | —
2.3.2 | Fill to subbase | Inspection |  | AP65 of other approved imported material. |  |  |  |  | Prior top placement. | — |  |  |  |  | H |  | H |  | — |  |  |  | —
3 | [8 empty] | CONSTRUCTION
3.1 | Set out | Document review. |  | Survey setout of chambers / pits in accordance with the design - marked on site |  |  |  |  | Prior to excavation. | Survey file / site inspection. |  |  |  |  | — |  | — |  | R |  |  |  | —
3.2 | Trenching | Site inspection. |  | Trench widths ok and no unsuitable materials present. Min widths: pipe dia DN75 - DN150 = 350mm width. Min covers in accordance with the specifications. |  |  |  |  | Prior to pipe laying | Engineer approval. |  |  |  |  | — |  | — |  | W |  |  |  | —
3.3 | Pipe bedding / haunching /overlay | Document review site inspection. |  | In accordance with AS/NZS 2566 for PVC pipelines. For PVC overlay >100mm over pipe. |  |  |  |  | Prior to backfill. | Photos or site inspection. |  |  |  |  | — |  | — |  | W |  |  |  | —
3.4 | Backfill | Clegg every 10m alignment for each layer of backfill (not exceeding 200mm) |  | Minimum 20 Clegg reading |  |  |  |  | Prior to placement of each layer of backfill. | Test records. |  |  |  |  | — |  | — |  | W |  |  |  | —
4 | [8 empty] | CLOSEOUT
4.1 | Collate and supply Producer Statements / Waranty Schedules | Document review |  | Collate and supply producer statements |  |  |  |  | Upon completion of Water supply works. | Producer statements |  |  |  |  | H |  | H |  | H |  |  |  | —
4.2 | Collate and supply Council inspection reports. | Document review. |  | Collate and supply Council inspection reports. |  |  |  |  | Upon completion of water supply works. | Inspection records. |  |  |  |  | H |  | H |  | S |  |  |  | —
4.3 | Collate and supply compaction records. | Document review. |  | Collate and supply compaction records. |  |  |  |  | Upon completion of water supply works. | Inspection records. |  |  |  |  | H |  | H |  | S |  |  |  | —
4.4 | Collate and supply as builts / CCTV inspections / water tests | Document review / as builts |  | Collate and supply as-builts and inspection records. |  |  |  |  | Upon completion of water supply works. | As-builts / test records. |  |  |  |  | H |  | H |  | S |  |  |  | —