## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
7d2d3d1b-a1ef-4d0c-885f-9bb63d575e90 | checklist | ITP - Paharakeke - Stage 4 Rev 1 | itp | ITP - Paharakeke - Stage 4
597101fe-561b-4c8a-940c-3f8a4c854bc2 | section | 1 - Site Safety & Traffic Management
543f44d2-f024-47c6-828f-9561738c549d | checkpoint | Safety Plan (1)
8d091727-f4dc-5e56-a21e-105e00a47358 | note | Frequency - Prior to works starting
18769719-0a88-58a7-a2af-feabd535e243 | note | Inspection / Test Method - Engineer to review Contractor's Plan
f04ce529-2ce7-5855-b4ae-c2abef7fd62e | note | Acceptance Criteria - Meets contract requirements
ead0bd13-3ecc-560a-b3ab-c06b8ccda89b | note | Verifying Documents - NTC acknowledging Safety Plan
23747cf5-65e4-587f-8ccd-7251b1e39c98 | note | Engineer / Client - H
b035ba1e-551b-418a-873a-8badc0663e54 | signoff | HOLD POINT
02078962-9d2e-4785-95d6-fa1ca80f07b4 | checkpoint | Safety Plan (2)
177db21c-32b4-5297-889f-83339e373e79 | note | Frequency - Daily
9d2eda95-eef2-537e-ac97-59a8fac63894 | note | Inspection / Test Method - Compliance monitored by the Contractor
ecc791d9-39d3-58fa-ba61-86bc99d6aad3 | note | Acceptance Criteria - Site Safety Plan is updated to reflect changes in the work place. Excavations are protected.
c04c8ab1-84fd-5d39-8863-7e7c63d7b771 | note | ○ Site Safety requirements are met.
270a7bf8-76e9-55bf-af44-ddcfee866a6e | note | ○ Pedestrian access is clearly defined and signage is in place. Accident reports have been completed.
681e3c07-f554-51cc-bddc-50028b6d6f39 | note | ○ Compliance report is completed.
fd16d9bc-7ad6-590a-96b4-712cc10f1a6c | note | Verifying Documents - Included in weekly report
fd8c64a0-03fe-44e1-b256-4bcc925759b5 | checkpoint | Traffic Management Plan (1)
35a6c709-592a-5d9c-89e1-051331596ace | note | Frequency - Prior to works starting
8f5f6460-ac2c-5ff8-896a-9d4a7146258a | note | Inspection / Test Method - Contractors TMP to be approved by the RCA (Road Controlling Authority) and a copy provided to the Engineer.
873e9b6e-6ea0-5aaf-9b09-c0d7acc273aa | note | Acceptance Criteria - Meets contract requirements
4ff17241-1f57-50e4-9f88-00b057b7df62 | note | Verifying Documents - NTC acknowledging Traffic Management Plan
631ab6a7-26ed-52b9-8536-5d28f69edf1f | note | Engineer / Client - H
218f4be1-94ab-49f7-8a7a-4070d1356ed4 | signoff | HOLD POINT
ed9351b7-e317-404e-8670-2fd9170941f5 | checkpoint | Traffic Management Plan (2)
5ff29b12-a1df-5db7-8688-2997b81a3f92 | note | Frequency - Daily
cc219488-dfed-5e59-84ff-eca53dfe5cb6 | note | Inspection / Test Method - Compliance monitored by the Contractor
17a33048-2159-52d6-8f0f-87d7052b450b | note | Acceptance Criteria - Traffic Management Plan is updated to reflect changes in work. Signage and devices are clean and set out appropriately.
bd75db89-cab9-576e-8956-9d3ade4ed6d1 | note | ○ Detour and single lane requirements have been met. Compliance report is completed.
8124b682-5c5a-50e7-b3fe-6c4bee81f5c7 | note | Verifying Documents - Included in weekly report
7986f884-4a4d-4414-987b-08f502814a8a | section | 2 - Quality Assurance & As-Built Information
9cc84b3a-995e-4b48-ab6a-4d90758ccb3a | checkpoint | Quality Plan
e66a4b5d-5cf6-56aa-b101-c7f2ff215273 | note | Frequency - Prior to works starting
414dc1dd-afab-5089-a793-fd775d14c103 | note | Inspection / Test Method - Engineer to review Contractor's Plan
005d9e2e-0d06-5d32-acdc-cdab2966046e | note | Acceptance Criteria - Meets contract requirements
06a3de2d-f6a4-5425-b115-de8ea2b7ebd8 | note | Verifying Documents - NTC acknowledging Quality Plan
62b43781-1376-5ce3-b448-7f9b16858895 | note | Engineer / Client - H
8806d523-1503-48f3-b2b8-c0f24f88e782 | signoff | HOLD POINT
96287ad9-4da7-403c-a6e8-8bb2432fba6f | checkpoint | Setting Out
38b423bf-2d69-5f52-96e5-a2d065fb9646 | note | Frequency - As works progress
e525bbb4-89ba-5770-98dd-51b784f12c2a | note | Inspection / Test Method - Survey control report
e0baa2ce-d9f3-52ea-90e5-c16a102e1cf2 | note | Acceptance Criteria - Meets construction tolerances
d7672d69-dd46-5bad-971b-d295d51d765c | note | Verifying Documents - Survey control report
8776071e-02bb-4c3a-b914-a35fa87bd2b2 | checkpoint | Construction
3cb85b6f-285e-5e42-ab52-e0cdaf9e656e | note | Frequency - Weekly
e2bbb0f3-df17-5e6a-bd39-a951b5caf1e6 | note | Inspection / Test Method - Progress report
ad6383de-0421-5d7f-b948-726a34002ff0 | note | Acceptance Criteria - Meets programme
8fb6a92a-aa61-530d-86c1-81c8c0656199 | note | Verifying Documents - Included in weekly report
f06d1df9-7471-40ac-ac44-36c293b503ae | checkpoint | Traffic Management
8036b1a0-b74e-54ac-abe0-c42282dd7744 | note | Frequency - Weekly
84314bcd-9f20-5afe-bbee-77721c56f7cf | note | Inspection / Test Method - Monitoring report
12273023-88fd-50ce-a235-561ad3ee51af | note | Acceptance Criteria - Safe traffic management
75959b9a-328a-524d-823e-183878e5fb64 | note | Verifying Documents - Included in weekly report
c3bcc66e-bc1e-40d2-b1ed-7dc9ea13081f | checkpoint | Site Safety
389ff9c7-c8e1-56c0-adc0-e168614e3012 | note | Frequency - Weekly
453efba1-376f-5004-9d15-917ee0db9326 | note | Inspection / Test Method - Monitoring report
933bce69-3424-5a15-84f3-c61b17f74019 | note | Acceptance Criteria - Safe site
30d0a084-8d2a-5a12-b02b-cb62576e6173 | note | Verifying Documents - Included in weekly report
7ed9e95b-f9db-4cf0-a490-445f0d05b479 | checkpoint | Water works
99155822-6c4b-5fc9-800c-e1f821005883 | note | Frequency - As works progress and on completion
d51dcad1-a009-5783-a76f-84037f781ab1 | note | Inspection / Test Method - Construction reports
dee0214b-8ef6-503d-bd91-1e93f9183b39 | note | Acceptance Criteria - Meets contract requirements
371ea685-5b5e-5592-a4e8-bdb1d0713b1f | note | Verifying Documents - Included in weekly report
b3355bad-d338-4e3f-8fef-71f96dd4492c | checkpoint | Stormwater works
8eed9208-f7cb-573c-83f7-19ad6e1b81dc | note | Frequency - As works progress and on completion
93d09031-839f-5501-91d4-f440c16ab98e | note | Inspection / Test Method - Construction reports
65fc2bb6-573f-5029-915c-7d10786919d3 | note | Acceptance Criteria - Meets contract requirements
64db1bf3-dee0-5c4f-b9ec-e91e4248d885 | note | Verifying Documents - Included in weekly report
eb08b342-5cb1-4192-abff-76a0ad535b5d | checkpoint | Sewer works
ad2a1dea-f982-54e9-b8e5-c74104c6742e | note | Frequency - As works progress and on completion
cb6aeee2-d183-58d6-aaa9-23cf86e5e1ec | note | Inspection / Test Method - Construction reports
f620ba31-2901-5033-9265-c37de0cd1706 | note | Acceptance Criteria - Meets contract requirements
3a99a32d-2911-583b-8663-1e8bb2dc9289 | note | Verifying Documents - Included in weekly report
fe531c8d-e427-48dd-bc8a-6a8edba8f696 | checkpoint | Earth works (1)
aef832d2-fc7e-516c-ae94-9aa53636b3f9 | note | Frequency - Prior to earthworks
0971e10f-a3ec-5ea1-a350-fbd00b68ff3d | note | Inspection / Test Method - Manhole inspection
3e31b890-6a7f-57bb-91aa-037bdf3d8164 | note | Acceptance Criteria - Temporary floors kept in place
1eb70682-5d4a-582a-8f99-ed8425b2354c | note | Verifying Documents - Visual inspection
6cfa5148-ad17-44e8-9689-5c28da7f6746 | checkpoint | Earth works (2)
53dbf641-78fe-5beb-8dc9-9b8a816ebf9d | note | Inspection / Test Method - Service cover location
d9125299-1e79-5508-a70c-656a668a4b51 | note | Acceptance Criteria - Lids marked and kept clear for use
b92390c1-ad43-5bd8-8e79-432ec8813ef7 | note | Verifying Documents - Visual inspection
a193b856-3ce5-4eac-bd41-040bc8bfaf1e | checkpoint | Earth works (3)
097f9879-6706-5c02-81e2-22d9bd6b7afb | note | Frequency - Prior to sub-base construction
914a5b82-4a73-5614-9109-bf0ce931ea72 | note | Inspection / Test Method - Construction reports
c7e30a85-f1d0-5c90-82d1-0ad0c2b9731f | note | Acceptance Criteria - Meets construction tolerances. Services covers exposed and marked. Service boxes clean and fit for use.
14821574-fd44-58eb-b00d-4ea2e5e5f2a8 | note | Verifying Documents - Included in weekly report and visual inspection
d19b1d9b-871b-4d68-9449-58ddf553dd2f | checkpoint | Sub-base works
068b6f9f-acc4-59aa-8e06-27a3a925d111 | note | Frequency - Prior to top course construction
7afc0cb2-1bb0-5875-b2fa-57e58d21d79a | note | Inspection / Test Method - Construction reports
a8445120-4903-5ea4-a530-a9acedab3e2a | note | Acceptance Criteria - Meets construction tolerances. Services covers exposed and marked. Service boxes clean and fit for use.
f5a716ac-1d4b-5440-8821-d7acae6d4a6e | note | Verifying Documents - Included in weekly report and visual inspection
281d1b66-ba63-4aab-8fcc-2b564ba3c9e7 | checkpoint | Basecourse works
ff2b7a67-8570-5c9f-91a0-4199f0a668aa | note | Frequency - Prior to sealing or construction of kerbing and paths
a61e1a35-ddc0-5ba5-8857-81feb05dd3f6 | note | Inspection / Test Method - Construction reports
06105f31-3ff2-5358-9a52-c16438439b7a | note | Acceptance Criteria - Meets construction tolerances. Services covers exposed and marked. Service boxes clean and fit for use.
37540039-949c-5c22-982e-434708a1851a | note | Verifying Documents - Included in weekly report and visual inspection
3b484bf5-35fc-45f7-814a-7a6b4a6c7f85 | checkpoint | Sealing works (1)
e94087cb-d76b-5164-b62f-f04819536158 | note | Frequency - Material tests and seal design prior to sealing. Seal reports on completion
f0280b1c-c659-5e31-81e4-77cb462c8c10 | note | Inspection / Test Method - Construction reports
b3e29a0a-2220-5ed6-b66d-babafbf36e06 | note | Acceptance Criteria - Meets construction tolerances Services covers exposed and marked. Service boxes clean and fit for use
6bc78cec-8c12-5446-964e-cce7e487d88a | note | Verifying Documents - NTE including material tests and seal design
5c289f71-0d1f-480a-8dcd-ab36b4f6e579 | checkpoint | Sealing works (2)
e3ac7f05-3908-5aca-8cd6-a8f7849bbf90 | note | Frequency - On completion of sealing
8f38f83a-faa5-561e-85de-fd9711ccb4c3 | note | Inspection / Test Method - Inspection of service lids and covers
b4d76fa9-5bcf-5a5a-943a-abd4ee87a179 | note | Acceptance Criteria - Temporary floors removed from all manholes
34d1c34a-d3ec-593a-850d-3ef6916c08dc | note | Verifying Documents - Visual inspection
b720c06c-0b22-4bcd-bd02-2868fc685c77 | checkpoint | Footpath, berm, kerbing and traffic island works
18aa1007-00eb-56a4-9881-57c5f0f5ce3a | note | Frequency - As works progress
e651d5ca-d5d0-51f4-9ace-e11696da5046 | note | Inspection / Test Method - Construction reports
37c732ce-0110-5b3c-95df-873d19f5ce38 | note | Acceptance Criteria - Meets construction tolerances. Services covers exposed and marked. Service boxes clean and fit for use.
e0e3743c-029e-5462-8eea-f065ed31ee5b | note | Verifying Documents - Included in weekly report and visual inspection
99b6bc0a-fb19-4328-a464-502c0425ffdf | checkpoint | Water works
e87a01fb-b25e-59e0-b7f3-748757117521 | note | Frequency - As works progress
cb2822d4-8364-56f5-ba85-111d05aad42d | note | Inspection / Test Method - Construction reports
247e3300-5d03-5786-b990-18f37bb8ba44 | note | Acceptance Criteria - Meets construction tolerances. Services covers exposed and marked, Service boxes clean and fit for use.
1e0d1e56-a4c8-52f2-bbeb-81c5673820d0 | note | Verifying Documents - Included in weekly report and visual inspection
5d1be857-257f-4150-9dcc-3e791cd072b5 | checkpoint | Sewer works
24050260-7245-574c-9a62-7e7f1e38673f | note | Frequency - As works progress
73ac2d2d-36c2-5fd7-982a-f9f6a9651a4b | note | Inspection / Test Method - Construction reports
3e634419-f98f-4076-ab36-be101128da4b | checkpoint | Stormwater works
b8f6ada8-ee88-5f58-8dd4-cbfeaa45880f | note | Frequency - As works progress
d6797b2c-b751-55cd-889b-4f5d6953c030 | note | Inspection / Test Method - Construction reports
b06fb3c1-71bd-44e6-8a90-1a180ad5036e | checkpoint | As built information
94c3a51d-9765-5d72-99ef-b32c1c06239a | note | Frequency - Completion of works Condition of Practical Completion
f5b120ec-05a7-5d9e-8e03-0d6202856890 | note | Inspection / Test Method - Levels and coordinates of nominated features in terms of datum and construction drawings.
4e235ad8-a8e2-5b12-b3c7-39d355c91aad | note | ○ RAMM data sheets.
de8cd4a8-59f3-5d3e-aec2-ef0b4f5ea36e | note | Acceptance Criteria - Horizontal +/- 50mm Vertical +/- 5mm
b0dc7f33-2fc8-52f4-8950-fad22b39bba1 | note | Verifying Documents - NTE with asbuilts in PDF and DWG
3ec39d77-f6ea-5576-97ce-7c2df1aeebc3 | note | Engineer / Client - H (Required for issue of PC)
79994e83-3b3e-484d-9224-f303847568d1 | signoff | HOLD POINT
b290c464-0620-43b0-ba9f-f4309356a6f0 | section | 3 - Environmental Management
9341b09c-e4ed-4daf-a3d3-cc1559849d4d | checkpoint | Environmental Management Plan
d0495a62-c2f9-5ac7-9299-9bf0dad3f437 | note | Frequency - Prior to works starting
5a2d8494-727d-57d5-9d9c-a6858024c2ea | note | Inspection / Test Method - Engineer to review Contractor's Plan
f33c0d16-fe5d-5c43-9ee6-d3700ecacb90 | note | Acceptance Criteria - Meets contract requirements
1c2d3adf-12d2-5ef0-8122-f0012e03c37b | note | Verifying Documents - NTC acknowledging Environmental Management Plan
78a45753-4704-5dbe-8e30-1e003fdf1367 | note | Engineer / Client - H
0cc91218-626e-49a1-8013-bd98e8c245a3 | signoff | HOLD POINT
e5238fad-2c96-438e-bc79-77b0961db566 | checkpoint | Contractor’s Resource consents
54d7e70a-2308-5c69-97ab-076b60479a05 | note | Frequency - Regular monitoring during contract
8e509b07-f074-5811-b32c-6d857b0fd62c | note | Inspection / Test Method - Contractor to review and test
cdf8caf5-772b-5ed5-be39-82cff0c4adf3 | note | Acceptance Criteria - Meets consent requirements
850a6a43-d731-525e-b92d-1447e021687f | note | Verifying Documents - Test records supplied on request
766428ef-8227-46ca-9005-dd8567964cc2 | checkpoint | Principal’s Resource consents
fb06c730-fd18-5bcc-96c5-047f9aa214ed | note | Frequency - Regular monitoring during contract
611def21-4655-5db5-8f6a-b050c0c738a4 | note | Inspection / Test Method - Engineer to review and audit
f7dc1d94-2bef-5b9b-af70-5d5ee0da144f | note | Acceptance Criteria - Meets consent requirements
f57a1c29-a946-48f8-93ea-96070bd0c3e3 | checkpoint | Environmental risks
983c981d-0d95-50fc-8868-19223046fac3 | note | Frequency - Regular monitoring during contract
fefda2cb-adce-57ea-93f5-d8dfb81ab622 | note | Inspection / Test Method - Contractor to review and test
c3464cff-a097-5109-a824-e59eb3993ad8 | note | Acceptance Criteria - Risks identified with mitigation measures in place and implemented
8f9edfcf-8a9c-5caa-817f-c6db0698e6d7 | note | Verifying Documents - Included in weekly report
f41f78bb-f85c-4701-9be8-a7d5f4c219dd | checkpoint | Water run off
d0621387-8135-5abc-a863-0244060da44b | note | Frequency - Daily discharge checks
50a412dc-1884-5cd8-8239-e02c5f3c352a | note | Inspection / Test Method - Visual
3bb09ef3-fbf7-5f5a-9474-dd4971c1221e | note | Acceptance Criteria - Silt traps in place with clear discharge down-stream to drainage systems
739e7a12-c4de-5289-9608-01ec0e3d1700 | note | Verifying Documents - Visual inspection
38ac4c40-505f-49da-ab90-349b916e67a2 | checkpoint | Dust and noise
2fca6f4b-e841-5a1b-a910-f7c24d108165 | note | Frequency - Daily nuisance and dust checkA
fa170dc8-f493-5985-92e2-192a540cf909 | note | Inspection / Test Method - udio and visual
6af1944d-6b41-5d12-af80-8dd2ef2f9ab7 | note | Acceptance Criteria - Site observance with mitigation of dust and noise nuisance
07228e82-c817-5782-ae9f-a66520b695f2 | note | Verifying Documents - Visual inspection
755ba8e3-40ba-4a99-b5ab-46e1a8f78492 | checkpoint | Fuel and oil spills
0abaa10a-a17d-5214-abc8-dbd9910235e4 | note | Frequency - Daily
e56df5af-8429-50a7-8725-172979bff837 | note | Inspection / Test Method - Visual
534e8312-47a9-53b5-9c2e-022c5ead9662 | note | Acceptance Criteria - Site observance with spill mitigation measures in place and implemented
aa074834-6161-5fd2-a8e3-3875ff30d4d5 | note | Verifying Documents - Visual inspection
e4d8b75b-003f-4887-9ee4-436b0d95ab09 | checkpoint | Concrete and seal cutting
11375ec3-8aaf-56bc-a0aa-1fd83f11bc4c | note | Frequency - Daily
20b5a21e-0837-552a-891b-ed33215faf11 | note | Inspection / Test Method - Visual
a947de94-7abf-5d01-830d-92acea3c9f13 | note | Acceptance Criteria - Contaminate traps in place with clear discharge down-stream to drainage systems
8296690c-f11e-5860-9e25-277d8132380c | note | Verifying Documents - Visual inspection
d915dc93-1c3e-4fd2-be65-d69b25d89710 | section | 4 - Pipe Trenches
53e2bb78-7c2e-496b-827b-9c911ba9cfd1 | checkpoint | Qualifications of Personnel
5fe58a9b-8330-5c34-9f7d-adbbbdd78c10 | note | Activity Description - Refer to Specification F100 Preliminary and General
6b09fa12-a8a5-5a55-bf76-a3b0144b76be | note | Frequency - Contract Start
03395a9d-0bb5-5c5a-a2a5-4f144338e64d | note | Acceptance Criteria - Evidence of Qualification and personnel on-site.
21424757-355c-5b1a-b9fa-7b81e2dc605c | note | Verifying Documents - Provide evidence where not previously provided or personnel change
72f4b4d2-33a1-559a-834a-5dd04c9fca7d | note | Engineer / Client - H
3b4360ad-54a5-4b58-a928-3566f5c78e2e | signoff | HOLD POINT
3b568ead-482a-4a8d-b3a6-367e27a5055f | checkpoint-no-value | Materials - Refer Section 2
53d86913-5bb1-450b-83ba-ed810186f931 | checkpoint | Selected fill
9b591827-5e65-5d18-91ad-1105881b88d7 | note | Activity Description - Grading, sand. Equivalent, CBR
2b4b0d57-3747-5590-af5f-4b23d776b144 | note | Inspection / Test Method - Lab testing
0915dc8d-41a4-5273-ab55-2f467533ce33 | note | Acceptance Criteria - Comply with grading specification 100% pass 50mm at least 45% pass the 19mm sieve, and not more than 10% pass 425 micron sieve, CBR not less than 40 and SE of not less than 40
91f609ef-9fb2-52f4-89a4-ac58e4a68811 | note | Verifying Documents - Lab results to be supplied to Engineer
6b2a2728-2f81-5c4e-94d7-915284b919c4 | note | Engineer / Client - H
9c5223de-b16a-4df2-9740-438095b91404 | signoff | HOLD POINT
4ca9f8a7-2c51-42e7-8273-15144ea7161d | checkpoint-no-value | Ground conditions
6c13ad55-42f4-4d01-ae6d-4a4fc07b7126 | checkpoint | Firm formation level
16759b9e-3e37-504d-9d31-3ddc695de4d7 | note | Activity Description - Bearing capacity of base
c01ebcf6-e976-5327-9748-527e25cd5ed9 | note | Inspection / Test Method - Inspection
002e8aa3-8a61-5d47-b6a6-a236d4d513bd | note | Acceptance Criteria - Bearing greater than 50 kPa
c00fecad-953f-54ee-9d89-dc6f1f6d9dbc | note | Verifying Documents - Inspection records available for review
96ca65cd-04c3-4ee1-90a9-9430dfdbc16b | checkpoint-no-value | Tolerances - Refer Section 3.8.3
216ff18b-8e34-49f4-85ac-c01b589f3e34 | checkpoint | Trench excavation (1)
c994b156-07ab-5989-a6b0-ff2fe602ed38 | note | Activity Description - Minimum to maximum range of trench width
2ec8ddbf-2a6d-5051-94f7-3fac83bf8fc0 | note | Inspection / Test Method - Survey
da6e3510-8832-5a24-91d5-3767ca8db34b | note | Acceptance Criteria - Tolerance range as per section 3.9.3
39ce7df2-88a1-5bf0-bbb1-dca326aac097 | note | Verifying Documents - Visual inspection and measurement on site
3d1320a2-4a7a-4361-8beb-9823530d60a3 | checkpoint | Trench excavation (2)
b12bc8c8-b777-5580-ac55-44cffff69e13 | note | Activity Description - Side slope of trench wall
7750edac-e3c2-534b-b3f7-c8b92a3e8970 | note | Inspection / Test Method - Survey
2c342a98-ea76-5fc8-ba37-b467db1e0436 | note | Acceptance Criteria - Near vertical
efccb91c-9792-5b10-86f3-cde9887c989b | note | Verifying Documents - Visual inspection
80804933-8f39-4a4a-a5e9-b184918c94bd | checkpoint-no-value | Inspection and Testing - Refer Section 3.10
4d750e69-5a87-41ee-a724-236b4fd4cb9a | section | 5 - Retaining Walls
ecdfa7b2-c5a8-4233-96fc-d18165d5237c | checkpoint-no-value | Methodology
0e9cd2bf-cf2d-4423-ad76-43c512e4904c | checkpoint | Review of Retaining wall construction methodology
eef3a273-f1f1-5db4-934a-39c842812c9d | note | Activity Description - Engineer to comment where required, on the proposed construction methodology and review aborist assessment. Refer to drawing DRG-WA-21802 (C02)
5c2c5997-bd25-5096-b774-1f837c8986b6 | note | Inspection / Test Method - Engineers review
3c941f83-ba06-50f6-9523-85194d052984 | note | Acceptance Criteria - Engineers acceptance
8ce09836-a33e-5017-852b-793e064b85e4 | note | Verifying Documents - Approved CMP
4d2fa38b-8584-5064-99ff-2160a7b047b4 | note | Engineer / Client - H
2dcb5399-ddd1-4e35-9cfb-283fdfdb8618 | signoff | HOLD POINT
81e0d640-81da-4e17-b999-0386ad3c5cb0 | checkpoint-no-value | Materials
c5dd7246-21be-4fe2-81bd-50fd4088a1a2 | checkpoint | Review Contractors supply of materials and QA documentation
1c46e02c-50b9-562a-9696-129e7770c9d5 | note | Activity Description - Engineers rep to review QA documentation for timber piles, timber lagging, concrete and drainage backfill. Refer to drawing DRG-WA-21802 (C02)
09a248c9-79ee-53b9-9384-bfd04413e818 | note | Frequency - 10 days prior to beginning work
7a36b466-a6af-5ee3-8865-7bd42772c78b | note | Inspection / Test Method - Engineers review
f85edfbf-8d31-5459-8504-fcfed5b22cae | note | Acceptance Criteria - Engineers acceptance
e4a9e31a-8258-549d-af30-1db8bb9ac1ce | note | Verifying Documents - Provide evidence of material spec.
b74d3da9-f292-54c9-b611-40b9d288badf | note | Engineer / Client - H
7cd1ebe3-484c-4203-bfd6-a85b70b0f155 | signoff | HOLD POINT
ba0e467c-78cf-4577-8601-74dce70f3907 | checkpoint | Confirmation / approval of any alternative materials
a2ffcce2-13f7-54e2-b99f-de9d38995b54 | note | Activity Description - Engineers rep to confirm acceptance of any alternative materials requested by Contractor. Refer to drawing DRG-WA-21802 (C02)
38d240ab-d0cc-5ad0-9261-c0ad753e2a27 | note | Frequency - 10 days prior to beginning work
f323aa0e-93c0-5281-bb8f-284665fd554b | note | Inspection / Test Method - Engineers review
bbba4d05-b29b-5a0f-9b15-dcf15dec049d | note | Acceptance Criteria - Engineers acceptance
b19cd13d-be06-5b47-b526-fcc7682f91d6 | note | Verifying Documents - Provide specs of any alternative materials
cebee1a1-1711-529c-b037-37108e320e9c | note | Engineer / Client - H
034f48f3-03b0-4000-bf7c-e5a6f77151b7 | signoff | HOLD POINT
e365d321-e9d1-4412-ae3b-e3b2b6740c8c | checkpoint-no-value | Setout
76dac771-5ce8-43b4-aa5f-e08364c2b28b | checkpoint | Site visit to approve set out of retaining wall
76c2de7c-cf41-536e-bda4-ca4c99070c8a | note | Activity Description - Engineers rep to provide site inspection report sheet with photos of set out and description of site conditions encountered and any issues relating to design. Contractor to provide survey data co- ordinates for set out of four piles at pipe crossing location. DRG- WA-21802 (C02)
b7d0d1bd-f8a6-5da3-8a63-5ea41c732ddb | note | Frequency - Once, after excavation to founding level and following survey set out
59510ba3-c3be-579f-b944-0950e89425ae | note | Inspection / Test Method - Survey
4fa1a3b8-8a08-508f-8eb9-93b1439d1368 | note | Acceptance Criteria - Engineers acceptance
56633076-5dfb-5942-8efa-bd3372d38819 | note | Verifying Documents - Site Report sheets
bd09c346-b3b3-5eae-8062-7f600f752fcc | note | Engineer / Client - H
eab3992d-1776-4cf5-b3b6-1a69a1973927 | signoff | HOLD POINT
1056103b-a487-4750-a2e8-ad15144c2501 | checkpoint-no-value | Piling
ecb9daef-a28e-4773-8498-7e01e61a15f8 | checkpoint | Inspection of augered pile holes
e4424d5b-04ca-59be-8d43-fc285a8aade5 | note | Activity Description - Engineers rep to witness installation of first two piles for each retaining wall and provide site visit report sheet detiling materials encountered, drill rate and any problems encountered and how they were resolved. Contractor shall record a pile log for all installed piles. This shall record the depth of hole, material encountered, comments on drill rate, if water was encountered and any temporary measures such as if pile casings were used, or any other issues that occured and how these were resolved. DRG-WA-21802 (C02)
7cbe6e87-abc3-5bc1-aff3-1a89527818d3 | note | Frequency - Once, after installation of first two piles on each side.
c7616c23-113b-5ab3-92ea-0610220833f2 | note | Inspection / Test Method - Engineers inspection
61de6f6f-e786-5379-aa49-b6374d29dcc8 | note | Acceptance Criteria - Engineers acceptance
5409ef6a-c4a0-5211-9e13-229957945bc1 | note | Verifying Documents - Site Report sheets
0690d1d3-54aa-5596-9374-1be415df915c | note | Engineer / Client - H
6d467fb5-d43c-49ca-908c-ace41efcf286 | signoff | HOLD POINT
28698b87-b3b7-4003-9b07-4d2d3589fafa | checkpoint-no-value | DN375 Stormwater
a650e76f-a3c6-47d3-9365-5df21467cfb9 | checkpoint | Inspection of DN375mm Stormwater pipe outlet
488ae737-26df-5f87-a657-6777287be926 | note | Activity Description - Contractor to provide photos of the pipe outlet location showing construction process of lagging and drainage material around the pipe. DRG-WA-21802 (C02)
d13b7078-23a9-5a8d-93fc-c1b147052160 | note | Frequency - Throughout pipe outlet construction
005d0de8-b187-5de9-9888-27305ff05e01 | note | Inspection / Test Method - Photos (Contractor)
d0ad5961-caf5-5f57-b6f4-7dfc6b2bc46e | note | Acceptance Criteria - Engineers acceptance (based on photos)
3555adba-7a11-539d-85da-3bd12de94485 | note | Verifying Documents - Photos
92482f0d-db1d-5825-95e4-3474cad1724b | note | Engineer / Client - H
4e7f265e-d33c-4bd0-bf7e-e5bcb7c1f9dc | signoff | HOLD POINT
7e4dbb16-fe4c-45e0-b351-c0bf776f8a06 | checkpoint-no-value | Retaining Walls
0d69ffa0-f67c-4c23-a3b4-94460c210a19 | checkpoint | Inspection of retaining wall at OD813 wastewater pipe crossing location
bff6a52b-0c8d-56b0-8965-8502ac71c9bd | note | Activity Description - Engineers rep to inspect pipe crossing location at each retaining wall prior to any drainage backfill being placed above the pipe. Engineers rep to provide site report sheet summarising inspection. DRG-WA-21802 (C02)
c05b5f7c-e2c6-56e4-9fae-bf1a138a01d3 | note | Frequency - Once, following installation of steel pipe crossing
13e95c20-b6d9-5d66-8a9b-a12a09d3e976 | note | Inspection / Test Method - Engineers inspection
f2d46587-49f5-5498-841c-547bfcc7a0da | note | Acceptance Criteria - Engineers acceptance
25a655e2-7c2e-5332-b045-a113fb52d4d2 | note | Verifying Documents - Site Report sheets
6331a082-37a4-57db-b0dc-8d12ce775fc9 | note | Engineer / Client - H
a33d0c4b-fbee-421d-ae9e-2e7a0188967e | signoff | HOLD POINT
bf63f391-351b-4efd-ba39-36757a7e4c8e | checkpoint | Inspection of lagging at 50% completion.
4657593c-903b-5627-8582-acecb2ade36b | note | Activity Description - Engineers rep to inspect lagging at 50% complete and summarise inspection in site report sheet. DRG-WA-21802
7c822ce6-9f6e-5407-8b18-fce51c15dfbb | note | Frequency - Once following installation of lagging to 50% height
bcd044b0-624a-562c-bfce-ac343f7e3407 | note | Inspection / Test Method - Engineers inspection
246c656c-176e-5c6a-94ee-7ac387b3cc2b | note | Acceptance Criteria - Engineers acceptance
3c24ead2-0c52-574f-aef6-961c048ae125 | note | Verifying Documents - Site Report sheets
7820c396-e25f-5261-80ad-5ca8ad8f6a2d | note | Engineer / Client - H
435f53ee-3e84-47e6-a983-a5c519c9b44d | signoff | HOLD POINT
f58ead3c-90f2-41c2-8634-fe6858a15470 | checkpoint | Inspection of drainage installation and determining subsoil outlet location
cc162e2f-7ca3-5673-8b0d-93961c7341c5 | note | Activity Description - Engineers rep to inspect drainage backfill and determine the location of the subsoil drain outlet for each wall. Engineers rep to provide site report sheet summarising inspection. DRG-WA- 21802 (C02)
1f53c7fb-ec30-50e4-8d39-f21587029fe4 | note | Frequency - Once, following drainage backfill for each wall
190c2d41-d170-5532-90c2-dcff2f6bf946 | note | Inspection / Test Method - Engineers inspection
33d587fb-3cd8-5eb6-be17-0e161f40315a | note | Acceptance Criteria - Engineers acceptance
3f0530fc-3ccb-57da-8b07-0177d1f86a96 | note | Verifying Documents - Site Report sheets
9c3fb4ed-cb0d-5b4f-aeec-687313f526ec | note | Engineer / Client - H
2bb8da9f-4eb6-4d6c-935b-18047bd74a82 | signoff | HOLD POINT
bc367b6c-b8a8-4796-9791-e33bad98eb4f | checkpoint | Final finished surface of site to be inspected
37f0b936-0bb0-52c6-88de-40f463b8b522 | note | Activity Description - Engineers rep to conduct final inspection of retaining walls and provide photos with site report sheet. DRG-WA-21802 (C02)
766be8d0-9b82-52ec-8e4e-1288243c5f4b | note | Frequency - Following retaining wall construction and all reinstatement works
70b63d2d-e318-5d83-a98b-8cabebcae2b3 | note | Inspection / Test Method - Engineers inspection
cc96ed2a-b00b-5a0e-9929-109dfba2c68d | note | Acceptance Criteria - Engineers acceptance
d6f46efc-31f1-58aa-aa5d-f7f959da8a22 | note | Verifying Documents - Site Report sheets
5d65c076-fb38-56ca-8f0b-772aa71f645a | note | Engineer / Client - H
48b21a3c-49a8-40c2-abfd-f425f5eddcc4 | signoff | HOLD POINT
5b798a5a-7e48-427d-b3fb-9e73d335452d | section | 6 - Gravity Pipelines
52731ea2-1c9d-44e5-955b-0557224d9321 | checkpoint | Qualifications of Personnel
cced81dc-52ba-50de-a3b5-d68c4aacf08c | note | Activity Description - Refer to Specification F100 Preliminary and General
ca9bc033-a2dc-5124-84ba-203461eb60e8 | note | Frequency - Contract Start
417f6f37-6f08-5193-ad69-7c55157cbb95 | note | Verifying Documents - Provide evidence where not previously provided or personnel change
9a3b0983-8747-58f4-a734-154a71e56d48 | note | Engineer / Client - H
c4f942eb-9ba0-4669-adc2-0165bd5144a2 | signoff | HOLD POINT
be6c766b-9b6c-41ba-b8e4-8586b974e2b4 | checkpoint-no-value | Materials - Refer Section 2
a12366df-b903-4eda-81bc-8ff9920b93e4 | checkpoint | Embedment Material
17d0d993-d9bf-5a67-98c9-a4159a6f4d3e | note | Activity Description - Grading
f09654e1-b7d6-5294-9e73-4d2e545c878a | note | Frequency - Contract Start
0b596c64-9f78-5f30-a7ed-6bff516bbd89 | note | Inspection / Test Method - Lab testing
f1cab953-46fd-5058-b0fa-f1c7487cae58 | note | Acceptance Criteria - Comply with grading specification
7e6054dc-cc27-5fbf-a86f-214eba46595c | note | Verifying Documents - Test results to be provided
4d2c98a5-1f7f-5d19-9181-890917456cf4 | note | Engineer / Client - H
59878d63-7dc5-4f12-b624-25adc7a84c7b | signoff | HOLD POINT
3bf43fd5-2c2a-42fd-b574-3bf5e11aa809 | checkpoint | Material Acceptance
280a8f78-aa10-5ad4-ae33-6ac1fcb92085 | note | Activity Description - Pipes and fittings
f4a18a90-260b-5e8a-bee8-4ec7de4020c5 | note | Frequency - Prior to use
4b6f04d4-c0fc-5092-8073-1c8bf2dae406 | note | Inspection / Test Method - Inspection
a6ef3176-c378-5d95-a7d7-c5076e8ad6cc | note | Acceptance Criteria - Comply with Section 3 AS/NZS2566.2
50864738-0446-5023-825d-d0b2f6c5f14c | note | Verifying Documents - Visual inspection
75c91924-848d-4ba1-a8e9-b1045bbf2fd3 | checkpoint-no-value | Bedding, Laying, Jointing and Manholes - Refer Section 3.3
d6bead91-5830-4dfb-8087-6346f8175aed | checkpoint | Pipe Jointing (1)
a79541fd-4cfc-51f9-a877-43444053966e | note | Activity Description - Clean and Dry
692baf44-3628-5b3d-8d7f-074f657aba63 | note | Frequency - During Jointing
8df9cb6b-aade-5903-a485-64410447a0ca | note | Inspection / Test Method - Inspection
e94ec86a-6643-58b4-a952-538cdfee263a | note | Acceptance Criteria - Workspace and materials clean and dry
3a829f7a-d562-5138-913c-a014774bfadc | note | Verifying Documents - Visual inspection
658e117b-746e-4b70-adc5-170cc9bd5d28 | checkpoint | Pipe Jointing (2)
287183bf-bcc5-58e9-b8e0-eeb920e46354 | note | Activity Description - Completed Joints
dfa17a8b-d181-5609-8ff2-b847568561b1 | note | Frequency - At completion of jointing
abb35650-a2e2-5476-89e3-a6fd3545d04e | note | Inspection / Test Method - Inspection
cc109cc2-25a9-5ed0-b56f-5895f64f329d | note | Acceptance Criteria - All fittings snug and firm no movement or leakage to Manufacturers' requirements
95879177-1be5-5ce2-87b7-7f8f59a9724d | note | Verifying Documents - Visual inspection
ede7bde2-9952-42cd-9e23-5333004044fa | checkpoint | Joints at Manholes and other fittings
7420d8a3-3aa5-50ef-b07e-acf098199d91 | note | Activity Description - Spacing and type of joint
85eea99c-fdff-5e59-a56f-862a762fabc1 | note | Frequency - Prior to Backfill around Manhole
b4af5cd0-93e5-5060-9c63-52d25a604863 | note | Inspection / Test Method - Inspection
99b52685-d286-528a-bfcf-60357bef3a53 | note | Acceptance Criteria - Comply with drawings
d24b0120-b626-5748-ba15-541b7f54fb33 | note | Verifying Documents - Visual inspection
051a4af0-1116-46a4-b002-6ac69c3409de | checkpoint | Manhole Benching
425ce5fc-32ef-5363-a123-23565e351ac4 | note | Activity Description - Finish
973a6a0f-a7c9-5993-a9e8-d2486d162472 | note | Frequency - At completion of manhole
895a7871-0bcc-53ea-a5e4-a7a999c92ad9 | note | Inspection / Test Method - Inspection
2c2da1b9-8256-5631-a420-9f4858c61f19 | note | Acceptance Criteria - Smooth and minimum turbulence
6596f1e0-90ab-524d-b62e-1df9b323d58c | note | Verifying Documents - Visual inspection
0ba9592e-d335-4a96-b231-4e8f06f18df2 | checkpoint-no-value | Tolerances - Refer Section 3.5
1a276030-0309-4a8b-887d-b0a558a8ac24 | checkpoint | Horizontal Tolerances
cc57e73d-21df-56e4-876e-970cf5818776 | note | Activity Description - Manholes and Structures
8a25d555-983d-5e33-8c5d-b76137895ce6 | note | Frequency - Set-out and Installation
e1a5f341-3e9b-5fa2-bf11-26d81bcccee7 | note | Inspection / Test Method - Survey
1dd3bb15-95d4-53f2-9195-8e1435836fcc | note | Acceptance Criteria - +/ – 100mm of design or where applicable +/ – 50mm of design
549a8ab3-4cba-5e22-9ed4-3c452ff06a21 | note | Verifying Documents - Asbuilts except where re- design is necessary
ea3e6219-97de-4f0a-b18e-3c599635a8a8 | checkpoint | Vertical Tolerances (1)
5f33303c-137b-5dce-b74c-3bd787a4c90b | note | Activity Description - Invert Level
b40c4827-e8ee-577f-b1e7-cb44abada494 | note | Frequency - Set-out and Installation
9e5c5ef1-5955-584c-a33f-ad457adcb0b0 | note | Inspection / Test Method - Survey
12458723-c01c-5347-ad0b-5bad8c42992a | note | Acceptance Criteria - +/ – 25mm of design level
60074593-fbb7-53cc-844c-c8c322ec87a1 | note | Verifying Documents - Asbuilts except where re-design is necessary
0966650d-04e5-4460-a97e-e6e1d8d5fa30 | checkpoint | Vertical Tolerances (2)
25795ccc-d1d3-5ab6-84b8-e100766c1851 | note | Activity Description - Pipe Grade
d081bd65-985f-53b9-8d52-91617d675a26 | note | Frequency - Set-out and Installation
8c02b0b7-fe3f-5a7d-a0d7-89b095e7d0fc | note | Inspection / Test Method - Survey
249fb39d-02dd-503f-b864-c18baf1a7098 | note | Acceptance Criteria - +/– 10%
64feb4a0-c206-582c-b127-d6ac6db36ea7 | note | Verifying Documents - Asbuilts except where re- design is necessary
8cd72661-21a8-4987-a9eb-828b7d508d21 | checkpoint | Verticality
2efc2dc1-26d5-5a1b-aa0c-5aa803997ceb | note | Activity Description - Structures and Manholes
d2f8e367-85c7-594a-ab45-865dd21e984e | note | Frequency - Installation
e517db3b-158c-5499-becd-697df1ba9bcb | note | Inspection / Test Method - Measure
1b105c89-8032-5664-81ea-a3731be89c46 | note | Acceptance Criteria - +/- 10mm /1m
920a7c87-92cb-567c-8f65-b2c4dae26e60 | note | Verifying Documents - Visual inspection and measurement on site
39531bbc-9e29-4fa9-b583-f5e6075b96ee | checkpoint-no-value | Inspection and Testing - Refer Section 3.6
a3fe00de-af10-47ce-833f-20cc13be9061 | checkpoint | Leakage Testing
32a4a019-3e8a-5f96-bb28-8797664203bd | note | Activity Description - Pipes and manholes
b08f2e3b-0962-597b-864e-8da119a92b7a | note | Frequency - Completion
11f369e4-2f0d-5578-84aa-92447b6d0fa1 | note | Inspection / Test Method - Low Pressure Air or hydrostatic
737cd07d-eab2-58e1-8b9d-09ed374a00e5 | note | Acceptance Criteria - Holds Pressure
943e3fed-7000-57d3-ba62-5f4393935029 | note | Verifying Documents - Test sheets from the Contract to be completed - Engineer to be present for testing
ab4c036f-a40e-5f7a-8723-e5bb003cf3ca | note | Engineer / Client - H
e4373308-b355-4f5b-b48a-2c7595e5e04c | signoff | HOLD POINT
684bd8be-210e-4eb9-a96f-4562075bd805 | checkpoint | CCTV or Internal Inspection
2311c1cc-a74c-5f54-b84e-5d72a881a80c | note | Activity Description - Section 3.6.5
2c827dbe-a22a-58a6-920c-fae486e42f39 | note | Frequency - Completion
90f2dd43-deb4-5557-a901-470635990357 | note | Inspection / Test Method - Inspection
5f9f9327-5e44-5dc6-a9a6-93bb1f58327b | note | Acceptance Criteria - No significant defects
8d3cb6de-7491-547d-bab9-a6f9a5d0f8b3 | note | Verifying Documents - CCTV to be provided prior to Practical Completion being issued
f17ffa4d-081e-5d1a-928c-670ee8cd7325 | note | Engineer / Client - H
d1bb0119-87e3-44b9-968a-fa9c5c34b1e8 | signoff | HOLD POINT
9e35a158-c4a8-45f4-bfd8-380cd27f2a2b | checkpoint | Concrete works
46c32aa3-1244-562a-bd2b-92de0e4359ea | note | Activity Description - Section 3.6.4
007fa039-b61c-510e-ba3a-4a7e01a9c57c | note | Frequency - Installation
4c6faa57-3c26-5fe0-9375-681e00c426ae | note | Inspection / Test Method - Lab testing
6a3fcd3d-76f4-57d8-a119-68bc2a8baedd | note | Acceptance Criteria - NZS 3104
416e16a4-1558-539a-b188-02bc5e4a9dfc | note | Verifying Documents - Test results to be provided
40c2d664-52bc-5181-9710-7d69a47a05a1 | note | Engineer / Client - H
a82e6198-d7ac-4094-aea1-e735e4f05d71 | signoff | HOLD POINT
c6d38aeb-df99-4a7a-b9a8-4c72902f647f | section | 7 - Pavement Construction
39c13484-c38a-4328-afd3-9f07fd730cba | checkpoint | Earthworks
59d7c777-196e-557a-a3da-5c538fdd532f | note | Activity Description - Set-out level and alignment
faacf434-23c6-5c73-89ef-f76996d3f7f8 | note | Frequency - After excavation and prior to sub- base construction and/or laying filter cloth
e8653ec5-7d18-5665-9fdd-474b3b14e594 | note | Inspection / Test Method - Survey check, and string line depth check
24a9e029-cd2a-5e45-9326-1c551f17ed92 | note | Acceptance Criteria - Horizontal -20mm / + 100mm Vertical -20mm / +5mm
cc4a2014-880d-5926-92e4-a7bfdc6c7788 | note | Verifying Documents - Survey & data sheets available for review
a44e56a4-31e2-44be-8546-9cefaa039100 | checkpoint | Sub-base layer construction (1)
fd9e2f44-2e4f-5f57-be9c-442c24745bc4 | note | Activity Description - Imported sub-base aggregate
59eb0a94-091a-557d-8b49-41d8df1d6312 | note | Frequency - At least 10 days prior to construction
3e5a7f1c-6e3b-5f73-81f9-1353496c0962 | note | Inspection / Test Method - Lab testing
c8dac4c7-7e52-53a0-bdf4-776e41eeedc2 | note | Acceptance Criteria - NZS 4402
09f33fb6-8156-57f8-9ccb-e44cea76489b | note | Verifying Documents - Test Results - criteria should be overlayed over the results to demonstrate that the material complies
c89a5b87-19c7-5310-8d05-e55785d866a9 | note | Engineer / Client - H
1c992c76-6785-4d57-aeee-25da8f309ba6 | signoff | HOLD POINT
78295536-3952-4397-82d2-5bfa862e6c53 | checkpoint | Sub-base layer construction (2)
7da3b68b-fc25-59e3-81c9-f89b3bf44078 | note | Activity Description - Set-out level and alignment
a3aad418-e9fe-5c40-9ad7-af4e995a43f0 | note | Frequency - After sub-base construction and prior to forming topping layers
2e4846b6-6d7f-5d95-bba0-aa043674abf0 | note | Inspection / Test Method - Survey check, depth check
9bd5e4f6-43e5-5c64-9548-882d358fe3ea | note | Acceptance Criteria - Horizontal: -20mm / +100mm
8978b8d3-523a-58e1-98e8-5493e760a326 | note | ○ Vertical: -20mm / +5mm
f640c58d-203e-5d7a-a7ae-7c2b62895416 | note | Verifying Documents - Survey & data sheets available for review
190d2a58-a478-4332-96d5-f47ed8b76960 | checkpoint | Sub-base layer construction (3)
acbcb90d-ee52-5498-aee9-1d90f82f1dbc | note | Activity Description - Compaction
47e4aa8d-e29c-5671-b47d-f6e0cac72476 | note | Frequency - After sub-base construction and prior to forming topping layers
7afdc08d-01a5-5fb7-bd79-ea961d6aa688 | note | Inspection / Test Method - Density testing
615358e0-0f7f-5ecf-b0e4-0bdf3aa54588 | note | Acceptance Criteria - TNZ B/2 – Clause 7
723af306-6585-5194-a455-9d9dfef49aeb | note | Verifying Documents - Test results - should also show the design criteria to demonstrate that the work complies with the design
4f84647f-7bf9-5633-827b-9cdcb4bbf064 | note | Engineer / Client - H
04ac47e0-8d01-4ea3-b2a1-20c8a295a12a | signoff | HOLD POINT
e278d62c-57a6-43d5-9d22-4a23a4440986 | checkpoint | Basecourse layer construction (1)
2695043a-9d8f-5772-a06b-aa291000302c | note | Activity Description - Basecourse aggregate grading tests
85358a6c-9062-5239-b442-1789a542491a | note | Frequency - Annual source tests, pre- delivery tests results to Engineer 10 days prior to use
785f3741-121e-53f9-ae1e-dfa792f1f1a0 | note | Inspection / Test Method - NZS 4407: 1991
a7db0627-c691-5f1d-90e2-52c443cd6fd5 | note | Acceptance Criteria - TNZ M/4 – Clause 4 Table 4 (Napier River Gravels)
c1bea3ff-0469-511f-8dcb-97833c959f42 | note | Verifying Documents - Test Results - criteria should be overlayed over the results to demonstrate that the material complies
07adc2a4-0ab5-59bb-8155-18da219b3073 | note | Engineer / Client - H
4503cfa0-c1d6-40ce-91c5-25161e4ecd5f | signoff | HOLD POINT
9b7f2e46-cbc8-4253-b6c2-2f521189f460 | checkpoint | Basecourse layer construction (2)
cedfd3fd-3c19-5abc-8751-48d05fc5a943 | note | Activity Description - Level and alignment
d7831c0b-83f9-5d44-b09b-31720c8f0428 | note | Frequency - After basecourse construction and prior to forming topping layers
550d0120-d27f-5cde-b024-cca38880a84f | note | Inspection / Test Method - Survey check, and string line depth check
b67ff012-8d96-59c1-b293-01af4c5d73e6 | note | Acceptance Criteria - TNZ B/2 – Clause 5
5ae243f8-b7a9-5aea-81c0-1dbef8538281 | note | Verifying Documents - Survey & data sheets available for review
fa6a086c-4407-4808-b5d9-845f1a798329 | checkpoint | Basecourse layer construction (3)
c0cc890d-132e-5058-a2af-54b1519ff298 | note | Activity Description - Compaction
e0ad905a-38ed-5c9b-abbe-6f715abd3a60 | note | Frequency - After basecourse construction and prior to forming topping layers.
1bcb0282-bc09-572e-86ab-41352ecef5c4 | note | Inspection / Test Method - Nuclear densometer density testing
5ed25269-ae3d-5280-9c60-9d67a6159e99 | note | Acceptance Criteria - TNZ B/2 – Clause 7
1cea3866-d2fe-50a5-b41f-6efd3fe24cba | note | Verifying Documents - Test results - should also show the design criteria to demonstrate that the work complies with the design
34ecfe85-0c54-581d-a2ab-4aced930d432 | note | Engineer / Client - H
bf478859-8cb3-4155-87a4-3219cc7c25f3 | signoff | HOLD POINT
9ecec579-7e0e-4afb-9bfb-1709638898ba | checkpoint | Basecourse layer construction (4)
97facc10-e442-5bf5-a3dd-6a24c061f560 | note | Activity Description - Compaction
2b70b3f0-2879-5055-836f-c8be5164df6f | note | Frequency - After basecourse construction and prior to forming topping layers.
2feafd89-9a31-5c6b-ab0c-106faea4f4d2 | note | Inspection / Test Method - Clegg impact test
b7ec8f71-76b4-562e-a7ba-a14b45da4ef3 | note | Acceptance Criteria - Refer to Section 4 below
c1ce4a44-3b63-5746-9acb-0c0f6a870e63 | note | Verifying Documents - Test results - should also show the design criteria to demonstrate that the work complies with the design
4b1512d3-6417-551a-9c04-1a77c0548eb7 | note | Engineer / Client - H
3b5ae813-b7ad-4972-8a87-7f063a8c9c72 | signoff | HOLD POINT
b68afc5d-5580-4e6e-a1a7-a4f32d7986ed | checkpoint | Basecourse layer construction (5)
a71fd9b9-20dd-50ff-99ca-06d706a26cf7 | note | Activity Description - Surface shape
10e833e9-57b9-5fe4-9293-c0c051439e10 | note | Frequency - After basecourse construction and prior to forming topping layers
b1e486bb-be7d-5058-9e6a-da46b2161bff | note | Inspection / Test Method - 3m straight edge, string line check
1aa3b883-f2da-5202-8f34-bec3b93c6ad8 | note | Acceptance Criteria - TNZ B/2 – Clause 7
11b5f8e7-903b-5980-b8b5-daea963c6f76 | note | Verifying Documents - Density and DOS Test results and Data Result Sheets, results should demonstrate they comply
3f7ba58d-d9c6-5535-adc3-fa951f6e8dd7 | note | Engineer / Client - H
4ae000ff-c39a-4fb2-9d28-d49ad6b76982 | signoff | HOLD POINT
79b042dc-3db9-4a8a-ab9a-1e7ddacc36dd | section | 8 - Kerb, Concrete Path & Landscape Construction
517a463e-7874-458d-a34e-2a57728cb020 | checkpoint | Earthworks
f45479e5-2f76-5ad9-8a4e-cde2d280ba11 | note | Activity Description - Set-out level and alignment
19be212f-93e3-559d-9394-90cf983ab827 | note | Frequency - After excavation and prior to sub- base construction and/or laying filter cloth
e5d283e7-f52c-5a60-a65d-4933ab9ca258 | note | Inspection / Test Method - Survey check, depth check
cc88e227-cb41-5a59-ae6a-6cdd5a8f712c | note | Acceptance Criteria - Horizontal: -20mm / +100mm Vertical: -20mm / +5mm
23c7337e-08a2-5f7e-aac7-dfe60cd3fc21 | note | Verifying Documents - Survey & data sheets available for review
218a7198-57bd-4d41-9c3a-a46ebb948024 | checkpoint | Basecourse layer construction (1)
ed925f48-23f1-58ce-9002-cf97e8751db9 | note | Activity Description - Basecourse aggregate grading tests
58f93dc2-e276-5434-825e-a669cd643cda | note | Frequency - Annual source tests Pre- delivery tests Results to Engineer 10 days prior to use
b73f36bc-faff-569e-a35d-dcba32b38074 | note | Inspection / Test Method - NZS 4407: 1991
b00f2400-ee24-5c05-acbe-a066ebae90d4 | note | Acceptance Criteria - TNZ M/4 – Clause 4 Table 4 (Napier River Gravels)
3e7f9526-0116-52b9-91d6-642f85db3b33 | note | Verifying Documents - Test Results - criteria should be overlayed over the results to demonstrate that the material complies
dda7b546-f26c-58a7-9556-1095e7cd5071 | note | Engineer / Client - H
c2eb8474-b744-49be-8b54-8bed8a3b563d | signoff | HOLD POINT
3f373514-878a-49f5-a8f8-bdb5d9e51d11 | checkpoint | Basecourse layer construction (2)
b2269965-f9d5-5036-a376-9323da75f011 | note | Activity Description - Level and alignment
38dc3a05-4ffc-52c6-87bd-2649322b1749 | note | Frequency - After basecourse construction and prior to forming topping layers
f3a9c828-dd9e-53b6-b835-7d467c3f5500 | note | Inspection / Test Method - Survey check, depth check
ffe7d650-2dc1-5bb0-a3a5-7c7e2ffa824c | note | Acceptance Criteria - TNZ B/2 – Clause 5
fe7e78aa-4e9e-5fdb-b951-3c69ff887ce5 | note | Verifying Documents - Data Sheets available for review
f97e8391-c26b-42cf-9554-d29350d91910 | checkpoint | Basecourse layer construction (3)
834ea3b9-78c6-5339-824b-2f2babf741a6 | note | Activity Description - Compaction
acf9ffe7-be6f-5dc4-b382-597342dcd7dd | note | Frequency - After basecourse construction and
65664976-7d07-586f-9ace-a99986750a9a | note | Inspection / Test Method - Nuclear densometer density testing
43aa1463-bdd2-5231-b352-2de54e9109d0 | note | Acceptance Criteria - TNZ B/2 – Clause 7
3cf6132e-1591-5bd0-93d9-8388cb570780 | note | Verifying Documents - Test results to be provided to demonstrate they comply
1cacbd60-69a0-57ce-a173-69d866191e5f | note | Engineer / Client - H
7a5c6d5b-3a12-4c94-94da-d1a5512e2278 | signoff | HOLD POINT
af7753f4-f509-4a35-8afd-98892bd4e0ed | checkpoint | Basecourse layer construction (4)
d222e239-c3ab-5ffb-a467-49f3c973689d | note | Activity Description - Compaction
abdcf721-ac32-5162-a911-6aae7690b7f3 | note | Frequency - After basecourse construction and
a195d606-d506-5808-8267-a01fe98c078d | note | Inspection / Test Method - Clegg impact test
6c6c5d9a-c7a1-57b5-9ddb-6642b9ade9af | note | Acceptance Criteria - HDC Specification Pavement Construction: Section 4
35b04c11-e69e-50a0-8efd-cafd9836211e | note | Verifying Documents - Test results to be provided to demonstrate they comply
45f61cf9-f4ba-5bb0-9b24-ab1613b9798b | note | Engineer / Client - H
e269bb6e-fc93-4dc8-aaf1-7d736b61f4f3 | signoff | HOLD POINT
19f8296c-1e80-4c0d-b7e0-de706c215093 | checkpoint | Basecourse layer construction (5)
af8ce578-ead7-5a89-99c9-e2ebad2623d3 | note | Activity Description - Surface shape
b977542d-ac86-538f-aa8c-8746067c35a9 | note | Frequency - After basecourse construction and prior to forming topping layers
17bed8d9-e8ff-56f6-af6a-d8ed6fef8963 | note | Inspection / Test Method - Survey check
c9661b5b-e1aa-5d59-9511-74552d677161 | note | Acceptance Criteria - TNZ B/2 – clause 5
d9aa71ff-b99d-52ce-8e14-70cfe154c98d | note | Verifying Documents - Result Sheets to demonstrate they comply
f459984f-22e8-5439-ab35-e0d4e3c3ccd9 | note | Engineer / Client - H
62f2068f-3c91-4359-a0c0-819ed624eef0 | signoff | HOLD POINT
3e7370b7-a6af-4da7-a1cf-34a66e889204 | checkpoint | Kerbing
a118f5e3-ddf7-5ec1-8222-bf01589e40dc | note | Activity Description - Set-out level and alignment
bfd59224-cb19-5443-b60b-35ee5e95b2e9 | note | Frequency - After base construction and prior to placement of concrete
029da09a-2fa6-5409-a891-0da258d78a18 | note | Inspection / Test Method - Survey check
9c033d4a-d9b9-5980-b6f2-9ec2a04ec211 | note | Acceptance Criteria - Horizontal: ± 20mm Vertical: ± 5mm
9fb6abb9-b99b-5c21-b8c7-feb75ce7b98a | note | Verifying Documents - Survey & data sheets available for review
9b99b674-58dc-45ab-8817-d08b42fb9d49 | checkpoint | Concrete Works
34827aee-ffc2-55db-85c7-fa3357e4632f | note | Activity Description - Section 2.1
f074b260-5639-5c70-8c06-67e7b0f93db2 | note | Frequency - Prior to placement of concrete
9ccdeb62-138f-5244-a52a-015d5f95be8a | note | Inspection / Test Method - Lab testing
3ea2f8ee-11e5-53e5-95ba-d26256360249 | note | Acceptance Criteria - NZS 3104
8286232d-996d-5e5d-b405-de082ca3e197 | note | Verifying Documents - Test results to be provided
c4a648be-26b4-5673-a461-e7bb09b1361e | note | Engineer / Client - H
95576985-98f0-4313-a61d-c738e66d757c | signoff | HOLD POINT
2465e4fd-a0b7-400c-bfaa-a1f45d4df436 | checkpoint | Paths
6f47f81e-1164-5afb-bfe6-7f38bd4859d7 | note | Activity Description - Set-out level and alignment
a10e8749-8d94-5118-97ac-d155b3e7f8db | note | Frequency - After base construction and prior to- placement of concrete
71f30b47-9fc8-5b2d-b641-20114075f5cc | note | Inspection / Test Method - Survey check
4df06e67-2b4a-57d0-977a-b4e39c97410d | note | Acceptance Criteria - Horizontal: ± 20mm Vertical: ± 5mm
6dfaddf6-0372-564a-b9f5-7f2bae7c8184 | note | Verifying Documents - Survey & data sheets available for review
74025ac7-005e-4872-92f7-d732d8b972c7 | checkpoint | Prepping on for grassing
cc4329b2-42e5-5a7f-b8d1-3b55ee42918c | note | Activity Description - Set-out level and alignment
353195d9-76e6-56cb-9947-a306636c17fd | note | Frequency - After base preparation and prior to- placement of top soil
d08d452d-b9a2-5ca8-a2b0-106e20326216 | note | Inspection / Test Method - Survey check
a5f68215-eb3c-5e01-b7ea-41281a3378ee | note | Acceptance Criteria - Horizontal: ± 20mm Vertical: ± 5mm
8db80100-d41b-532a-97c0-d6f137f36b07 | note | Verifying Documents - Data Sheets available for review
6a171d5e-88e7-466b-8737-debf1ce12a72 | checkpoint | Insitu seeding and turfing
6aec5b5b-d525-52f2-846c-39b4468824aa | note | Activity Description - Suitability of soil
68c5c23a-c906-5f01-a3b3-dc5a1413f073 | note | Frequency - After placement of top soil and before grassing
c454d25c-de67-5446-951a-4150aeb5b86b | note | Inspection / Test Method - Visual material check
bccd66ed-1c45-5369-ab40-547e26b8d99e | note | Acceptance Criteria - Soil is free of weeds, stone and other hard materials
1da3d3f8-4bfc-519c-aef5-aa70abaafe45 | note | Verifying Documents - Visual inspection
fd9cbd14-8e71-496a-aa2a-d4d7bf243b0c | section | 9 - Adjustment of Service Covers
f8b8dd20-eac7-4066-ba54-446e2a6d2fcd | checkpoint | Service covers and manholes in road (1)
ac7a40a5-2954-513c-9182-44902e50ee14 | note | Activity Description - Level, securely fitted and clear of debris
2a515bc0-cd73-56e6-b067-bc67fe04bc77 | note | Frequency - After basecourse and prior to sealing
d1ca98c4-4b99-5bd5-9de0-3f8e071df8d2 | note | Inspection / Test Method - 3m straight edge laid on final surface
eb4d7baa-9db5-5355-9ed5-85e50afc7391 | note | Acceptance Criteria - Vertical: +10mm and - 0mm
14d169d4-4523-522c-a26e-9c331e0259c4 | note | ○ Reinstatement of pavement to match adjacent levels
70496ebf-a0b3-5fc0-9e4e-a2a5876a8c2d | note | Verifying Documents - Visual inspection
0ca3586a-9502-4ff9-b324-52d73f2011d6 | checkpoint | Service covers and manholes in road (2)
268b1db5-ffa7-5cac-9f47-94e42700f155 | note | Activity Description - Level, securely fitted and clear of debris
f4f9b98a-a316-5e2f-9613-a67b908ee413 | note | Frequency - After basecourse and prior to sealing
0e93382e-1bbd-5425-b5a0-2efc43dfe02d | note | Inspection / Test Method - Visual inspection
b74c7216-0968-5226-b204-499436209d80 | note | Acceptance Criteria - Access and internal space is clear of debris. No rocking
be3f9248-7034-517a-8354-aab85739f253 | note | Verifying Documents - Visual inspection
bd0646b8-d40e-4aa3-9af8-6bf76275ce1a | checkpoint | Service covers and manholes in path (1)
3d64e5f2-ae0d-59fc-8857-83d4cc2ba582 | note | Activity Description - Level, securely fitted and clear of debris
6a499ff9-dea4-5abf-8242-7add631dadc9 | note | Frequency - After basecourse construction and prior to concrete
0c8e518e-191d-51a1-a4c7-d9ed3cac5648 | note | Inspection / Test Method - 3m straight edge laid on final surface
664e3542-6483-5670-9dac-c96b56044787 | note | Acceptance Criteria - Vertical: + 10mm and - 0mm
58e3e84a-3542-515e-83a3-543db719668f | note | Verifying Documents - Visual inspection
e46e4cce-86c3-4876-acb4-1c0de8910b1f | checkpoint | Service covers and manholes in path (2)
58f46dd8-d209-54c9-af21-85161751f66e | note | Activity Description - Level, securely fitted and clear of debris
daa4c5a8-4e0a-5971-938c-4fe7cceb9f9e | note | Frequency - After basecourse construction and prior to concrete
71c366a4-b31b-5ca4-a803-458bdd587beb | note | Inspection / Test Method - Visual inspection
b118f8ff-874a-5061-b3a6-96ffdc135fb9 | note | Acceptance Criteria - Access and internal space is clear of debris. No rocking
bd1e1426-7c1a-5133-82c8-8a8ec187e8cf | note | Verifying Documents - Visual inspection
1810ce7b-7191-4495-b704-7080cc407452 | checkpoint | Service covers and manholes in berm (1)
7d581b13-6ccd-5921-a88e-0d2eabeb65a7 | note | Activity Description - Level, securely fitted and clear of debris
5e31afc3-5bd0-54b8-bb37-8dd0ccfa76e3 | note | Frequency - After topsoil and prior to grassing
e332e510-4563-52eb-9f9c-e6cd7000218b | note | Inspection / Test Method - 3m straight edge laid on final surface
664493a2-a0f3-58cf-8387-85b7538154b3 | note | Acceptance Criteria - Vertical: + 10mm and - 0mm
1ad738df-dc40-575d-9d12-5ee0047e0f2e | note | Verifying Documents - Visual inspection
b1f7b938-bef4-4ce3-b604-c05e3c139794 | checkpoint | Service covers and manholes in berm (2)
546cad58-d9a3-567a-8b72-74522930e8e4 | note | Activity Description - Level, securely fitted and clear of debris
1e12c48d-6661-573e-8182-e837b8c2cc89 | note | Frequency - After topsoil and prior to grassing
30247501-8b2f-5a82-a9a2-5103a43adbe8 | note | Inspection / Test Method - Visual inspection
6f50414a-789d-5e2b-8c15-285bb7e125f2 | note | Acceptance Criteria - Access and internal space is clear of debris. No rocking
68df0e0b-b49d-5e9a-825d-04cb2a620029 | note | Verifying Documents - Visual inspection
9b61b990-1092-4f0b-9fb9-73f5d190ac98 | section | 10 - Surfacing Construction (Evenden Rd)
bb39d6fc-7501-4008-8c6e-f2a1db9e471e | checkpoint | Surfacing Materials
8966f2e3-1614-5fcf-a347-f467f33d2595 | note | Activity Description - Materials
a6e53c53-639a-5aa3-ae11-f65bfd845f3c | note | Frequency - Prior to surfacing
8f367a63-18de-56df-9f23-bbfa5dbefa93 | note | Inspection / Test Method - Supply of surfacing materials (chip test results, asphaltic concrete materials)
7d165113-ab81-51f2-bedc-ac654892ff94 | note | Acceptance Criteria - NZTA M/6: 2011 specification for sealing chip NZTA M/10: 2014 Dense Graded and Stone Mastic asphalt
539e5f58-9597-5f4f-b33d-5322f75250c9 | note | Verifying Documents - Test results to be provided to demonstrate they comply
42a79996-3d69-5823-903c-0a1c35ed177d | note | Engineer / Client - H
c24b1be2-b75a-4d65-a036-a71f90efabfd | signoff | HOLD POINT
32fbf3a9-b2a9-46ac-a223-3e9685385f9d | checkpoint | Surfacing Design
6530b365-7a5a-55fd-a566-b5667835137b | note | Activity Description - Design
2179899e-8095-5521-b25e-55da5fa6a4b4 | note | Frequency - Seal design prior to sealing.
60ae34a4-9e7e-5449-a7b9-c85ed04407f3 | note | Inspection / Test Method - Chip Seal Design/JMF
567b4bc1-648c-5ea5-a0fd-0f88459cb484 | note | Acceptance Criteria - NZTA P/3: 1995: specification for first coat sealing NZTA M/10: 2014 Dense Graded and Stone Mastic asphalt
7aa38c0e-645f-551f-ada0-afb494b3b429 | note | Verifying Documents - Design provided 48 hours prior to application
e4b0f1bc-aad3-5ce9-a7ed-16c0080d4a72 | note | Engineer / Client - H
5e68ffb2-c032-40fd-988d-3ef020efc82a | signoff | HOLD POINT
bb047b24-a61c-4a37-886f-9980f40f20c4 | checkpoint | Sealing works (1)
34f8ff22-0f1a-54ce-b64a-73bbb670c7c2 | note | Activity Description - Preparedness for sealing
bc9db761-6368-5ed0-9c8d-31e341b113c7 | note | Frequency - After sweeping and prior to sealing
012ec344-8f74-516e-9d07-8fe3b2ab31ee | note | Inspection / Test Method - Visual check
1e50a06d-a841-53dd-b31f-42ffb3ed7fce | note | Acceptance Criteria - Clean aggregate mix exposed to accept binder coat
bb68bf45-3e63-52e3-854e-5ef470fde828 | note | Verifying Documents - Visual inspection
9c2b03ab-a65f-5bbd-930a-dbd60919bd30 | note | Engineer / Client - H
691fad30-d3b3-42f5-83f2-8d98b3aed960 | signoff | HOLD POINT
4c80f6ed-58fa-444a-9a08-4694bb761177 | checkpoint | Sealing works (2)
1fa31cc9-c6d9-536a-a20b-e927b23eb4f7 | note | Activity Description - Reporting
ab4edb6b-6249-5e1e-abbc-86440c1cdf3d | note | Frequency - Seal reports on completion
379295b3-31ca-5ba6-a18d-fe9448848a5b | note | Inspection / Test Method - Construction reports
72c1aa6c-c9e4-5c1e-9756-c73dddd178e6 | note | Acceptance Criteria - Meets construction tolerances Services covers exposed and marked. Service boxes clean and fit for use
73db1a2b-0b5f-4baa-a038-a5183747500f | checkpoint | Sealing works (3)
76e208eb-5589-5c79-9790-8437d818f7e1 | note | Activity Description - Service lids and covers
b7fc1893-f5e2-5563-90c1-77f6fd7d9e5e | note | Frequency - On completion of sealing
ddc5fde3-a537-5d0a-8a72-5543d501efd0 | note | Inspection / Test Method - Inspection of service lids and covers
3456ace2-1d63-5c1d-ac53-b9cb13043854 | note | Acceptance Criteria - Temporary floors removed from all manholes
cb03b164-fd3e-5954-8911-2900b3e4ba92 | note | Verifying Documents - Visual inspection