## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | [Rename] Document Upload Checklist |  | [Rename] Document Upload Checklist |  | 76c6cdce-e3d9-41a3-8540-d3cda204792b
| checkpoint | Document Uploaded Below
| checklist | INF-HSEQ CC0398-ITP-002 Bulk Earthworks REV D | itp | INF-HSEQ CC0398-ITP-002 Bulk Earthworks REV D |  | c49b5c58-0a77-4f97-93e4-48886035b4bf
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Determine lot size
17c2ed7f-6649-5816-b0d9-c9f08c804f2d | note | Acceptance criteria - What is the lot size?
939eeafe-eea4-5169-8369-1b238759f0fb | textbox | Acceptance |  |  | m2
d7856abb-22da-55e1-ac94-131e27f59581 | note | Key - S
3f5c9f41-ba36-59f3-aa3e-d7d953263178 | note | MDR/VIVA Key - S
| checkpoint | 1.2 - Survey set-out
95c23751-464a-5c23-8c42-6c4475203c53 | note | Ref docs - 235929 IFC Drawings
a003dc98-8074-5f09-bf30-347080541f43 | note | Acceptance criteria - Has the work area been set out for line and level?
414fc0b9-d0aa-503a-8b72-1acc0142d5e7 | button | Acceptance | Yes,No,N/A
244e5a50-04fe-53a3-996b-948074e374a1 | note | Key - S
87ade986-a2da-519e-a4d5-964d14d3564b | note | MDR/VIVA Key - S
93a9bdc1-186a-52b6-a29c-66d2021e49f0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
5feb5bf7-0aac-5792-a0c4-02653b7d41cf | textbox | IFC drawing number:
9f62bc1b-b9a8-564c-a937-859df44285e6 | textbox | Rev:
| checkpoint | 1.3 - Excavation material classification
a386b8ef-731d-5cf5-85fd-d2db39fe7f49 | note | Ref docs - 235929-000- CV-SP-00002
475ed1a0-a607-5f85-825b-1cafb9b13c08 | note | Acceptance criteria - Has the material being excavated been inspected with category agreed upon by Superintendent and/or Superintendents Environmental Representative?
39dfcc38-a132-502d-b61c-e070d7fa269c | note | Tick category below:
16d27692-38e0-575c-8923-9bee94e3c519 | tickbox | Common Fill (CF1)
c9acafa7-2d96-5355-b866-959295f39c36 | tickbox | Sand Fill (S1)
dc14a3b9-f0b4-5abf-89ce-46bb6222f428 | tickbox | Structural Fill (SF1)
48594622-3c27-5471-b593-1cc677bff502 | tickbox | Topsoil (TS1)
fdd39b43-d498-582a-af44-4616da946bd2 | tickbox | Reuse of Site Won material
c00254ca-c049-53a1-a7b8-1884a2c653d2 | tickbox | Rock
a54318c8-52cd-539d-88c0-f050911d3d4f | tickbox | Contaminated Material
1183bc04-d025-5e22-9ecb-27f15ba52dff | button | Acceptance | Yes,No,N/A
d2efc44e-4948-521c-a787-b6633d9f67ce | note | Key - H
7b586300-13bb-5686-abd2-dfda87b38f31 | note | MDR/VIVA Key - W
| checkpoint | 1.4 - Material Submission / Approval
a0176bd7-d038-5164-97ec-68460346314a | note | Ref docs - 235929-000- CV-SP-00002 Sec 11.1 Aggregate report
881c9d6c-e129-5c59-9257-eb9855179d9b | note | Acceptance criteria - Has any imported material (to be used as permanent fill) been approved by MDR for usage on site.
5d547fea-255f-56da-91aa-79525e69c8df | button | Acceptance | Yes,No,N/A
3be45e37-2c04-58b9-a4c2-d8753b2f82f5 | note | Key - H
0ab96b98-a950-5ce1-be24-24bc7efc1d34 | note | MDR/VIVA Key - H
4f0825b1-5d2f-581d-b3fe-bebcc0e8520c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
42e5086d-e728-57fb-b1df-376f7a475cd9 | tickbox | Material mix design
| signoff | AUTHORITY HOLDPOINT
| section | 2.0 Bulk earthworks – cut
| checkpoint | 2.1 - Subgrade preparation
079f5e68-cd67-56df-b0cd-3c707fbe5dc2 | note | Acceptance criteria - Has the area been excavated to top of earthworks layer.
7d15c849-32c2-5dd2-8314-4b8a1a458e35 | note | ○ Note: Existing surface material is approximately 200-300mm of crushed rock.
ded8d32c-22b4-56d2-978e-5e1449224d11 | note | ○ Is the surface evenly graded and free-draining.
443106d1-8ecc-5b77-8c79-0478f9a1e8f8 | button | Acceptance | Yes,No,N/A
a53716f1-44f3-559b-9222-3b3f49b71e3e | note | Key - S
543f0d46-93a3-5fb4-8c5b-c7498753c251 | note | MDR/VIVA Key - S
| checkpoint | 2.2 - Material Export / Stockpiling
743366f3-681d-5363-9d44-c0b79f0b780e | note | Ref docs - SMP 20359156-211-R-Rev
e8031a82-714d-5411-b201-9f3e72df01b8 | note | Acceptance criteria - Adherence to Soil Management Plan.
e142d24b-eeab-5ed9-9a2e-7c11f2d83c71 | button | Acceptance | Yes,No,N/A
b4742af9-5605-57e9-bd5d-53ecc9238a6b | note | Key - S
2e09c9db-4dc1-5810-8cda-c8b97f430d49 | note | MDR/VIVA Key - S
| section | 3.0 Bulk earthworks - fill
| checkpoint | 3.1 - Preparation of surface
247b5235-85c8-5547-b733-127f326c7585 | note | Acceptance criteria - Has surface been cleared of all loose material visible on surface.
94210f34-239e-5a10-859b-1ba3ee25fd17 | button | Acceptance | Yes,No,N/A
6d2f2968-c8a7-58ae-b197-1ea0492a2235 | note | Key - S
5986627b-044d-5721-98fc-f156ab469f1f | note | MDR/VIVA Key - S
| checkpoint | 3.2 - Compaction Trial for Blended Material
600de072-e43d-5d8a-8b29-310d6c0f9dd1 | note | Ref docs - 235929-PE- WI-000009 - Backfill Specification
6ef316aa-259f-5d74-990d-2ad22aa91172 | note | Acceptance criteria -
3265b67a-9766-5a39-8ece-21c60a190621 | button | ○ Is the material to be used for backfill blended material. | Yes,No,N/A
00f6c107-39d5-5e67-9602-24b0ca652853 | note | If No, go to item 3.3.
87ff2c05-68f2-5396-a1f1-7eb495a3802a | button | ○ Has the compaction trial been undertaken? | Yes,No,N/A
356fb490-cdc6-5a1b-b546-9af580793365 | button | ○ Did the compaction trial achieve the appropriate design backfill requirements of 70kPa? | Yes,No,N/A
3339ed77-d485-5166-a70b-2d70228c0523 | button | ○ Does MDR approve usage of site blended material for backfill purposes? | Yes,No,N/A
8f4995db-6b67-5ad9-b136-cd0a4dbb8d5c | button | Acceptance | Yes,No,N/A
7e239d07-0614-5b34-b811-48925eaf4a53 | note | Key - H
e5fd72dd-8075-5ba8-a67a-0ecc5afc56e7 | note | MDR/VIVA Key - W
5dfb2fbb-bad2-58e2-a061-7784fedb11df | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a51ec0d1-a2fb-5fd1-b764-ceb991274e3f | textbox | MDR approval:
0b7b470a-f52a-5f02-b88c-e9edcad8ceaa | textbox | (correspondence reference number)
| checkpoint | 3.3 - Fill Placement
119184bd-f636-5039-a4bc-8c3367637c5b | note | Ref docs - 235929-000-CV-SP-00002 Sec 12.2, 235929 IFC Drawings
8fe5cde6-7b3f-5a72-8946-3885580a2681 | note | Acceptance criteria - Has fill been placed in maximum 200mm compacted layer thickness?
e434c6a8-d8c4-59f1-8425-5c6dcfa01fdd | button | Acceptance | Yes,No,N/A
e1ba56e0-6c97-5bc7-8eb9-5cfd038ffa44 | note | Key - W
319a9a92-6fef-5c4c-a011-4dad984f2936 | note | MDR/VIVA Key - W
8238465d-3205-5dbd-8a22-5814f173459c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
| checkpoint | 3.4 - Moisture
bdf9774c-c3d0-504f-841f-a11c1fdddcfe | note | Acceptance criteria - Has the material maintained at +/- 3% modified moisture content, with additional water being added if required during compaction?
0f4d56a2-bda2-532b-9091-eafaab18f2b2 | button | Acceptance | Yes,No,N/A
bb7fa767-0045-5e73-a054-4da887129cfa | note | Key - S
34a0df43-7447-5733-ad0b-0dd2d99083ce | note | MDR/VIVA Key - W
28c50542-a9e3-515e-9348-931f076e399c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
fd4397c8-78db-561f-9d22-ae417982ce64 | tickbox | Test reports
| checkpoint | 3.5 - Compaction
8dd9625d-58f3-5dee-9a01-ee1f6a3e57f4 | note | Ref docs - 235929-000- CV-SP-00002 Sec 13 & Sec 14.2
2c1c660f-8f9f-5b23-be56-388e897a363d | note | Acceptance criteria - Has the layer been adequately compacted achieving a mean value of minimum 98% MDD?
1992ca89-242d-5eb6-84a4-40644a7ed472 | note | ○ Density test to be completed on first backfill to verify procedure. Procedure assumed to be equal henceforth (Inspector may request additional test upon insufficient density or compaction).
53ea1341-e06d-547d-9811-a95dfe9944cd | note | Acceptance -
546263c4-daee-50e1-b864-598846089603 | tickbox | Small Foundations
d51e168c-162f-5adf-bf72-52fdea3e663f | note | (1 test per foundation)
23220f2a-3f3c-57c2-b1d0-57f60b977850 | tickbox | Large Foundation
01aa0de9-31c1-5d45-aeb4-b608cb4902ed | note | (larger than 10m2) minimum 3 tests per lift
6436025b-dd51-55ff-9291-3dc905aa5e84 | tickbox | Fill Areas minimum 2 tests per 185m2 but not less than 3 tests per area
2ab8f6fe-1eb4-561d-84f5-4aa65506abc0 | note | Key - H
52be4b23-9644-5961-8d24-4cc6ca25475a | note | MDR/VIVA Key - W
acbbca5f-8ef6-587f-bf83-cd62e724f47a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a7f397a5-8ecc-560c-856b-3123b1ee5078 | tickbox | Test reports
| checkpoint | 3.6 - Fill layer – test rolling
fa9b9cb2-6e5c-5ab7-ae3e-35fcfc6dd76f | note | Ref docs - 235929-000- CV-SP-00002 Sec 12
c71e2bf6-058c-503c-b18a-b7a318ffa9a9 | note | Acceptance criteria - Does the layer withstand test rolling without visible deformation or springing?
a9285242-a497-526b-8026-b59279a7e060 | textbox | List Attendees:
e091273a-d4b8-5080-bf13-985e291dfac3 | button | Acceptance | Yes,No,N/A
8cbc68c6-937d-52ba-99a4-36cb9d70a2f9 | note | If 'no' please see below If 'yes' please proceed to Conformance Check
39c24a2e-6181-598d-89b5-7e85ebabfe9c | note | Key - H
441e742f-19dc-5f26-b13b-bb0253a4db09 | note | MDR/VIVA Key - W
c9e4d077-121e-5383-b93c-65cd02b4cb90 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
74ba581f-2fc9-5ce5-b627-f90f5236bd6e | tickbox | Proof roll checklist [235929-MG1668-CV- 003-SUBC-000053]
| checkpoint | 3.7 - Identification of soft wet or unstable material
95e5b108-fac5-5515-b8c0-cc9048cdb6c9 | note | Acceptance criteria - Has any soft or wet unsuitable material been found?
e010e420-4c20-55bc-98eb-15eb30ae9f9c | button | Acceptance | Yes,No,N/A
febfea7e-0b56-5b46-8dc1-237eac1d2d42 | note | Key - W
80d09676-4e64-50f1-87bf-572b396ef562 | note | MDR/VIVA Key - S
| checkpoint | 3.8 - Treatment of unsuitable material
7623fbb6-0b92-5c0e-acd8-4fa1c88f85a5 | note | Ref docs - 235929-000- CV-SP-00002 Sec 12.1, Symal Proof Roll Procedure Doc
0526dd2b-c120-5c17-857b-56d93c49baa5 | note | Acceptance criteria - Have any issues been determined?
44dcaf17-29d8-5dcb-b903-396ebbd75e82 | textbox | (length) |  |  | m
f2c2b076-ad13-5148-9185-a729d9f65fd5 | textbox | (width) |  |  | m
498a0a65-ffd3-5383-9400-4d9a02b89f6f | button | Acceptance | Yes,No,N/A
6a2b81fc-9995-5f0f-bde7-357d0f7e278d | note | Key - W
8ce4edd9-e6a3-5cf4-bac8-f7eb4d94ab9b | note | MDR/VIVA Key - W
c1711777-6c0f-538d-94d4-5734d8e221ef | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Proof Roll Checklist, Dockets / Photos
| section | 4.0 Conformance check
| checkpoint | 4.1 - Subgrade level and shape
4a32164d-617a-5d45-b7d9-c8c2d2c62728 | note | Ref docs - 235929 IFC Drawings
1ec92379-64a0-51e5-8d42-44d7d51ad26b | note | Acceptance criteria - Has the prepared subgrade been surveyed in accordance with and verifying specified requirements?
9d26e3ab-8309-5a70-8eae-6226750a50af | note | ○ Final grade +- 60mm
57c34ad4-27ed-57c5-9994-5f4ed7d17c25 | button | Acceptance | Yes,No,N/A
78001b3d-1342-56e5-a5f7-0ddd17672814 | note | Key - H
19578b77-12aa-50e7-a3a6-6215b317b037 | note | MDR/VIVA Key - W
60c3c6fe-2e3a-588b-9791-af591495ee2e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
86e2d997-539e-568a-a7d5-4b04bc121298 | tickbox | As built report
5f382c3b-f132-5b5c-875d-59a7be186117 | textbox | IFC drawing number:
ad5daabb-5230-587b-bce5-a329176f6c59 | textbox | Rev:
| checklist | INF-HSEQ CC0398-ITP-003 Base Pavement Construction Rev 1 | itp | INF-HSEQ CC0398-ITP-003 Base Pavement Construction Rev 1 |  | c2d50d7f-6b8c-4b90-9a2a-f936795b5260
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Determine lot size
6501d8b1-cb43-5bdf-9dd5-67d2dba00fa2 | note | Ref docs - 235929-000-CV-SP-002
8f839c3d-0f6f-57fd-ba40-2524e8f064c0 | note | Acceptance criteria - Lot sizes is determined by the lesser of: One day’s production or 4000m2
5b2bd2ef-3e75-540d-8649-4edd104a0c67 | textbox | Acceptance |  |  | m2
cca7cbfa-c2a2-5d83-aafb-5efa18c67deb | note | Maximum lot size = 4000m2
54c4c5c8-e11c-59fa-87eb-3fd3e9d0f909 | note | Key - S
43d09c37-555c-5265-aaf5-711e3df335c7 | note | VIVA - S
26acb492-9acd-5d06-9f7a-caaa1143b6cb | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
5f18f051-a676-5e3f-ba60-44534e570e48 | tickbox | Lot Mark-Up
| checkpoint | 1.2 - Survey set-out
e8633a6d-758b-59ef-888f-cfbd143e64c6 | note | Ref docs - IFC Drawings
8aa7e653-16c3-56d5-a513-2a0363d44dbf | note | Acceptance criteria - Is the work area clearly pegged out for line and level?
0cf98971-5246-5cfd-bb65-0aeee80bd42a | button | Acceptance | Yes,No,N/A
f05c6e9a-36fd-54f4-9394-97ae24b54482 | note | Key - W
80487666-1cd6-59d5-9be7-ddf3c4831cbf | note | VIVA - S
| checkpoint | 1.3 - Material classification and source
c8bdf585-db77-5229-bb64-061071d89421 | note | Ref docs - 235929-000-CV-SP-002
e7cdf885-173b-58de-9df0-d8f3b7831e41 | note | Acceptance criteria - Has the nominated materials been approved for use on the project?
de56d295-db70-5412-bccf-81f55a7a0d9e | button | Acceptance | Yes,No,N/A
09c71a68-3758-568f-9a6d-6c9c77bb59ac | note | Key - H
da0fb1c6-15c0-5f0d-b6cd-10bfcd11bd24 | note | VIVA - H
50b1f835-aba7-5703-b6c1-ad3b1bee2549 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
0b95c8ae-2a21-58f2-83fd-e8a8b36dcac9 | tickbox | iDocs Approval Document
a0b6986c-2be2-535f-9125-dee4d5976015 | textbox | iDocs Number
| signoff | AUTHORITY HOLDPOINT
| section | 2.0 Conformance of previous layer
| checkpoint | 2.1 - Conformance of previous layer
81e0e4e3-8ddc-5612-87a0-8bea0288a50d | note | Acceptance criteria - Has the previous layer passed acceptance criteria?
b612900e-50a7-53c2-9c3e-25418ac21c1e | button | Acceptance | Yes,No,N/A
20018853-84de-5729-a379-0079ffd0af5d | note | Key - H
7189376a-d627-5626-ac23-398505e4b612 | note | VIVA - H
69de0e78-36f8-56fa-8320-0efe083ebfcc | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
1dfb806b-055f-532e-a775-2f5f663def65 | tickbox | ITP Number
| signoff | AUTHORITY HOLDPOINT
| checkpoint-no-value | Type of Pavement:
92c74975-23d8-5dba-ac9b-cfbc0807f4fd | note | ○ For Crushed Rock Placement Below Concrete Pavement Refer to Section 3.0
bb8147f6-6b95-58d6-9639-45561ac2fbe2 | note | ○ For Crushed Rock Placement for Gravel Pavement Refer to Section 4.0
6f7016fe-c9ef-5f8e-96f6-14ac56a767c4 | note | ○ If multiple pavement types exist please complete as applicable
fa1f7190-e811-5ac9-aa81-8394c776142d | note | ○ Please strikeout not applicable sections
| section | 3.0 Crushed Rock Placement Below Concrete Paving
| checkpoint | 3.1 - Placement
01389caa-4b1a-5fa6-bc77-a97e7bfdaf7c | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
eedb55a1-590d-5c8e-bd12-a9b3399987a2 | note | Acceptance criteria - Has Class 2 Crushed Rock been placed to be a minimum of 250mm Thick as per IFC Drawings?
49a7d8d8-0a74-59b1-a156-b8b99f0eca12 | note | ○ Crushed Rock Layers must not exceed 250mm thick lifts if additional Crushed Rock is required.
aa11b76c-a823-5d46-b72f-3ab49ffe384d | button | Acceptance | Yes,No,N/A
13d22732-d375-567f-ae22-91ec50f1151b | note | Key - S
d33cfb8c-8769-50e6-b2c3-6b5e9d1a63ec | note | VIVA - S
| checkpoint | 3.2 - Moisture
35ca5b69-0a83-52dd-90db-9a5dd46b3dcf | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
d36c6c8c-68d5-5902-a3df-69c08681e1ac | note | Acceptance criteria - Has the material maintained at optimum moisture content (>85%), with additional water being added if required during compaction?
56384fb5-6c00-5e73-9829-9bc53e2d806e | button | Acceptance | Yes,No,N/A
d9a60ee9-b6a9-5faf-94b2-132f3ffa344e | note | Key - S
dfbb937b-ae3c-5a8e-b34e-c057068ebd28 | note | VIVA - S
| checkpoint | 3.3 - Compaction
6f254900-fcbe-5d4b-8fd3-ef732cce8350 | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
c5812e5c-1512-46fc-bbf0-45478166e4d4 | note | ○ DoT 304.09
0b93ef45-aedf-4281-93b0-8d235b2a6aff | note | ○ DoT 304.11
c354666d-5886-45a9-b59d-58f25b3e3039 | note | ○ DoT 304.121
b13d3546-2115-5f3d-a10f-5ad32e2d15eb | note | Acceptance criteria - Compaction Testing is to be completed at 3 tests per lot to the below requirements:
9e51b6f7-df24-5291-853d-8e637d5708dd | note | ○ 98% MDD
777dfafa-dd95-5ab7-84cf-43a2ea10dcb4 | note | ○ +-3% of Modified Moisture Content
d4759b59-4e66-559e-8bf6-e84562d8c480 | note | – If testing of the first 3 consecutive lots have achieved the above requirements testing is to be reduced to testing per 2 lots until such time that a lot fails to meet the specified requirements.
fc38b74e-a939-5072-bb4d-f2930e7803e7 | button | Acceptance | Yes,No,N/A
3caeb15a-4034-5a12-9768-059f494dea8f | note | Key - H
cc0b4ae2-f2cb-50c8-9a1f-3885365cab1b | note | VIVA - S
15b9e5e0-0d48-574a-8e61-7d86ed4b494d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ced06147-f3a9-5f5e-8a88-a800e350c339 | tickbox | Compaction test reports
| checkpoint | 3.5 - Test rolling
8417ed8f-2d33-52ef-a780-bd97adf43f18 | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
a8f60c05-766d-5571-addc-cbcb1fc24664 | note | Acceptance criteria - Does the layer withstand test rolling without visible deformation?
e3bad8fa-53d1-560a-af29-9e43dcc80a08 | textbox | List attendees:
96a4c8b6-a202-5e3e-a455-8cf8a1489620 | button | Acceptance | Yes,No,N/A
9121f4ae-077d-5192-9de9-8264c6fc4043 | note | If ‘no’ please see below
60e4dcc6-7e37-5a9a-8641-39b5671cd033 | note | If ‘yes’ please proceed
dd985b01-e537-5220-bc7c-0a7c3b8bebe5 | note | Key - H
f612c7e6-fcca-5810-a8f0-6ec9ace8f618 | note | VIVA - W
3d64c171-4402-579f-80a6-972f4c57472a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
823e135f-1efe-55b0-add1-ccb87dbe91b1 | tickbox | Proof Roll Sheet
| checkpoint | 3.6 - Identification of soft wet or unstable material
97ec0340-9dee-5e5e-b847-719c46b8fabb | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
bb6b736c-dcf1-52ac-8f40-6f3784b729f9 | note | Acceptance criteria - What quantity of soft, wet or unstable material is present?
9d156093-5a40-585f-813e-1c1b080e35b6 | button | Acceptance | Yes,No,N/A
e576fcb6-bb54-5c0f-8724-31107bfd1a20 | textbox
4cde47f5-e32c-561b-b519-d786462843ab | note | Key - H
711c6f8c-97d8-5f7f-aed0-21b69f7e8ea8 | note | VIVA - W
| checkpoint | 3.7 - Treatment of unsuitable material
7cee4b29-d1cb-58e1-8c35-56348ddcbb6c | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
99bdd0a0-8ccf-522e-94f1-0e32eeec3810 | note | Acceptance criteria - Has the nominated soft/wet spot been rectified by a remove and replace method?
64a62daa-c37e-54dd-b280-2dd59e017376 | button | Acceptance | Yes,No,N/A
45041a27-b536-5253-abd1-fa5e6a8ccc1e | note | Key - H
ac86a90b-0949-513b-8285-c65a5a3f4e25 | note | VIVA - W
| checkpoint | 3.8 - Placement of Polythene Membrane
d828a38b-e40c-5ade-94aa-c9a127b199e4 | note | Ref docs - IFC Drawings
c5623489-4e10-5d5e-abbc-4fd16d806e60 | note | Acceptance criteria - Has the Polythene Membrane been installed above the completed Crushed Rock layer?
cf22dba4-bc72-5cf7-b78c-84e43e394556 | button | Acceptance | Yes,No,N/A
7ba0d442-51ce-5efd-8ef4-30b7ca7ed19d | note | Key - S
e4125fc3-a679-5ef3-aa19-0754b7f8a6c9 | note | VIVA - S
| section | 4.0 Crushed Rock Paving
| checkpoint | 4.1 - Placement of Geogrid
0dfc6fcf-b3d8-54cb-be50-3a61746a69f7 | note | Ref docs - IFC Drawings
6f887263-f3e7-51de-b4bc-4c53f829ef5d | note | Acceptance criteria - Has Geogrid been installed where non-paved areas have been excavated?
6add77c9-adf0-5e59-8097-b90ed6bf983e | button | Acceptance | Yes,No,N/A
e9c174ad-573b-5fa3-84ff-93dea5f41103 | note | Key - W
b1571a35-8fd3-55ca-8946-26ccf49e833f | note | VIVA - S
0de21b6f-e82a-575c-aefb-940a38bbfcfa | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
f3ff3c71-43a1-54e0-8bdb-05d75404f2e3 | tickbox | Material Approval
| checkpoint | 4.2 - Placement of Crushed Rock
a903b078-bc18-51df-b13c-98e9eaabc123 | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
d72fa877-9882-5c97-bf6e-e26e10174d14 | note | Acceptance criteria - Has 20mm Class 3 Crushed Rock been placed to be 400mm thick?
853dda95-b172-5def-a1dc-8a3763e8c205 | note | ○ Crushed Rock Layers must not exceed 250mm thick
5a401019-1e96-5ec9-af57-9ee3a4591000 | button | Acceptance | Yes,No,N/A
cd392d81-4008-5da9-9916-cc3bdabb4f79 | note | Key - S
fa358042-4cbf-5c10-91c1-e7292a11b583 | note | VIVA - S
| checkpoint | 4.3 - Moisture
2331b14f-f1d0-57ed-870e-6dbaa9f9ee1a | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
43495157-14fb-57dd-940e-3c1945e4c980 | note | Acceptance criteria - Has the material maintained at optimum moisture content (>85%), with additional water being added if required during compaction?
6ec08d96-7bff-5e62-9518-0224f15059c6 | button | Acceptance | Yes,No,N/A
6c99e8bd-c06d-578b-be29-711ddc8e0327 | note | Key - S
156e0296-e4be-5c66-b962-6dbc51d53533 | note | VIVA - S
| checkpoint | 4.4 - Compaction
429d6bce-33c6-59a5-8d64-2ad478c6f108 | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
323c7877-ecd9-418a-b9d7-7ab2eaffa700 | note | ○ DoT 304.09
ff870aea-f513-41dc-b928-aa14702d4cd8 | note | ○ DoT 304.11
992fb4f9-436a-40ad-9d9f-b51fc1d38104 | note | ○ DoT 304.121
d3209243-9c30-5573-a1c7-30fafcce5b85 | note | Acceptance criteria - Compaction Testing is to be completed at 3 tests per lot to the below requirements:
89d3e070-4413-528d-a4ab-06f872de98b9 | note | ○ 100% Standard Compaction
7d6e1f91-a934-5645-955d-5a669e035a9e | note | ○ +-3% of Modified Moisture Content
cae85642-5db5-5937-8890-cff42144a5c2 | note | If testing of the first 3 consecutive lots have achieved the above requirements testing is to be reduced to testing per 2 lots until such time that a lot fails to meet the specified requirements.
077a6c37-c1ca-518a-a2fe-3f5d83345928 | button | Acceptance | Yes,No,N/A
bbc07bbe-5011-5668-b581-002833c721dc | note | Key - H
5e43bae2-a18c-5b73-802c-99b64fe06a10 | note | VIVA - S
31de37d4-20c8-5b82-ac43-255a2389f771 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
2ab9353d-83ac-5c89-8b8b-fff09aebef9c | tickbox | Compaction test reports
| checkpoint | 4.5 - Test rolling
97553362-56f8-5ff2-96e9-adceb75265b9 | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
e2b50d78-d3a3-5c10-8da2-5bbaef359853 | note | Acceptance criteria - Does the layer withstand test rolling without visible deformation?
73e1ee2b-08c7-59b8-8150-983da127d3d2 | textbox | List attendees:
9ed16321-b204-5483-84c0-64512d1e5bb4 | button | Acceptance | Yes,No,N/A
d94bbfa0-63bf-5cb6-84b5-b96884759f4e | note | If ‘no’ please see below
99f6596e-bfaa-57ed-976b-bf8607a2d7da | note | If ‘yes’ please proceed
b404bfbf-5950-599a-85c1-593556c3903a | note | Key - H
92ec5bda-49ea-54a3-997a-d6a6a08fec5c | note | VIVA - W
b44fcef6-f2ee-5175-8a9e-11575b2a3639 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
88894f45-536d-5d61-9345-5e915faf41f9 | tickbox | Proof Roll Sheet
| checkpoint | 4.6 - Identification of soft wet or unstable material
d9af96d1-8e5a-5322-b353-453a3f02f9b6 | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
49f6f314-8b5e-5f7f-a09d-2ea51e17b811 | note | Acceptance criteria - What quantity of soft, wet or unstable material is present?
57d94117-c5d9-5bab-9a31-aedeb125c5ff | textbox | Acceptance |  |  | m2
2dc07789-628d-5968-8330-be11e9005f8e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
14f24b55-a5a3-5dec-bcae-aeeaa06a36b3 | tickbox | Photos
| checkpoint | 4.7 - Treatment of unsuitable material
7e103013-e4ba-5867-b406-eb6bdcf54080 | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
8b850234-8a5d-5309-94cb-d3464137601c | note | Acceptance criteria - Has the nominated soft/wet spot been rectified by a remove and replace method?
cd5e9e8a-b263-5276-817a-74fadbaa2bd3 | button | Acceptance | Yes,No,N/A
e0c726a2-a991-5162-a318-691e492d7a7e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e99da963-0e22-5ffe-b518-56c61c6bc0b1 | tickbox | Proof Roll Sheet
| section | 5.0 Conformance check
| checkpoint | 5.1 - Pavement finish
e3602dc3-74e4-5984-a2d1-dc831e4cf811 | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
5ae04c9c-9fe2-5dab-9a1f-ccbd33dd9cbf | note | Acceptance criteria - Has the crushed rock layer been finished to a smooth and uniform surface?
cc0f4e16-2509-583f-9afe-298f60b0c4e7 | button | Acceptance | Yes,No,N/A
2717a8ab-24fb-5764-8c65-53db17151273 | note | Key - W
| checkpoint | 5.2 - Surface level of pavement courses
053d23a8-26a5-5bff-87cd-6177a5936e8f | note | Ref docs - IFC Drawings 235929-000-CV-SP-002
52c172d6-67d7-5bb0-95e7-f4602e1d0206 | note | Acceptance criteria - Has the prepared layer been surveyed in accordance with and verifying specified requirements?
b56f3ef5-c7f8-51f5-8117-6ae41b140ee4 | note | ○ Tolerance: +-15mm
fbe17cc5-0a4e-58f6-8614-779e62dcaadb | button | Acceptance | Yes,No,N/A
6ecc219a-e6f4-5a30-bc48-062c3d1071c0 | note | Key - H
563af117-9dcf-54aa-b1e7-1c84bd60befc | note | VIVA - H
26c1a71c-e3c7-54f6-8619-3035514505c5 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
8128f3ee-2a3d-56f1-9e6a-fb0a34a30417 | tickbox | As built reports
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0398-ITP-014 Electrical Conduit Installation Rev 1 | itp | INF-HSEQ CC0398-ITP-014 Electrical Conduit Installation Rev 1 |  | aab78521-e30f-49c2-a8de-8871263e6974
| section | 1.0 Pre-start activities
| checkpoint | 1.1 - Set out
1103763d-3203-5b23-8d01-7ffd83b0a3bf | note | Ref docs - Composite Drawings
baea0935-acee-50fa-991a-e11a977b35f9 | note | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
6087ad65-65cc-5e9e-8e86-2eaead5e0733 | note | ○ IFC and latest available revision used?
bbd68c2b-9710-5c52-8ce0-cb0c63029af3 | button | Frequency | Yes,No,N/A
ddbaf7dd-4446-55b8-869b-1831c4fc0d8a | note | Key - H
576eb695-05f7-5ed1-a4df-dc13949ef257 | note | MDR/VIVA - W
| checkpoint | 1.2 - IFC Submission & Approval
d4692abf-369a-5619-8e85-3be78cb86c88 | note | Ref docs - Composite Drawings
b5eb0725-54e5-505d-83fd-72367add37c2 | note | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
8d2f11fe-99b3-557b-83b3-69b4294b5844 | button | Frequency | Yes,No,N/A
d1dae0c1-7ece-5256-96ec-a1a0d04d8609 | note | Key - H
65f3cb6c-dd47-5ac2-9460-887af1cdce4c | note | MDR/VIVA - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.3 - Permits
ad696d41-c65c-5ce8-8ece-f4f5be10c6c1 | note | Ref docs - Symal Safety Procedure
eea60ce2-aa64-57ba-a299-fffbfdc8497a | note | Acceptance criteria - Have the below permits been created.
a3f79c57-07ad-54a6-b9bd-4d465fe8d825 | note | – GPP
8cf2c107-28df-57e9-8cc7-865548497cdf | note | – Working at Heights
ef2e6c7b-74ad-542f-bba0-b1fd577953ce | note | – Hot Works
d7d058b1-616e-5e83-ae75-b0c075cd0a50 | note | – Confined Space
14a317f5-b194-566b-8893-48b60747d7b5 | button | Frequency | Yes,No,N/A
1922f7ae-3740-560b-88ee-1cf481d53473 | note | Key - H
90e0dc93-a46f-5faf-8324-1f8747af9aeb | note | MDR/VIVA - W
| checkpoint | 1.4 - Determine Lot Size
fb6a004b-76cd-55f5-a879-3c19728e41db | note | Acceptance criteria - Has the lot size been determined?
9cac09c7-ed59-5cc6-948c-035ae399718d | button | Frequency | Yes,No,N/A
a9f11d2c-2831-5478-aa3b-835284bab343 | note | Key - S
9bfe7bc8-c769-52b1-b350-4d0682d6a73d | note | MDR/VIVA - W
4433b698-0407-56e0-94a9-553a24170e4a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
c879e416-8961-5fb7-81f3-3086b15aa863 | tickbox | LOT map
| checkpoint | 1.5 - Delivered materials
faf54236-bf17-5c9c-a510-0925830b1a92 | note | Acceptance criteria - Has a material inspection checklist been completed?
0da7ccb4-206d-537d-af25-0c2b7a3e269b | note | ○ Have the materials and tag numbers/heat numbers been verified?
e62be9ca-0b60-5cd5-8f05-735f6416edc3 | button | Frequency | Yes,No,N/A
e6edf1da-c880-5e3b-b553-67678fc0d9ad | note | Key - W
34cdbfd2-d246-5709-82a5-1fb8e99f76f0 | note | MDR/VIVA - W
90041ad3-1bf4-575e-adc4-350ceee5d705 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
b6f14163-44a5-5040-8abf-f57cf1fb6c9e | tickbox | Material Inspection Checklist
| checkpoint | 1.6 - Electrical and Earthing Pre- Qualification
4e44ed13-1d43-5efb-8001-db91cda60ad3 | note | Ref docs - 235929- MG1668-CV- 003-SUBC-000181
7767152d-32f3-5dc5-8011-8c292c318565 | note | Acceptance criteria - Welding procedures, equipment to be used, welding qualifications and calibration of welding machines to be submitted and approved by the client, has this been completed?
c291cbd7-5b65-5765-97b5-9b611aae21b8 | button | Frequency | Yes,No,N/A
04e35efb-135b-5b11-9ed5-eec76864af9d | note | Key - H
3fc5f82f-71b3-530c-8a7b-62d7d692cb74 | note | MDR/VIVA - H
138ad1c9-5dd5-52c5-951a-f81dc3e74ac9 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
79f0886f-656c-58c5-abc5-0666f09fa285 | tickbox | Welding Qualifications
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.7 - Backfill Materials Approval
ed8555be-45a3-50a2-b0c0-0755765d3883 | note | Ref docs - 235929- MG1668-CV-
de896422-a54d-5dca-8546-0c6b65bdc8f4 | note | Acceptance criteria - Has bedding and backfill materials been approved for use?
fa2501cb-52ba-5577-b3b4-d486a91c9ecc | button | Frequency | Yes,No,N/A
96e32297-2c94-5e65-88e4-f23054fee8d9 | note | Key - H
c9c517ec-e7e8-562a-881b-df30cae436df | note | MDR/VIVA - H
45b31951-de66-5cef-b62e-21fc18f50108 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
8a3fae06-4d66-5e3f-81de-6659c5faba2f | textbox | Approval number:
| signoff | AUTHORITY HOLDPOINT
| section | 2.0 Excavation and Placement
| checkpoint | 2.1 - Service Location
f5dd4e52-7676-56dc-b9ff-06870f1c849e | note | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
40263034-5fbd-5409-8659-6cf0454dc093 | note | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
d1e4ac7a-2717-54ee-90b6-8b38d4e68d1c | button | Frequency | Yes,No,N/A
7111c7ff-dd0e-5948-a47e-fdd5346a030e | note | Key - H
6dfab305-5162-50c9-80a8-2e614eaa0b0e | note | MDR/VIVA - S
| checkpoint | 2.2 - Excavation
31705c26-3c76-51d4-8a98-bc5f6aa51a63 | note | Ref docs - 235929-000- CV-SP- 00006 UG PIPE FAB and INSTALL Section 12.1.12
438574e2-88a0-5442-bae3-c2c2577c2701 | note | Acceptance criteria - Excavation shall be to depth adequate to provide full specified bedding depth of 100mm.
5144d833-8b0d-5231-8261-1992d3ad92d9 | note | ○ Trench width to provide 50mm from edge of trench to conduit walls at minimum.
cae4db40-c0c5-5a73-ad3e-2ce422ebd58f | note | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
0328c583-c28c-5b0f-ad1c-be938bf463ff | button | Frequency | Yes,No,N/A
399e6f67-d97a-59ce-9df0-58f24d8d6d3f | note | Key - W
9e6e5f6b-d082-5be5-9657-a4887e84a36d | note | MDR/VIVA - S
| checkpoint | 2.3 - Conduit materials and size
8d0c329f-feb7-574e-b1e4-5b628989250b | note | Ref docs - 235929- MG1668-CV-003-SUBC-000112 (Shop Drawings)
4ae8a4a8-1792-5daf-8a31-08dc850e991c | note | ○ 235929-MG1668-CV-003-SUBC-000009 (UG Services AMS)
37dd0192-aac6-5ab7-9eb2-ed23bee3fcd9 | note | ○ 235929-154-CV-08-92002-080001 (Rev1) & 080002 (Rev1) & 080005 (Rev2)
cfce4612-afba-5425-bc55-a962e200c674 | note | Acceptance criteria - Are the HDPE conduits approved for use?
c34bc2d7-1e1c-5007-bcf4-7111c1c4ccb3 | note | ○ Have the conduits been installed using approved couplers?
4bf91e3d-d1a9-588a-bf38-201b2edac232 | note | ○ Has the installation of the couplers been reviewed by the client?
48eacfb7-7956-5465-a20e-0f077b222dcd | note | ○ Has the bend radii been checked and adheres to the drawing?
d24125a3-2ed0-5837-9e7a-fbaf9eb2a87e | button | Frequency | Yes,No,N/A
d9452e8c-4d05-5488-9cdb-9ed8278023a7 | note | Key - W
4db4758f-38b4-53f0-8d38-f3e9de71b780 | note | MDR/VIVA - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.4 - Conduit placement
8516ec96-4321-5c27-ace6-7fbae8b2707d | note | Ref docs - 235929-154- CV-08- 92002-080001 (Rev1) & 080002 (Rev1) & 080005 (Rev2)
6bd7b8f1-c44e-5c55-bf0d-ce090a0cb0c1 | note | Acceptance criteria - Have the Conduits have been placed as per drawings and specifications and inspected by a VIVA representative?
e9a6b259-ee54-5deb-a49b-b6993bfc6230 | button | Frequency | Yes,No,N/A
93518f9a-1822-509b-a093-1c08852405aa | note | Key - H
ea77579a-f49b-543e-8272-8b0806f7dd5f | note | MDR/VIVA - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.5 - Backfill placement & Marker Tape & Rope
147710ae-de45-5278-9b99-f058fcb01461 | note | Ref docs - 235929-000- CV-SP- 00002
1a98b052-1c04-5779-acce-5710fb75c752 | note | Acceptance criteria -
7fd662e6-da04-5ecd-8a78-35c76b49dbff | button | ○ Have all trenching works been recorded for as- built and digital data prior to backfilling? | Yes,No
bb11efe4-a379-57c2-9aea-54121f10378d | button | ○ Has bedding material/sand been placed for the full width of the trench over the conduits for a minimum cover depth of 200mm? | Yes,No
83b09002-499e-575a-ba91-125d4c312726 | button | ○ Has marker tape been placed in-line and above the conduits on the surface of the sand layer? | Yes,No
218a9bea-0d4c-537b-a384-d855b5e2c270 | button | ○ Has draw rope been installed through the conduit? | Yes,No
5de0e56c-9cff-5303-a686-f5668c8ade0f | button | Frequency | Yes,No,N/A
1f396bba-c341-536e-9c87-706ef810b30d | note | Key - W
a823cb7f-dcff-52f1-b558-66bf3cdf8538 | note | MDR/VIVA - R
b0d39732-d08d-57e4-8444-293ec10fffe1 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
0b91bb22-a9d0-59c3-b72d-6fdfbe4945ad | tickbox | Photos
| section | 3.0 Finishing
| checkpoint | 3.1 - Clean-up of site
6b81d36d-7ca2-5aa7-8f93-cfd3c837ff8a | button | Acceptance criteria - Have the areas affected by the works been restored to a condition similar to that which existed prior to the commencement of the work? | Yes,No
319ebba0-564c-5502-a165-36e704ddb325 | button | Frequency | Yes,No,N/A
a3f7764f-b495-5837-86ba-119170beadd4 | note | Key - S
5a6f278d-58a9-56cc-a207-402d379dc048 | note | MDR/VIVA - S
| checkpoint | 3.2 - Identification and recording
40871e02-7778-53f0-9565-4394a5f03baa | button | Acceptance criteria - Have the actual installed location and depth of the conduits, and location of pits, been accurately recorded on an as-built? | Yes,No
9d421667-cb2b-55a4-939c-c5680e40e6dc | button | Frequency | Yes,No,N/A
64b4cdf9-2523-56ae-b7c1-6facff86b4ac | note | Key - S
62827790-ca8e-5df4-bfb9-24dfbc6eebad | note | MDR/VIVA - H
9edaa3ec-4e81-5b63-b7f7-65ed012d4147 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
b791b950-b7df-52a5-982f-40f99a23a200 | tickbox | As-built
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Work is complete and complies with design plans / drawings / specs
4eb51d99-1e06-56ca-8683-abc147039ea0 | note | Acceptance criteria - Redline mark-ups As-Built Survey: Conduits to conform to the required depths and locations.
6755acf2-cc83-5b9e-a4ea-ac001f1e36bc | button | Frequency | Yes,No,N/A
6d1dfd6a-aac6-53a8-92cd-36344bce3c0a | note | Key - H
7627c440-a603-5aa6-9eb6-1b2fc6950050 | note | MDR/VIVA - H
6f58148e-825f-5a9e-a43d-38c6f0c855ef | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
89694bb5-8187-5a6e-9ba9-48e6e223b743 | tickbox | As-built
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.4 - Certificate of electrical safety
b5568540-b843-5dff-9b6c-f1e3a6a038a3 | note | Acceptance criteria - Electrician to supply Certificate of electrical safety for conduit installation witnessed
5f0a1fa8-5df5-54e6-b0ec-6e6992f5c869 | button | Frequency | Yes,No,N/A
1073ef31-6b00-52e2-bbce-da3f4f345cb1 | note | Key - H
e72071bb-5764-581a-ba0f-08ed92ae0a45 | note | MDR/VIVA - H
8d53235f-f828-5720-95c0-856d20016331 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Certificate of electrical safety
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0398-ITP-021 Concrete Pavement Constructions Rev 0 | itp | INF-HSEQ CC0398-ITP-021 Concrete Pavement Constructions Rev 0 |  | 63b89fec-ae32-4be6-b458-8741033dd22a
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Determine Lot Size
e3cff05b-62e3-548e-873b-9babb06eedf1 | note | Ref docs - IFC DRAWINGS
f38181a0-f49c-591f-9652-6bec78581062 | note | Acceptance criteria - Lot size Lot Size = Each pour section per day (location or m2)
bf343427-f7f5-5d99-8533-bd3188a4b23b | note | Acceptance - Marked Plan
c2f09575-55d4-58d2-8113-dd8187168f8a | note | Key - S
45451835-d6ca-56eb-8edb-32b1570c14c7 | note | MDR/VIVA - S
803299bf-52ef-5ea2-9c26-3c0bdb180049 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
7b84fcf0-fbb1-5c1c-b874-8f3d415acdf1 | tickbox | Lot Map
| checkpoint | 1.2 - Survey set-out
05297db0-51cc-5eb0-b90d-f590d0a32eb0 | note | Ref docs - IFC DRAWINGS
090f1ed6-b79e-51ae-96ae-cf1cef1d7fdd | note | Acceptance criteria - Has the work area been set out for line and level?
0cb80111-8eab-5407-9e9d-6543332fec8a | button | Acceptance | Yes,No,N/A
5dc82db9-ee09-53e1-bc28-717bdf031569 | note | Key - S
80ce9576-50f5-5e80-b721-6fc220a42c1d | note | MDR/VIVA - S
39d1fb4d-07aa-5413-af08-fe53863f2dc0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - As Per IFC Drawings
| checkpoint | 1.3 - Material Submission / Approval
b6747361-8246-5737-9e23-9334c1164f8b | note | Ref docs - AS 3600 235929-000-CV-SP-00007
eafbd3de-d6a0-5cef-840a-ae772af9ab9d | note | Acceptance criteria - Has the mix design to be approved prior to placement. Material properties meet project specification, AS 3600, AS 1379?
07b079d1-3b51-5693-903c-66c9e7d85e9a | note | – Minimum Concrete strength 25MPa or as specified in Drawings?
0b477870-6c30-5aa8-a39a-be801d8de8d0 | note | – Steel Reinforcement certificates of conformance provided?
49c36947-dc00-5cfe-8137-d2771833698c | note | – Do admixtures shall conform with AS 1478.1 and are permitted if used in accordance with manufacturer’s instructions?
bcdc7b84-9c0b-51f5-accf-5e81ec9def8c | note | – Are all admixtures free of calcium chloride?
4d55281a-bee2-5833-9032-762cf9f5ee8e | note | – Has jointing materials & Sealants been approved?
87cb8a7d-ec7f-598e-acee-ff5903d38f41 | note | – Has vapour barrier material been approved
03b107ce-66ac-5cdc-926e-f27425645853 | button | Acceptance | Yes,No,N/A
1d5a276a-0555-554d-b4d4-25d2bd614e55 | note | Key - H
36ae1bfc-fc45-500c-92f8-f1aba0251e7b | note | MDR/VIVA - H
c68c8274-d42d-5237-bf7a-fa4a9c5484b5 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
35d82958-a622-5059-b450-bf490bd5fc31 | textbox | Mix Design Number
0c8b3203-dee3-5e82-973c-c5942737e269 | tickbox | Material Compliance Certificates
e9056f80-97e0-540e-ab1b-81f49e26023b | textbox | Idocs Approval Reference
| signoff | AUTHORITY HOLDPOINT
| section | 2.0 Form Work
| checkpoint | 2.1 - Vapour Barrier Installed
5c73229c-b620-5a95-89fc-5d717bc951c0 | note | Ref docs - 235929-000-CV-SP-00007 Section 6.2
980b17d9-1238-5377-a45f-2c6c818ac90f | note | Acceptance criteria - Approved vapour barrier installed on surface of crushed rock base?
c7b8f9ae-038e-53be-a12a-06e598c4c4d0 | note | ○ Are all lap joints minimum 300 mm and sealed with duct tape?
0950f71d-3066-5014-baf4-ba02cc0ccf3c | note | ○ Are major punctures in the vapour barrier patched of taped?
ec015ecb-4d95-5612-bee1-ea0a3943b56c | button | Acceptance | Yes,No,N/A
091e37c3-2b63-5e7e-a845-95c21f101fae | note | Key - W
c1cc0ad8-a311-5e6c-938a-6b76c1ca0390 | note | MDR/VIVA - W
| checkpoint | 2.2 - Formwork Setout and positioning correct
8d283459-6982-5f15-bc8e-583927cb4849 | note | Ref docs - IFC DRAWINGS 235929-000-CV-SP 00008
115eab0c-077d-5dd9-a82f-e269a09f78ea | note | Acceptance criteria - Is formwork checked for potential loose sections, ensuring no movement upon placement of concrete?
91538d04-3476-534e-9408-29a3493fabb5 | note | ○ Is formwork in line with survey markings?
e8d7274b-e2b8-534e-8dd2-6983e766785d | note | ○ Have chamfers (if required) been attached to formwork in level manner?
ceaf839f-aa8d-5fe8-af2a-739fbbe02a09 | button | Acceptance | Yes,No,N/A
1e491d5b-aca2-5c8f-ab9f-9b42a4c9a567 | note | Key - W
62dc63c9-69e8-5154-a378-f3bea5dab6ec | note | MDR/VIVA - W
| checkpoint | 2.3 - Concrete jointing
b3b10119-54a4-5b49-b785-f7a4f58c9ae1 | note | Ref docs - IFC DRAWINGS
099b54ad-52a1-569b-a51d-3d8b725dd05c | note | Acceptance criteria - Have construction joints to be installed as detailed and in locations nominated on IFC Drawings and notes using approved materials?
bdde3652-ea21-5f87-8a73-65ad2016dc81 | button | Acceptance | Yes,No,N/A
a4530fe8-1784-5ae3-8cd6-805f5bf9c4b0 | note | Key - W
11435d09-6246-5a71-94d5-ac2694a940ed | note | MDR/VIVA - W
9fe4de70-7f70-5159-9aea-6eae7666c614 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
3be33c12-09b6-5af3-bbb9-c6c6f47d8c12 | tickbox | Delivery Dockets
| section | 3.0 Reinforcement
| checkpoint | 3.1 - Steel reinforcement Supply
596611d2-349d-5564-aba8-6131b917c3d5 | note | Ref docs - IFC DRAWINGS
490de5b7-f5cf-5065-81a7-a5294dbec2cb | note | Acceptance criteria - Has correct reinforcement been delivered?
7fbd18bd-20e3-5a5f-b0d1-e7b791b218de | note | ○ Is reinforcement free from rust and other contaminates that may affect bonding?
6ffcd710-4570-5070-b145-eb016a04732f | button | Acceptance | Yes,No,N/A
fde47089-42b8-5b59-b22e-6ef58e4a16ee | note | Key - S
1398b4e6-fbf2-501d-a17c-c5d0d0807d7a | note | MDR/VIVA - S
c9e870a7-a94d-5668-a94f-604615940649 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
10e84119-9dd3-5bd7-afeb-18185749ec38 | tickbox | Incoming material checklist
2f0d6a97-55c0-5f6f-9002-b54f99a410b8 | tickbox | Delivery Dockets
| checkpoint | 3.2 - Steel reinforcement installation
695fca6d-c286-5e12-928c-ac819baf513b | note | Ref docs - AS3600 17.5.3 235929-000-CV-SP-00009, IFC Drawing 235929-000-CV-01-92002- 010002
030ebe87-80d1-5fe0-849d-0f3376784f39 | note | Acceptance criteria - Is steel installed as per the latest IFC drawings?
4545e27d-0a10-5db7-8e8c-40b747b814d8 | note | ○ Does steel reinforcement conform with AS 3600:17.5.3?
c2d7b78b-dd4b-5a6f-9ad4-f347e4d4a4f3 | note | ○ Does cover to unformed surfaces comply with IFC drawings?
61134d37-8574-534e-a6b7-f13c9de72e80 | note | – – – – – – – – – – – – – –
cf830b17-dadd-51e3-bcf9-e333a04c24e2 | note | 17.5.3 Tolerance on position of reinforcement and tendons
a63f590f-7278-506a-a523-bccc9bd5f230 | note | – – – – – – – – – – – – – –
5338e11e-d263-5eb3-9687-97e195e89399 | note | The deviation from the specified position of reinforcement and tendons shall not exceed the following:
5118ff21-4350-5e63-91d6-0239a540b1da | note | (a) For positions controlled by cover –
4ad4fbda-3157-5693-b368-7437f4991ffd | note | (i) in beams, slabs columns and walls… -5, +10 mm;
47960318-0d4f-59ab-8d36-b011e46a2306 | note | (ii) in slabs-on-ground… -10, +20 mm; and
c9dd6df3-5bf6-5bcf-8fa6-ade7755f367a | note | (iii) in footings cast in the ground… -10, +40 mm,
b83d74df-2249-5f35-86a3-1f03b402ff58 | note | where a positive value indicates the amount the cover increases and negative value indicates the amount the cover decreases.
efa2ade2-8ad2-5069-ae99-820bc521d76b | note | (b) For positions not controlled by cover, namely –
fe3ce8b0-8842-5517-a288-1d04de832405 | note | (i) the location of tendons on a profile… 5 mm;
e053e7aa-e639-55d2-9d69-a16e3def80c5 | note | (ii) the position of the ends of reinforcement… 50 mm; and
aeb82a67-8a10-5a69-9002-8c14862484b2 | note | (iii) the spacing of bars in walls and slabs and of fitments in beams and columns… 10% of the specified spacing or 15 mm, whichever is greater.
efad0451-85ce-5de9-bf87-db674f675166 | note | – – – – – – – – – – – – – –
66ec8bf3-0d3f-52a4-8136-e103c38906fe | note | 8.0 CONCRETE COVER
e2c9f875-221a-5084-aa6c-bd1d98ed6795 | note | – – – – – – – – – – – – – –
9a7bceeb-a83f-59e8-b12c-8aa4d6f87771 | note | 8.1 CONCRETE COVER SHALL BE IN ACCORDANCE WITH AUSTRALIAN STANDARD AS 3600 OR THE VALUES STATED BELOW, WHICH EVER IS GREATER.
713d63aa-0146-591e-bd80-7d6c74837e2f | note | ○ PAVING (TOP) = 30mm
c06a971d-d9a5-57f0-880c-03745d4fe50c | note | ○ PAVING (BOTTOM - AGAINST GROUND) = 50mm
16d70702-3330-59c9-9fd0-4688e5b6695a | note | ○ FOUNDATIONS CAST AGAINST FORMWORK (INCL. EXPOSED WEATHER FACE) = 45mm
27e4f6b9-baaf-55bc-84c8-f2bba851952f | note | ○ FOUNDATIONS CAST AGAINST GROUND = 65mm
7ca613d0-6576-5306-a5c3-54b4083768bc | note | ○ EXPOSED TO WASH DOWN WATER AND/OR PROCESS SPILLAGE = 50mm
e423a939-bfe6-50d3-8f7f-e00bca284967 | note | ○ CAST ON LEAN ON CONCRETE = 45mm
74d4d96a-76bb-5675-a5bd-ff1f3cb0ba33 | note | ○ CFA PILES = 70mm
9acea169-5d6c-5ee0-9d2a-807605d6c72c | note | – – – – – – – – – – – – – –
38f7886a-05ce-55ca-ae65-fdfb625b5d3c | button | Acceptance | Yes,No,N/A
472fb123-d047-5bab-9d63-d603931fa535 | note | Key - W
6ceb1360-5531-5f3f-873c-245b2e359aad | note | MDR/VIVA - S
| section | 4.0 Concrete Pavement Placement
| checkpoint | 4.1 - Pre-pour Inspection
915a36ae-3d62-51c8-804b-31483dc5c526 | note | Ref docs - 235929-000-CV-SP-00007, Appendix 7.1 Pre-Concrete Placement Checklist
1ae11140-780e-5fee-8a65-a859dbb918c2 | note | Acceptance criteria - Has a pre-pour inspection checklist completed prior to placement?
ba2da0b7-d5f9-564e-aa35-be6e3805fdde | button | Acceptance | Yes,No,N/A
4227106c-d573-511b-8cbb-3ea27c32bc04 | note | Key - H
a1c20725-9f46-5bbc-9da3-5d88a04b2de5 | note | MDR/VIVA - H
c630142f-31a5-5df6-ad1e-c3197161b870 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
1df05ce8-1c30-5f44-a2da-88cc0cc2e44c | button | Pre-Pour Checklist Attached? | Yes,No,N/A
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4.2 - Placement
ea394a95-fe9e-5ccb-abc9-10ea3fe60295 | note | Ref docs - 235929-000-CV-SP-00007, Appendix 7.3 Concrete Truck Record
d70a2301-12b5-5267-8596-f9817a029b00 | note | Acceptance criteria - Concrete shall not be placed when temperature is less the 5°C or greater than 36°C. Between 32°C and 36°C admixtures and placing requirements must be met.
eecf61b5-2dc9-538a-a731-1abd8eb94d10 | note | ○ Concrete shall be transported, handled and placed to prevent segregation, loss or leakage of materials.
50fc55b9-4fb5-5dc2-8b75-92fd15dfa74a | note | ○ Concrete shall not be dropped from a height greater than 2m.
94322f4b-834d-5bb5-80cb-af829e4c7190 | note | ○ Concrete shall be discharge within 90 minutes of dispatch from plant.
02f2902d-a46a-5118-ada9-16259d82fd7c | note | ○ For continuous pours, the maximum time lag between truck loads shall not exceed 25 minutes.
e3377e4f-58e5-5b00-aa70-073bdfaa3d27 | note | ○ Concrete shall be thoroughly vibrated to ensure no honey combing, voids or surface defects occurs and compaction is achieve throughout structure.
06f72c08-7c33-5083-b031-1a8179efeb16 | note | ○ Water shall not be added to achieve slump greater than specified. If additional water is added, slump test to be performed after water is added.
549023c8-a482-5e6e-b73c-ead2e3ecab1a | button | Acceptance | Yes,No,N/A
a258f9f8-9268-5fa0-8644-050b8b1ea373 | note | Key - S
0b6dcc43-2025-516d-85c6-6bd0e78f73da | note | MDR/VIVA - S
ff521fc1-8b0e-53e7-9c6b-91e4dbab48ff | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
992be8cd-46cc-5170-94fe-54590539e86b | tickbox | Concrete Truck Pour Record
8ce629c2-6deb-51bd-bf73-a03a5cabce25 | tickbox | Concrete Delivery Dockets
| checkpoint | 4.3 - Slump Test
8f4ebecb-36e7-5475-be99-38c0141f2ebd | note | Ref docs - Section 5.1.1 235929-000-CV-SP-00007
79a0d9df-9055-5b40-9bdc-c09f7beb213d | note | Acceptance criteria - Slump must be within tolerance of designed slump. Testing shall be +- 15% of stated approved mix design slump.
09dcde1e-5a6b-5283-a752-942e2ff50e59 | button | Acceptance | Yes,No,N/A
e11fef28-af9c-504d-b78e-cebef3e4d1b7 | note | Key - W
f349b48d-a8fc-5f48-b47a-1f1d8075d8ab | note | MDR/VIVA - S
69c14d9f-2dc9-5494-bcd7-ddd9a3c3d4db | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
353ba9dc-9fba-5c0f-bec1-474c8fea0370 | tickbox | Concrete Test Report
| checkpoint | 4.4 - Strength Testing
4d549bff-afd8-5321-ac19-cc0e5b59aa7c | note | Ref docs - 235929-000-CV-SP-00007 Section 6.8
45a56bc1-88d5-5e59-8ab5-9626e79cbc1d | note | Acceptance criteria - Samples to be taken from chute. 5 cylinders collected per sample – 1x 7day, 3x 28day, 1x reserve.
ea859ff3-b7cd-578d-ab15-1ada3bff0847 | note | ○ 1 test for the first 20m3
a34400fd-01fa-5b2a-90d4-fab14e5e9212 | note | ○ 1 test per 40n3 thereafter
7e6bc7da-1832-5b82-a0cf-c4d757c9dcda | note | ○ Frequency reduce to 1 test per 80m3 for pours over 400m3
79a87dad-7b15-5aca-9522-3869c3c80abf | note | Acceptance
20a78d21-e9b3-5b77-9f0c-7744c1dd6d04 | note | – – – – – – – – – – – – – –
0f21931c-f040-57ce-8e3f-30d2a796fd5e | note | No. of Samples ¦¦ Vol. of Pour (m^3)
6359218e-d0cc-56c5-9ad3-e741bf230721 | note | – – – – – – – – – – – – – –
c4307d14-b7cd-558b-995f-b34717a2642b | note | 1 ¦¦ <20
a5a2f058-8c8f-5baa-8ff3-0ea7db124254 | note | 2 ¦¦ 20-60
95cc7908-facb-5de5-b36c-420677228eb2 | note | 3 ¦¦ 60-100
6ad80ded-1a09-5d83-bb74-296a2bd1ed72 | note | 4 ¦¦ 100-140
0eaf698f-46c2-5bc8-9145-59fd9038dcdd | note | 5 ¦¦ 140-180
f0c60f26-4b4e-57d6-9473-442843b690e6 | note | 6 ¦¦ 180-220
80560e6b-6bcd-570f-87b8-0359d60273ad | note | 7 ¦¦ 220-260
990b723a-ef94-5fc2-8e9a-fc03b6c6fde4 | note | 8 ¦¦ 260-300
d34f342e-7510-5eb5-b111-b6bcb3513323 | note | 9 ¦¦ 300-340
6dbca2ff-18a2-5e1f-a9ac-401e0ae53877 | note | 10 ¦¦ 340-380
adea7023-0b6e-5a13-822d-fe661ee46981 | note | – – – – – – – – – – – – – –
a1f0e421-f05d-5d39-859a-4c6609f1085c | note | Key - H
f9047c88-33dd-5d76-990c-8ad6dbd4b70b | note | MDR/VIVA - S
d7a05f16-60d2-5d5a-a55d-a1f42157aede | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
6188e887-fdf5-57d7-8842-418bdc42eb9d | tickbox | Concrete Test Report
| checkpoint | 4.5 - Curing of Concrete
581741fa-ffea-53c6-83a1-9abe95c6b509 | note | Ref docs - 235929-000-CV-SP-00007 Section 6.5
e74a8979-8910-5a29-b687-f8f576bea9ce | note | Acceptance criteria - As per the approved Curing Methodology.
df107372-20c1-5158-be23-872dabd172e6 | note | – Applied once bleed water has gone
7a96f1d2-24f2-5dcf-ae60-dff034acea1b | note | – Continuous uniform film achieved
99a96a89-c3d3-553a-91e6-e0fe63ef10e8 | note | – Rate of 5m 2/L
764e527f-dd27-5b87-8c77-e1b71a271396 | note | ○ Has curing been conducted as per approved curing methodology?
a18330b3-b63e-5ec9-ba4a-bd5b0dc272e4 | button | Acceptance | Yes,No,N/A
cb2e51ed-8bb2-5c93-aba9-bb1c5c770642 | note | Key - H
b097c186-91e6-5cfc-95c7-c014105daa77 | note | MDR/VIVA - W
fb7e8181-9dfd-5075-bf6a-d26ff0fb563c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
f7414eda-c9a9-5889-8790-1938c4e7058b | tickbox | Approved Curing Technical Data Sheet
| checkpoint | 4.6 - Colouring of Concrete
e72906b2-fe5a-5b0d-bfe5-e44050234211 | note | Ref docs - 235929-000-CV-01-92002-010015 Note 9
363a2d10-2458-5e7c-ba71-2ae3a3b794fc | note | Acceptance criteria - Concrete paving above conduit, shall be pigmented:
9a76b413-90a7-54db-abd7-7a5b817438ff | note | – Red for electrical;
1e0178ca-a874-5d19-b1b3-1b521ae29602 | note | – Green for instrumentation.
ff27678c-1910-5dc0-bd21-0a411fb004eb | note | ○ The method to be used is the dry shake, with oxide minerals after bleeding.
d1d25368-6441-5634-84e4-7b9e444f65e0 | note | ○ Pigments shall be used in accordance with the material manufacturer's specifications
73aaea01-e6ee-5421-aa33-790c126ea2f6 | button | Acceptance | Yes,No,N/A
e4e71429-4fdd-5abe-870c-76d910e01eca | note | Key - H
ff3b52e2-aa6a-5fd1-b27f-319143738c22 | note | MDR/VIVA - W
d8348763-e1eb-5be2-bf00-c8d74693d8b3 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
be61b032-4d75-5653-9480-6dd88c805b51 | tickbox | Material Approval
3c1e20bb-ad19-5f1f-b0c7-a648cb319865 | tickbox | Delivery Dockets
| checkpoint | 4.7 - Concrete Finishing
113965a6-b35a-5c7f-8185-ea35cebc6a55 | note | Ref docs - 235929-000-CV-SP-00007 Section 6.4
8a668b9b-447b-5062-a95a-fec7be42d00f | note | Acceptance criteria - Finish concrete per schedule below:
54567ab9-a602-56f7-9b4b-7ea12553ac2e | note | – Exterior slabs (i.e. foot traffic): broom finish.
499014b1-5716-552f-8f9e-d2c0df81461d | note | – Other approved non slip finish (i.e. stipple finish)
97bdb90a-df4f-578c-837a-45dd8ad1649b | button | Acceptance | Yes,No,N/A
f1cb240c-52ab-5503-a4d4-8ebc990c868d | note | Key - S
e91ff60c-a30b-57ad-972f-3992b771f70b | note | MDR/VIVA - S
1cd2ca2a-09d4-5bb2-a4f9-25e2c3d75d53 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
b826021f-9768-5e57-893f-f230311bb2df | tickbox | Material Approval
6860e125-67c4-50bc-be54-0481620753b7 | tickbox | Delivery Dockets
| checkpoint | 4.8 - Formwork Stripping
1b127e7b-b7b1-5751-bf82-5b5a708fc0c3 | note | Ref docs - AS 3600 Table 4.4
e69b09b2-cdf5-5428-aef4-e949bf496c69 | note | Acceptance criteria - Minimum Initial curing requirement for 25MPa concrete:
79ef44bd-a4e9-56f9-878b-d32473300a61 | note | ○ Cure continuously for at least 3 days or minimum average compressive strength of 15MPa
ba3a5a33-291f-5dde-9970-a44d7c9c97af | note | ○ Has the formwork been removed in the same sequence as concrete placement to achieve similar concrete surface coloration?
921faeca-32f3-5c25-aac8-09369c86b408 | button | Acceptance | Yes,No,N/A
6b02bf20-0cae-52e6-a893-98805c0b4514 | note | Key - H
3415d278-4b6c-5ac1-9bf0-16b4ad23e672 | note | MDR/VIVA - W
| checkpoint | 4.9 - Saw Cutting of contraction joints
b3584f8c-4087-5948-adae-4bc70b8d08fe | note | Ref docs - IFC Drawings 235929-000-CV-SP-00007 6.4.4
1267435d-0168-57d6-882d-a319369264f9 | note | Acceptance criteria - Should the joint detail differ from design this shall be changed only with written approval by the Client.
504069d3-2226-5e28-b98d-7b1cc8822355 | note | ○ Saw cut joints shown on the Construction Drawings within 12 hours after placement.
95abdc03-7a98-5b25-8fd4-63450d4da462 | note | ○ The cut depth shall be 25% of the slab thickness.
a650b7ff-b4a2-5aaf-bcd0-f6912c160e5c | button | Acceptance | Yes,No,N/A
1258bb37-3d15-51f0-ae15-312980dded05 | note | Key - H
e92ed812-89e3-54fd-90bd-17007a324dd3 | note | MDR/VIVA - W
28f3b31f-8ee3-5ea1-9996-2a4ccf8eb462 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - RFI (if applicable)
| checkpoint | 4.10 - Post Pour inspection
fa8580ea-6edf-5d51-bdf4-a7362f56ed9c | note | Ref docs - 235929-000- CV-SP-00007
f4db46ac-1d43-5918-b0e0-b0a50f60a1ab | note | Acceptance criteria - All abovementioned works have been completed in-line with the drawings and specification and backfilling around structure can be completed (if applicable)
be608834-ba0c-576f-90f4-c10c635a1d27 | button | Acceptance | Yes,No,N/A
6aa9178c-1006-51e2-8680-efd41b2f1096 | note | Key - H
9f3c5a85-d1ca-5c2d-b538-341f4e586fd8 | note | MDR/VIVA - H
760951c0-c71a-5265-8cc1-94fce2f746e8 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
234dc14d-0c2a-5a12-88f6-7d773f4b8f30 | tickbox | Post-pour Checklist
| signoff | AUTHORITY HOLDPOINT
| section | 5.0 Completion
| checkpoint | 5.1 - As Built
a50a5d8d-0fc5-5922-8606-30c6d8a606a2 | note | Ref docs - YJRP-SPE- CC-M-0001
50f89dbd-0b41-5d4c-a750-14d7a41ee597 | note | Acceptance criteria - As built to be submitted after pour, showing set out, RLs, grades and any cast-in elements
1cb37836-715c-51d1-982c-19b821b09989 | button | Acceptance | Yes,No,N/A
ace517df-e1fd-56f9-b5ba-f1d7be4af77c | note | Key - S
c85a96e0-2524-5b10-a70a-51ebb47339ee | note | MDR/VIVA - H
6b872cd9-76d3-5757-b73b-be2fe76120b0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
4c4ac923-7050-53b9-aa9c-8dd13b0e9df2 | tickbox | Survey Conformance report
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 5.2 - Concrete Test Results
c49956b4-65e2-5375-a44d-80429af0f613 | note | Ref docs - 235929-000-CV-SP-00007, AS3600, AS1379, AS3610
e52813d6-d550-5f91-a97d-684002b78c9f | note | Acceptance criteria - Submission of 28 days results. Results meet requirements of 25MPa.
81177830-4201-5da5-b3ac-bf4b4d807677 | button | Acceptance | Yes,No,N/A
7c1bce3f-4988-54e3-99ea-7f254bbad6f1 | note | Key - H
9027f07b-bcb6-5e8c-9ad5-dc1919d85067 | note | MDR/VIVA - S
5ffd51fe-1035-5958-94ef-5a1bde40cfad | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
afefde41-bd67-5d64-a317-0f01f07ebea1 | tickbox | NATA endorsed test report
| section | 6.0 Crack Repairs (if applicable)
| checkpoint | 6.1 - Cracking repair methodology approval
6944e8d1-36b3-55ad-88cf-dc3bccfdb229 | note | Acceptance criteria - Contractor to submit a concrete crack repair methodology to MDR prior to commencing any crack repair.
6d2fea31-0f32-59d3-879e-e379bd8e6cd5 | note | ○ Has this been approved?
104f13ab-83cc-5653-abc2-bac0de31c0b3 | button | Acceptance | Yes,No,N/A
00450c35-382e-5b48-9fcb-899ee5c3510b | note | Key - H
ce587645-5945-5e12-9d2c-6e921c3a8a53 | note | MDR/VIVA - H
eaa3a7ee-9576-501f-bf6b-91e813534432 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
62802349-7d34-59c6-a9a8-bada7bc2fa6f | tickbox | Concrete Repair Method Document
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 6.2 - Crack Repair
8a5287bf-7fb6-5a94-8826-4178bf02c7e0 | note | Acceptance criteria - Has concrete crack repair been undertaken as per the approved method?
629f0d33-74c4-55ab-a297-0628c85149a1 | button | Acceptance | Yes,No,N/A
b1a356c0-4ed6-57f8-8285-8d2222ca9d74 | note | Key - H
ca801b5c-83ee-516e-ad20-83040eb49dee | note | MDR/VIVA - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0398-ITP-031 Blinding, Pile Caps and Slab Footings Rev D | itp | INF-HSEQ CC0398-ITP-031 Blinding, Pile Caps and Slab Footings Rev D |  | fb9861af-a689-4541-93a0-241e1cc8be4a
| section | 1.0 General
| checkpoint | 1.1 - Material Submission / Approval
38dc39c1-97aa-5987-bc61-8cc1a17d59b7 | note | Ref docs - AS 3600 235929-000- CV-SP-00007
66bc53e2-f270-563e-a4b5-d9d15ed3de85 | note | Acceptance criteria - Has the mix design to be approved prior to placement. Material properties meet project specification, AS 3600, AS 1379?
2051261c-d26c-51f1-a53b-15cc5181a8cd | note | ○ Do Structural Elements meet: Minimum Concrete strength 40 MPa or as specified in Drawings?
5f725601-87d4-5f25-98f8-ff0c4a102d4e | note | ○ Do Non-Structural Elements meet: Minimum Concrete strength 15 MPa or as specified in Drawings?
0b478f3b-221b-593b-bd2a-27904927049d | note | ○ Has Steel Reinforcement schedule provided to MDR for review and approved?
fd49ac14-fc4c-577d-b810-d73735edd6c8 | note | ○ Do admixtures shall conform with AS 1478.1 and are permitted if used in accordance with manufacturers instructions?
bfd4a202-eac0-583a-8d60-53ff6f4a61f1 | note | ○ Mixtures containing calcium chloride shall not be used.
1e83a2a2-1a47-58b0-9171-77d1d5b38a78 | button | Acceptance | Yes,No,N/A
de1c3c54-5e6f-59fd-9d9f-cc7d4a4f11f6 | note | Key - H
dc65c313-7a5a-5d5d-a677-e787b15d0c60 | note | MDR/VIVA Key - H
556114eb-a1b4-5385-b989-cb03ac46bf52 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Mix Design Number, Bar Bending Schedules, Material compliance certificates
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.2 - Determine lot size
5ae5a78b-cf2a-597c-bce9-680c9cdad51c | note | Acceptance criteria -
9cc93c84-89f3-523e-af5a-3b1a4e2623ca | textbox | Lot Size = Each pour section per day (location or m2) or each structural (Pilecap)
dfe7de41-a4ef-5ac9-b818-c1a6c13751da | note | Key - S
c76448c8-724e-5395-b5f5-34fc6089ff77 | note | MDR/VIVA Key - S
| checkpoint | 1.3 - Permits
9bff6d0e-771e-52a8-946a-8d127d399758 | note | Acceptance criteria - The following are relevant, in place and signed onto:
5af0f85a-9817-5358-b330-02e31e30ebc7 | note | – Penetration permit
da668d64-52b7-55d5-b6ed-31b53edc1a2d | note | – Hot works permit
f304070e-4b95-5b82-a3d3-695a812a5b09 | note | – Temporary work permit
79378160-af0d-5fa8-97d6-79591e53e5bc | note | – Working at heights permit
1b6ccd4a-1282-5b7c-b04d-9e07d17fb828 | button | Acceptance | Yes,No,N/A
138c99c4-157f-5bbc-9974-29302a05cf6b | note | Key - H
51da0678-2edf-5890-9cd5-b33a628dca49 | note | MDR/VIVA Key - S
| section | 2.0 Blinding/Lean Concrete
| checkpoint | 2.1 - Set out
86fe4bc4-62ff-5c40-9bb9-3a7cd82075f1 | note | Ref docs - IFC drawings
089626ac-9bbd-548e-bd18-dacf51ff92f9 | note | Acceptance criteria - Extents, grades and levels correct to relevant drawings. All services have been marked out.
33a08e2f-ba2f-5484-a2b9-57125200af6a | button | Acceptance | Yes,No,N/A
f591230a-d954-5fcf-a8ca-acc37573e700 | note | Key - W
a4ef8778-38d4-53a9-b6bb-1d5f4a174358 | note | MDR/VIVA Key - W
| checkpoint | 2.2 - Pre-Pour Inspection
ec7ee693-13c8-5626-ab42-5d7cca6da121 | note | Ref docs - IFC drawings, Pre Blinding inspection
508b44c2-a4d5-5b6a-8064-f431605ab32e | note | Acceptance criteria - Has a pre-pour inspection been completed with the client, and they have verified in writing that the pour is able to commence?
01eabe0a-10f8-5400-9041-d074788419d5 | note | ○ The foundation base excavation shall be tested, surface compacted and approved prior to placement of the blinding.
ae86cf42-f983-5714-ab6c-42571514a449 | note | ○ The foundation location, depth and dimensions shall also be checked and confirmed prior. to placing the blinding.
4de94789-0a5f-514d-b31d-d228bee0d2aa | note | ○ Approval shall be provided, in writing, by McDermott to the foundation. subcontractor before commencing with concrete placement.
766f8803-c430-5e51-9098-f4c55463bf94 | note | ○ Has this been completed?
be854e56-748b-562b-b097-10edb85de43e | button | Acceptance | Yes,No,N/A
85c6c7fb-2f8a-53f4-b9f3-8d5eac4d1f55 | note | Key - H
e6e9c8c3-c1d8-54f1-88e0-e11486688fa5 | note | MDR/VIVA Key - H
ca558a49-2270-58c0-a08d-98204cced2cc | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Pre-Pour Checklist
e926e661-5f2b-4bd0-9d7a-0948022852ac | note | ○ 235929-000-CV-SP-00007 Appendix 7.1 Pre-Concrete Placement Checklist
d18e565f-315f-5077-a941-29d82d8c1e6f | note | ○ Bearing Capacity report (if not on piles)
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Lean Mix Concrete
c0181690-db59-5f12-936c-d0cb9382f4ec | note | Ref docs - Section 5.1.2 of document 235929-000- CV-SP-00007
b999404c-0268-5609-b37f-fe95f278faf5 | note | Acceptance criteria - Approved Concrete Mix Design.
d4c31910-d804-590a-8b32-76c475a8e69a | button | Acceptance | Yes,No,N/A
6983f950-b771-5c06-850e-ab5b59e303b2 | note | Key - W
0c5e9dcb-64e5-5698-8cf9-c92c8380d069 | note | MDR/VIVA Key - W
15a44087-ddb2-5c30-a1fc-a12f8ba0a5ef | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Dockets
| checkpoint | 2.4 - Placement of Lean Mix
49209e33-c527-599b-bd12-ae606910c89e | note | Ref docs - 235929-000-CV-SP-00007
a84414c6-b35c-56cf-b14c-8fc6cd13cf02 | note | Acceptance criteria - Has the blinding been poured to the correct level? The following are acceptable:
5a62b3de-cf3f-5125-bd5e-4329bb47d03b | note | – Minimum Thickness = 50mm
6e9a8561-a3de-5bbf-a3cd-386009a4c82c | button | Acceptance | Yes,No,N/A
0a030111-d672-5aef-a44c-b2489fda43a8 | note | Key - W
7387a6ed-a301-5b0b-b17e-e8e79b0d6977 | note | MDR/VIVA Key - W
d5da4906-4e10-5691-b7c4-785fe3ed91e4 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - As-built Survey
| section | 3.0 Formwork
| checkpoint | 3.1 - Temporary works requirements
c7819eff-ac8d-5ff9-b597-0f2b6f3a4a78 | note | Ref docs - SYM-INF-Temporary Work Procedure IFU 05122
fb975dca-1c9e-50e7-9e2d-f87b208c3eeb | note | Acceptance criteria - Formwork above 1.0m to be designed by temporary works engineer.
2ab242e7-9df3-5ef7-8398-aa12988d9771 | note | ○ Has design to be undertaken by external consultant complying with AS1170 and AS3610 plus any project specification requirements?
4478758b-9afd-5146-93d3-af9f63a08daf | button | Acceptance | Yes,No,N/A
f8449bb5-6135-5252-a322-90a42793f594 | note | Key - H
1f9c2ac4-53bd-5031-986d-94e9fcfd3364 | note | MDR/VIVA Key - S
| checkpoint | 3.2 - Pile Penetration
ca94c097-afa7-5f79-a50e-916650438797 | note | Ref docs - Civil Drawings IFC
20309ffe-f6ee-590f-9186-18ba5bd6f161 | note | Acceptance criteria - Pile C.O.L to penetrate 50mm above blinding of pile cap (+/- 25mm).
7b063ac0-ac9b-5948-9e3a-1146ce759369 | note | ○ Has the pile been determined to be free of cracking and concrete damage following cropping?
9f1bb396-e983-53ed-ba99-e6d9d34cd1a8 | button | Acceptance | Yes,No,N/A
344e6758-6c88-5409-8f2f-0a58e050cf22 | note | Key - H
9de46810-e107-5e8a-96c8-6c10f3f048d1 | note | MDR/VIVA Key - H
854479c7-f6e2-581e-8033-e770c58f9fef | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Survey Report
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Formwork Setout and positioning correct
5535dc21-45a0-5166-aeaa-70a54f48f3ca | note | Ref docs - Civil drawings 235929-000- CV-SP-00008; Section 6
e7480757-5b6f-5994-b7b2-b90610675b29 | note | Acceptance criteria - Is formwork checked for potential loose sections, ensuring no movement upon placement of concrete?
5b47baf0-737f-596f-9bbf-ebb400095fe0 | note | ○ Is formwork in line with survey markings?
7f7dd498-3c4f-5eff-9bc5-ce271fcbfc67 | note | ○ Have chamfers (if required) been attached to formwork in level manner?
7d1dcfdb-096d-5461-ab3a-78ebee5e310f | button | Acceptance | Yes,No,N/A
7ad068b9-91fc-590d-b608-0150ab8ff736 | note | Key - W
1b82924b-a9bb-5542-aacf-0703c64a07b0 | note | MDR/VIVA Key - W
| checkpoint | 3.4 - Concrete jointing
4f59ced6-d6b0-5831-837d-bf1581fcd594 | note | Ref docs - Civil drawings
91eede06-c374-5b5f-92ff-d89a7db6e3f2 | note | Acceptance criteria - Have construction joints to be installed as detailed on Drawings and notes using correct materials?
5721c9c0-a3fc-546a-97d9-092302ebc07b | button | Acceptance | Yes,No,N/A
0228c326-27c4-510e-b07a-cb7faf01793e | note | Key - W
4c1d22f1-532a-514d-9c9b-f26cbffbb870 | note | MDR/VIVA Key - S
| section | 4.0 Reinforcement
| checkpoint | 4.1 - Steel reinforcement supply
f42931b2-66a1-51f1-be50-2c7e599cc49e | note | Acceptance criteria - Have steel tags checked against supply schedule prior to installation?
61b24da6-4ac4-5952-8d6b-4337b1843aec | note | ○ Does the manufacturer hold a valid ACRS certificate?
fd813473-0387-5126-a63b-b569baf3b18c | note | ○ Is reinforcement is free from rust and other contaminates that may affect bonding?
e59386e9-e209-5aaa-82f8-cdd0697773db | button | Acceptance | Yes,No,N/A
890a24d8-f366-56c7-b083-3bffc08bdef2 | note | Key - S
8221f792-3caa-5c2e-ba97-26cff7f5ab2f | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Delivery Dockets / certificates / product tags, Incoming material checklist Photo’s
| checkpoint | 4.2 - Steel reinforcement installation
d22409ec-ccf9-5370-b6eb-4dbbf8715b67 | note | Ref docs - 235929-000- CV-SP-00009, AS3600 17.5.3, 235929-000- CV-01-92002- 010002
6810c17f-d835-59a0-ac94-7a3df2f24a31 | note | Acceptance criteria - Is steel installed as per the latest IFC drawings?
70f1ae2d-0b63-5ef3-8fa0-1d2c9a22913e | note | ○ Does steel reinforcement conform with Steel Reinforcement Specification?
866f16bd-0658-51b0-95d6-2bc197050c44 | note | – – – – – – – – – – – – – –
4fdf6b1d-4ff2-5ef9-9362-2baa7e9ab501 | note | 17.5.3 Tolerance on position of reinforcement and tendons
216d941c-878a-5ede-ab23-3d86b51297ec | note | The deviation from the specified position of reinforcement and tendons shall not exceed the following:
bf01ae81-1011-5a6a-81c4-8f7e5eb74919 | note | (a) For positions controlled by cover –
e7b5e44b-7575-5e12-a0c2-ecaff87cd733 | note | (i) in beams, slabs, columns and walls: -5, +10 mm;
f8f39c39-2cfc-51fd-ba00-ce6cfa6e2b3f | note | (ii) in slabs-on-ground: -10, +20 mm; and
ea7f388f-2b47-5ff4-8246-2e841888ff04 | note | (iii) in footings cast in the ground: -10, +40 mm,
a4f8bc42-4867-53e0-b2a1-65ce6b07823a | note | where a positive value indicates the amount the cover increases and a negative value indicates the amount the cover decreases.
823636fa-9bb5-59e4-b47f-57b5832f0b1c | note | (b) For positions not controlled by cover, namely –
b9133cb8-cb80-5600-aaaf-d6ee1eb8d8d1 | note | (i) the location of tendons on a profile: 5 mm;
99065f29-b07c-594f-841c-6df3a506c4d7 | note | (ii) the position of the ends of reinforcement: 50 mm; and
af268ade-110f-5716-a4cf-67cdaebfb06a | note | (iii) the spacing of bars in walls and slabs and of fitments in beams and columns: 10% of the specified spacing or 15 mm, whichever is greater.
ee259f74-8863-5c36-899c-9be71202c541 | note | – – – – – – – – – – – – – –
16a1861c-5b6b-5fc6-846f-36200d7dcc3b | note | ○ Has minimum cover to inside face of wall must be maintained? All reinforcement shall be in accordance with AS 3600 & Civil drawings.
d2fe726d-b515-5987-9f1d-bbd12508d9b8 | note | – – – – – – – – – – – – – –
d63c2bfc-fe63-5578-a6d5-82ffca82744a | note | 8.1 CONCRETE COVER SHALL BE IN ACCORDANCE WITH AUSTRALIAN STANDARD AS 3600 OR THE VALUES STATED BELOW, WHICHEVER IS GREATER.
0f40a8cf-669f-53ed-9c92-6f5ebb5f02ac | note | ○ PAVING (TOP) = 30 mm
6d8f4b08-39eb-5b25-8d96-a62bdab591f1 | note | ○ PAVING (BOTTOM - AGAINST GROUND) = 50 mm
16e94149-4024-5b9f-9d6f-42ae460a5559 | note | ○ FOUNDATIONS CAST AGAINST FORMWORK (INCL. EXPOSED WEATHER FACE) = 45 mm
021a922d-e5d0-513f-890d-c06debe22372 | note | ○ FOUNDATIONS CAST AGAINST GROUND = 65 mm
0973c0aa-da2f-5900-88f6-b3260841c5fc | note | ○ EXPOSED TO WASH DOWN WATER AND/OR PROCESS SPILLAGE = 50 mm
81964aa0-8a8f-543e-8519-793fafead59f | note | ○ CAST ON LEAN CONCRETE = 45 mm
c7557033-23b8-54df-98eb-9909d90dc9ca | note | ○ CFA PILES = 70 mm
9926baa2-c277-5d16-8aa2-294dd6120c87 | note | – – – – – – – – – – – – – –
7e9e464f-63c6-50ef-a40b-8ee9989570f8 | button | Acceptance | Yes,No,N/A
9f00da5c-02b5-57c6-9ee4-45d014933309 | note | Key - H
5d6b38f5-845a-5e80-993e-560195f284be | note | MDR/VIVA Key - S
05102a51-0c35-550a-ad38-1a1984d66084 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - IFC Drawing Number and Revision
| section | 5.0 Structural Concrete Pour
| checkpoint | 5.1 - Pre-pour Inspection
239ffe9e-5ec3-5fd1-b0c4-f20c7e67ae4b | note | Ref docs - 235929-000-CV-SP-00007 Appendix 7.1 Pre-Concrete Placement Checklist
4db2740b-4bb6-5ccc-b27e-5b092ab54960 | note | Acceptance criteria - Has a pre-pour inspection checklist completed prior to placement?
0b4afb99-2b27-5759-b940-2528358e76b5 | button | Acceptance | Yes,No,N/A
9236e013-4ce8-5ec0-bf67-f3a5d594cb12 | note | Key - H
b137a84d-23cd-5150-ada7-fac772779c01 | note | MDR/VIVA Key - H
52f81244-cb49-539d-80e2-05c4178e5004 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - 235929-000-CVSP-00007 Appendix 7.1 Pre-Concrete Placement Checklist
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 5.2 - Placement
cf45ad69-6304-520e-ac92-0418c788afea | note | Ref docs - 235929-000- CV-SP-00007 Appendix 7.3 Concrete Truck Record
b20d327c-4997-5b05-b905-9173ff44a912 | note | Acceptance criteria - Concrete shall not be placed when temperature is less the 5°C or greater than 36°C. Between 32°C and 36°C admixtures and placing requirements must be met.
3b518dbe-f4ef-51f9-a0de-f4b0f17e3944 | note | ○ Concrete shall be transported, handled and placed to prevent segregation, loss or leakage of materials.
90b508b7-9702-5ee3-921a-475378d98e79 | note | ○ Concrete shall not be dropped from a height greater than 2m.
5f46a6c2-e296-59d7-83f1-6aece02703d6 | note | ○ Concrete shall be discharge within 90 minutes of dispatch from plant.
2deae49a-8fe0-535d-9ff4-94c49e292fcc | note | ○ For continuous pours, the maximum time lag between truck loads shall not exceed 25 minutes.
a8eeefbb-ca7c-5b1d-9a41-e4a56283a0b2 | note | ○ Concrete shall be thoroughly vibrated to ensure no honey combing, voids or surface defects occurs and compaction is achieve throughout structure.
77a59b85-24df-5680-8886-66f8739d49d4 | note | ○ Water shall not be added to achieve slump greater than that specified. Slump test to be completed after water is added.
895d47a5-a1aa-549c-a38c-11b1e0dd2ae1 | button | Acceptance | Yes,No,N/A
2f23a380-2723-599a-8be2-b9d622724aab | note | Key - H
74c06dfc-9064-5b62-9ade-07340b55e3cf | note | MDR/VIVA Key - W
0d5bea98-5a15-51b4-a762-f1c9019ae34c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - 235929-000-CVSP-00007 Appendix 7.3 Concrete Truck Pour Record/Dockets
| checkpoint | 5.3 - Slump Test
df23455f-3b5a-5d55-8fac-fa1d22e46fe8 | note | Ref docs - Section 5.1.1 235929-000- CV-SP-00007
32e1fcef-a061-5f7c-ba59-e3482e2575f3 | note | Acceptance criteria - Slump must be within tolerance of designed slump.
c2171f33-7ce8-5763-adaf-bb6787dbadbf | note | ○ Testing shall be +- 15% of stated.
86df0126-48a2-5e18-bd77-5ff70ac53d96 | note | ○ Approved mix design slump
d1ef89bb-380e-5796-91f7-2829c0908bde | button | Acceptance | Yes,No,N/A
ecd5aa8f-f4ed-54d6-a786-af29109ff584 | note | Key - S
16baa9ec-1bc4-597c-b27e-8406c7aa512f | note | MDR/VIVA Key - S
f6a24409-a0b3-536c-afca-48d362553b0f | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test docket
| checkpoint | 5.4 - Strength Testing
6a712eec-24b0-515d-b216-0914620452ee | note | Ref docs - 235929-000- CV-SP-00007 Section 6.8
436c519e-acfa-54a4-9e8c-583a2586890a | note | Acceptance criteria - Samples to be taken from chute. 5 cylinders collected per sample – 1x 7day, 3x 28day, 1x reserve.
36fa5d97-aa53-5a90-b994-98f5f4f0ebc9 | note | ○ 1 test for the first 20m3
5d6827c1-535d-50ae-b753-418f1a284471 | note | ○ 1 test per 40n3 thereafter
35fcfc0c-c309-5d8d-9de0-4c58c778f5bf | note | ○ Frequency reduce to 1 test per 80m3 for pours over 400m3
322fdf96-ea09-5a44-ad31-dbc9ae3f6d98 | note | Acceptance
a0426478-4d97-538c-b10c-52d69069e918 | note | – – – – – – – – – – – – – –
1d705805-ea00-5501-94af-40d2904998cb | note | No. of samples ¦¦ Volume of concrete (m3)
eeedf888-d6b9-54ea-a141-1f1d40027f74 | note | – – – – – – – – – – – – – –
bbc71923-925e-575e-98d7-466e7be68a57 | note | 1 ¦¦ <20
5a9c0c7a-b950-5538-a8d8-739efd701cfe | note | 2 ¦¦ 20-60
e971d102-313c-5225-a980-fd95f29b565d | note | 3 ¦¦ 60-100
80c633b5-0611-5e1b-861a-88805ff61a31 | note | 4 ¦¦ 100-140
e2ab1c0c-441c-5b5d-9c66-11b4d40eb400 | note | – – – – – – – – – – – – – –
9983feff-0c46-5f99-948b-86aed595806f | note | Key - H
45500009-804d-54b6-8fed-29d19bac0829 | note | MDR/VIVA Key - S
180eefb4-5dcc-5324-a1ed-2aaee9d8ddcc | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test report
| checkpoint | 5.6 - Curing of Concrete
f7c0712b-8955-55e8-ab27-f69d4626a3a7 | note | Ref docs - 235929-000-CV-SP-00007 Section 6.5
c1edee11-ee08-5473-b83b-4a2a6ed25110 | note | Acceptance criteria - As per the approved Curing Methodology.
adf2a0c3-8e3f-5603-81f6-b2380f89ae5a | note | – Applied once bleed water has gone
65f5950e-d5e8-54bd-8253-75674123c1e6 | note | – Continuous uniform film achieved
cb076cc0-2c21-551d-bb2e-620e61c15228 | note | – Rate of 5m2/L
b5547988-aa51-55c8-a251-12d415d7da7d | note | ○ Has curing been conducted as per approved curing methodology?
817fae1c-00a7-52d5-a06c-fbc361bf5901 | button | Acceptance | Yes,No,N/A
17874744-6164-5a97-933e-416f164d96fc | note | Key - H
1e74c937-5f23-5ec4-bba8-f6195146f428 | note | MDR/VIVA Key - W
92fa07e0-a3fe-5057-a34f-dd18e3de53c6 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Approved Curing Technical Data Sheet
| checkpoint | 5.7 - Concrete Finishing
ca172474-abe9-5707-9354-92222823cb7e | note | Ref docs - 235929-000-CV-SP-00007 Section 6.4
0e6e3ad2-49b5-5869-92fb-3e51d525d504 | note | Acceptance criteria - Finish concrete per schedule below:
a0814925-0f71-561b-b587-d7a05fccbb1e | note | ○ Interior walls or columns exposed: smooth form/rubbed finish.
c5f50b3a-6d8c-5caf-9989-bb2fea7549bf | note | ○ Exterior walls or columns exposed: smooth form/rubbed finish.
5ecdd4ef-02b2-56c3-bb96-20a75b791a03 | note | ○ Walls below grade: rough form finish.
d6ea72f1-fd74-5653-ad3c-401c3053c4f9 | note | ○ Exterior slabs for spill containment: float finish.
a6b1b127-b96e-5e22-9317-4a01d53b7d2c | note | ○ Other exterior slabs (i.e. foot traffic): broom finish.
bc06f7d0-e86b-5d4f-a708-03e036c88fd7 | note | ○ Interior slabs: steel trowel.
a11f21c5-2d68-555f-8348-706701894c3a | note | ○ Interior slabs to accept additional finish: steel trowel.
9dea0913-2eda-5e7d-b7bc-d4c125d26d0b | note | ○ Surfaces to be grouted: rough [6 mm amplitude] but even finish with laitance removed to provide good bond between grout and concrete.
a30e398c-0496-5a92-b198-9caff7926968 | button | Acceptance | Yes,No,N/A
860f64e1-1579-5c3c-ad59-70ce5fcc6bdd | note | Key - S
1c75f4e8-aabf-5861-9841-72c7b9f3affc | note | MDR/VIVA Key - S
315fb1fd-846f-5914-a953-3709828694a0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - 235929-000-CVSP-00007 Appendix 7.3 Concrete Truck Pour
| checkpoint | 5.8 - Formwork Stripping
fa3a5756-6946-57eb-acac-9d5d87d55622 | note | Ref docs - 235929-000-CV-SP-00007, AS1510, AS1509, Section 6.6 of 235929-000-CV SP-00008 CONC FORMWORK
8b21296e-c06f-5993-954b-ae76c7df9417 | note | Acceptance criteria - Has Remove formwork progressively so no unbalanced loads are applied to the structure, or concrete is damaged?
0c2c6fda-7612-55fb-aefd-5e0c545ef761 | note | ○ Has the formwork been removed in the same sequence as concrete placement to achieve similar concrete surface coloration?
50ba77fb-2509-5919-89c0-9c478a004902 | note | ○ In accordance with AS3600 Table 4.4 and Section 17.1.5, removal of forms before 7 days would require a curing membrane conforming to AS3799 to be applied immediately or any other approved acceptable method of water retention in the concrete.
621e2dc8-4940-5541-bdf8-c42a4b914fca | note | ○ Has this been completed?
501e0beb-5a27-5550-b675-c737dea147cd | button | Acceptance | Yes,No,N/A
396cd9db-d4ed-5070-8c8c-3651e219380c | note | Key - S
a95a6b67-8daf-5635-8665-fea3aa2b89dd | note | MDR/VIVA Key - S
| checkpoint | 5.9 - Post Pour inspection
83b22758-b60c-5795-93f8-c10d1940174c | note | Acceptance criteria - All abovementioned works have been completed in-line with the drawings and specification and backfilling around structure can be completed (if applicable)
481205fd-06dc-5e83-86f2-969975dc853b | button | Acceptance | Yes,No,N/A
1700a992-191f-5f1d-82cb-31f02e3c63b6 | note | Key - H
ec247bc9-a2be-5b86-9e16-1a94cc9299f9 | note | MDR/VIVA Key - H
| signoff | AUTHORITY HOLDPOINT
| section | 6.0 Completion
| checkpoint | 6.1 - As Built
a4a248be-348c-596f-bb94-db2e17b0b3ee | note | Acceptance criteria - As built to be submitted after pour, showing set out, RLs, grades, extents, bolts, grout tubes, starter bars, etc.
dd426662-ba58-5d08-a428-ffd5f9a65067 | button | Acceptance | Yes,No,N/A
31c043f2-f95a-5193-af01-8d294bcbac7a | note | Key - S
2eae9447-6a3d-5a16-9da6-e962fa10673d | note | MDR/VIVA Key - H
f461e7b7-35df-5ee5-b3f2-3cd1c91fea8e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Survey Conformance report
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 6.2 - Concrete Test Results
b0567501-b655-5047-805f-92a97030f726 | note | Ref docs - 235929-000-CV-SP-00007 AS3600, AS1379, AS3610 IFC drawings
4c830c25-5a30-5cde-8b1c-c4ad69c131fd | note | Acceptance criteria - Submission of 28 days results. Results meet requirements of 40MPa.
882fd5d6-c066-5d45-ac9e-f6265108dcbe | button | Acceptance | Yes,No,N/A
9378086f-efbb-56df-a8d4-c7f36335e80d | note | Key - H
62736c2b-c383-51eb-814a-f744b74d40ff | note | MDR/VIVA Key - S
da0c4da8-e8c2-5f85-8aaa-0ab3912af901 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - NATA endorsed test report
| checkpoint | 6.3 - Concrete cracking approval
ee34ac15-e616-59bb-8540-c270d0479483 | note | Acceptance criteria - Contractor is to submit a concrete crack repair methodology to MDR prior to commencing any crack repair. Has this been approved?
ef164b3f-5bce-5145-a896-fd14f3aa7aa9 | note | – – – – – – – – – – – – – –
c19c26dc-0b16-532a-bdcc-050cae2b75d3 | note | Maximum Allowable Crack Widths in New Concrete
843c554a-8132-52c5-9c68-020dd3a3602f | note | – – – – – – – – – – – – – –
34360a93-ec16-558c-8d16-8eaae13492ef | note | Service Exposure Condition ¦¦ Crack Width, μm
a11b7ea0-7c7b-5a1f-afef-85f410f63e8c | note | – – – – – – – – – – – – – –
7c9647fa-d9e2-5392-b4b3-156699739c90 | note | Interior ¦¦ 300
3105f302-a6da-57b6-aee1-73160c8d4993 | note | Exterior air (or soil) ¦¦ 200
320853ad-9ad1-5686-87f5-fd0b0b860ad3 | note | Water-retaining structures ¦¦ 100
f5b4a7d2-f20c-59ea-b522-91085f645b10 | note | – – – – – – – – – – – – – –
75e83a5f-9507-5d54-aefc-f438730e4bd0 | button | Acceptance | Yes,No,N/A
318f2ad8-d665-5344-8acb-3bf3225ac2b9 | note | Key - H
b16419de-1901-5fd9-bfea-cc56b3ed6245 | note | MDR/VIVA Key - H
6d3a76c9-6037-5d0a-be16-9752f81fb2ae | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Concrete Repair Method Document Approval
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 6.4 - Concrete cracking repair
4690863e-91d7-573c-928b-0dc622373387 | note | Acceptance criteria - Has concrete crack repair been undertaken as per the approved method?
d5217aab-b234-5307-ba82-f79ac01566e9 | button | Acceptance | Yes,No,N/A
0a981ae8-f477-5408-a8fb-c610b4e47dfc | note | Key - H
b6f635be-858e-52e8-b614-4c5c61f0214a | note | MDR/VIVA Key - H
cb75cf7c-87e6-551c-a1d3-29fc188af5aa | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photo’s
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 6.5 - Leak Testing
f0bc5ff6-a703-5ea3-94ad-c84071958231 | note | Ref docs - 235929-DM-AT-000002
ad1590fb-52e5-5324-9352-8b43e5d1fbb2 | note | Acceptance criteria - Has the nominated structure had leak testing completed and passed as per the approved testing procedure.
bc84f206-8228-5747-819f-45f42a58d86f | button | Acceptance | Yes,No,N/A
235c43bb-6a7e-51e4-bd2a-d180ad9dea00 | note | Key - H
e4da6402-2ff7-5c05-9008-d7774e20e814 | note | MDR/VIVA Key - H
a9b4c81b-fe00-5038-b395-33a02fd6f0bc | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Water Test Check-list
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0398-ITP-032 GRE Installation Rev 1 | itp | INF-HSEQ CC0398-ITP-032 GRE Installation Rev 1 |  | 89d4c807-6fd7-47cb-ab95-9fa653e64bf6
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Set out
30713abf-c728-50b9-be2b-6ed4b4a9e9d2 | note | Ref docs - Drawings
786e257b-6d88-5f96-94c1-2ea430fa376d | note | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
3b23c7b9-71f8-5b57-a725-40fe12f52f8c | button | Acceptance | Yes,No,N/A
4cf31203-4eee-51d6-9509-a70825913db4 | note | Key - H
e413c664-690d-5106-b782-861b88454577 | note | MDR/VIVA - W
65d4218c-b18d-5ae5-8445-1dcdeeee490d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e2899be5-b8d7-58b5-84bf-564a010beee8 | textbox | Drawing No.
b405ebfc-9fbe-5046-b9cd-df742066b028 | textbox | Rev
| checkpoint | 1.2 - IFC Submission & Approval
f96de24c-a172-59b5-81b7-e8d30660ffd6 | note | Ref docs - Drawings
1993cee6-53af-5cdf-914a-2a07012ec46d | note | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
00df8c37-fe2a-5b97-bbf3-5323ec4dcbbf | button | Acceptance | Yes,No,N/A
588c79be-bedf-5ff9-a61a-09045614bcfe | note | Key - W
239d854c-89d2-57f5-b7e9-6b1b122f3c5f | note | MDR/VIVA - W
| checkpoint | 1.3 - GRE pipe confirmation
ba7e2e4d-dbad-5f0e-92b7-ea558b642845 | note | Ref docs - Drawings, QF-108-01 Material Receipt Initial Inspection
936cd6f9-24e6-5ed5-aca3-7df2086375d0 | note | Acceptance criteria - Has the correct class & type of GRE pipe been supplied and free of defects?
b52e2cad-3baf-5e11-93f5-bf50dfda8077 | note | ○ Verification of material tag (heat) number
54e1cb37-b599-5877-ac4e-d086997d692a | button | Acceptance | Yes,No,N/A
de104475-90b8-5af3-8ec7-309b331a5bfa | note | Key - H
eb5c0fc7-f264-5168-824f-f7e78a91288a | note | MDR/VIVA - W
fe2dca5e-38b0-54a9-a1c8-c7323eda5c20 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
97378374-0cce-5b5b-ae85-b1843024c635 | tickbox | Material Inspection Checklist
| checkpoint | 1.4 - Permits
facfa38f-1cd7-58f0-a248-1fb4e787f1d0 | note | Ref docs - Symal Safety Procedure
25f4168a-d062-5e3b-aa57-b46b9db0948e | note | Acceptance criteria - Have the below permits been created as required.
e80a82e8-381a-531d-bcea-0134343b8a00 | note | – GPP
e47e8d71-7556-5d5f-8ed5-4e7b509a2c12 | note | – Working at Heights
b664ff73-05f5-51df-99d4-216f445adade | note | – Hot Works
cee09680-e01f-552a-aa6d-7b3e898cab09 | note | – Confined Space
15b6ba1d-3c9e-5ded-8ab0-30aa5438e010 | button | Acceptance | Yes,No,N/A
f8c19699-76b6-5e43-a329-cab66101b23e | note | Key - H
0ef20b02-7e86-5f25-9348-87e9cc93d093 | note | MDR/VIVA - W
| checkpoint | 1.5 - Determine Lot Size
e21f428f-a0bc-5753-8bb3-35c1d7d4868f | note | Acceptance criteria - What is the lot size?
2663c145-56ab-5646-b24c-8286a8e0e071 | button | Acceptance | Yes,No,N/A
19d3046e-c7cb-57bb-bb39-8b3e3fc79912 | note | Key - S
be91c779-2273-528c-8cab-08fae293e146 | note | MDR/VIVA - W
48a2fae0-d4d3-52d5-91d3-e3757a3f64f7 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
0e5fb777-fbc3-5563-9810-4fdb69d32e65 | tickbox | Lot Map
| checkpoint | 1.6 - Joint Pre-Qualifications
1da3b421-5826-5393-84df-468965e8b937 | note | Ref docs - Qualified technician qualifications and this ITP
b89d1b2b-6593-5bf4-b701-1e0fa94ca9e1 | note | Acceptance criteria - Technician qualifications submitted to client for approval
6c601e05-23e8-57e0-9dbd-3f2e7ca6d618 | note | ○ Welding Qualifications Equipment Calibrations
0320eb26-4f89-5952-9e5a-12a6042e28ec | button | Acceptance | Yes,No,N/A
06ae4ce3-f304-53b7-92f6-27013394d5c9 | note | Key - H
f23d664f-473f-5e88-887c-df62ed7d6583 | note | MDR/VIVA - H
693d66bf-e7ff-5a87-acd9-365576b0e6bf | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
733e509e-ab28-5d1a-8831-c6361343a3b3 | tickbox | Certifications provided to client
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.7 - Material Approval
4f5ffb21-a37b-5c66-987d-32a2250ad910 | note | Acceptance criteria -
7979c967-4c4d-5c97-8fc2-40445dcac3e5 | note | Have all materials been approved for use
684403d9-1876-58f4-af5a-3db3e7715e9d | textbox | Bedding/Haunching Material
5b25a19d-79c4-5f1a-a4cf-f6ae4256c98a | textbox | Backfill Material
ecff2fb0-fee7-5349-92fe-09c4c47939e5 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
30197b59-df69-54e2-beb4-cc07e29b22c1 | textbox | Material Approval Reference
| section | 2.0 Excavation and Bedding
| checkpoint | 2.1 - Service Locating
cf29ad10-f86e-50dc-9540-73ee4d504b63 | note | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
9cdd3930-cd3c-5455-a906-8d4d841d96f9 | note | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
44c97db5-6c6d-55a7-b059-b5b01305bef3 | button | Acceptance | Yes,No,N/A
74b04a3e-3017-5527-a473-10ae7f2b9fa6 | note | Key - H
32df1a5b-1a2a-5b6c-a049-a9911ebd6328 | note | MDR/VIVA - S
| checkpoint | 2.2 - Excavation
16fbca72-4794-519e-a9fa-4e1de14d41bb | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALLSect ion 12.1.12
62155c81-3b03-5392-b137-1d0fd014cd4d | note | ○ SUN_ENG_P RO_015 Bondstrand Piping UG Installation Procedure Section 3
bb9363e7-048f-5d7f-9c6a-127e57cd2445 | note | Acceptance criteria - Excavation shall be to depth adequate to provide full specified bedding depth.
a53247f9-7304-595a-8b9c-353ff3bfc137 | note | ○ Width of excavation to be 1.25 * OD + 300mm
a82df1b2-f768-53a0-a213-1f4d37bb5124 | textbox | Pipe Diameter
5fa84543-4642-5d7d-bb14-07e154d9c9df | note | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
92fc4509-5166-59ea-96b5-f0bbd04d6c99 | note | ○ Trenches to be benched and battered as required (if trench >1m deep). Benches/batters to be 1:1. No material/plant to be placed within zone of influence.
de1d88cb-9936-5a9a-a462-b08004b2418a | button | Acceptance | Yes,No,N/A
ca7decc9-bd3d-5b95-875b-90d1d27d6afc | note | Key - W
c277ddbc-ba32-52ba-9e7c-e0bab806a685 | note | MDR/VIVA - W
| checkpoint | 2.3 - Bedding
54faa16d-8371-5b8b-bec7-391dde68b4e2 | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8.
f386c04f-2692-5e15-b5d1-61a2ab2612c2 | note | ○ 239529- MG1668- 15740-0400- SD-000010- NOV Bondstrand pipe installation guide - GRE
be5c67d8-a9c2-5bf9-a44c-859551ed1361 | note | ○ SUN_ENG_P RO_015 Bondstrand Piping UG Installation Procedure Section 3
307f42ad-853d-598d-b7ce-168ed0d96f2c | note | Acceptance criteria - 150mm Bedding to be placed & compacted at the base of the trench.
a6732c34-6ebb-5d32-8ae0-4b8821ec0739 | button | Acceptance | Yes,No,N/A
c9d859d5-68ae-5fc6-9df0-e89bfe051a13 | note | Key - S
5428a919-e1c4-57f0-9e89-a65ea123f96a | note | MDR/VIVA - S
a6dd7323-79be-573b-af5a-b1975bfa15b0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
0b8e0979-7ff9-5f98-9748-6f5c29201350 | tickbox | Delivery docket
| section | 3.0 Bonding & Laying
| checkpoint | 3.1 - Above ground fabrication
ac128511-4058-54f3-abc5-477770663af0 | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
24c01a29-bf81-5ec9-a0c0-e9381b39454f | note | Acceptance criteria - Has works been conducted as per Sunrise ITP SUN_23_003?
e1039a33-f996-56f4-9ac0-6c7ef7b6b1bc | button | Acceptance | Yes,No,N/A
7c318ffc-084a-5803-97d2-23e993a23be9 | note | Key - W
ad16aebf-dfd2-560a-9ad7-19d2b80f5f7f | note | MDR/VIVA - S
149682e8-cca6-5aff-8df3-e93af23b1f9c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ce8994a6-7625-5ba1-ade7-29640d9d99f7 | tickbox | QF-068-18 – GRE Bonding Joint Record
| checkpoint | 3.2 - Lifting into trench
8e861b5d-2860-52e7-8cf5-69cf6dbd59c6 | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.2.1 Item 12.2.7
7c1c5b9d-26fe-5349-8623-42f0eb01bdce | note | Acceptance criteria - Before lowering in, caps shall be placed on open ends, flanges, etc., which shall remain in place until piping connection can be made. Particular attention shall be given to the need to protect pipes from damage due to loads from heavy plant, has this been completed?
0ae23950-b10e-5318-afc9-b6c1442dd3a4 | note | ○ Have pipes been laid to true line and level?
c65b0773-d204-5979-80bb-ff6a3629d952 | note | ○ Has MDR been notified before the laying of pipework?
86849bfc-cf35-5ada-b8b9-2f6ac00abff1 | button | Acceptance | Yes,No,N/A
61838248-ac87-5356-a463-5bfd1bfff234 | note | Key - W
d94489fc-0488-594b-8b37-2bcb1844d20c | note | MDR/VIVA - S
| checkpoint | 3.3 - In ground fabrication
dd92a3d5-6faf-55a8-88ab-3d2e1b31ef42 | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
72f09452-57bf-51ff-960b-702c99a35d79 | note | Acceptance criteria - Has works been conducted as per Sunrise ITP SUN_23_003?
741c6690-04de-5cc0-83bc-66718277384d | button | Acceptance | Yes,No,N/A
debd8762-a75c-54cb-8faa-652eba5c170e | note | Key - W
2afe1bed-fd29-5200-9503-285e0c55a3c5 | note | MDR/VIVA - S
9b72c91b-ca8e-5082-bb73-53d305b34568 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
f0f767ce-8ab1-5fcc-8ac6-8ce53bd3aaa0 | tickbox | QF-068-18 – GRE Bonding Joint Record
| checkpoint | 3.4 - Haunching
0b2e9937-b249-51fa-8f22-89fcf2e2d0be | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
57ddd853-6e4a-58ce-b5bb-6c5d199d68b6 | note | Acceptance criteria - Has the pipe been haunched?
0fb8dd1a-6b10-5d5b-9199-ff5784090173 | note | ○ Have voids been removed from haunching material?
ae52b1d8-8849-5f4d-bac9-d89e53d43c2a | button | Acceptance | Yes,No,N/A
7f6caa72-8b13-5cf2-ae14-d7b7e35fec87 | note | Key - W
d2485979-e57a-59e8-bbc2-455441c4159a | note | MDR/VIVA - S
| checkpoint | 3.5 - Survey Pickup
8f6a8730-4ed1-5d87-9e55-365b105e9f06 | note | Acceptance criteria - Has the pipe been picked up by the surveyor? Tolerances in alignments shall be limited to +/- 25 mm vertically or horizontally, unless otherwise specified on engineering drawing, has this been completed?
89542738-7ef5-526f-8dab-702b999f512b | button | Acceptance | Yes,No,N/A
d8c1fafc-8cc4-5772-87f5-147a8d20f6a3 | note | Key - H
5bc1259f-2ac4-5069-9458-305c5e040340 | note | MDR/VIVA - S
2be8cae6-4c17-5bfd-88f3-4504bac1dc0f | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
9060a391-0bcb-5407-b7d7-e5964bc20d1b | tickbox | Survey as-built report
| section | 4.0 Testing and Conformance Check
| checkpoint | 4.1 - Test Pack
02a3257c-afbb-5eef-8166-5ca6f887ca65 | note | Ref docs - SUN_ENG_P RO_010 R0 GRE Hydrotesting procedure
bc78c93e-6e45-57fc-9b6e-c941fadc02d4 | note | Acceptance criteria - Has the test pack been reviewed and accepted prior to Hydrostatic Testing?
d828e2cb-e953-54ab-9fab-95395747e17f | note | Test Pack to include:
77abd582-cab0-5f60-b942-9da198e90dea | note | – Pipe Runs/Location of testing
09dbcddd-e90b-5e47-9782-1eab54dcf140 | note | – Materials initial inspection
52d47666-02c6-5293-9aef-fd5a0c513019 | note | – Joint Inspections
66a26b63-0d3e-5c48-94d4-93cc42915f80 | note | – GRE Bonding Joint Record Form
fa1782ea-204f-5d5e-b4b4-93018f62be9f | note | – Flange Record Sheet
9b008a47-6087-5db9-84bb-2b399b318c99 | button | Acceptance | Yes,No,N/A
594d641b-f31f-53d2-9650-4887a27fdc83 | note | Key - H
72732447-ad9c-5613-9abc-7a3344f4ea3f | note | MDR/VIVA - H
fe18d6be-516e-55cd-8164-bbfd7b7fb75d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
71a52ff0-e8af-5f42-b8a2-e22fbdf19b9d | tickbox | Test Pack
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4.2 - Hydrostatic Testing
377786da-0344-56ed-ae85-34d86deb3eff | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 13.2
3f8e3e78-d038-5d16-8891-a41a6d3be94d | note | ○ SUN_ENG_P RO_010 R0 GRE Hydrotesting procedure
175a3580-8587-54d9-b551-621f8f9fac8c | note | Acceptance criteria - Has the pipework been tested as per the manufacturer’s specification for the required duration?
ad4363f6-0a97-58ab-8bb3-b84209370b72 | note | Integrity Test
4d8896da-f11c-5d62-b634-f9b2deb7288a | note | ○ 2-hour test –1.5 x design pressure for 2 hour hold (Refer to Hold Point in Subcontactor ITP below). Visual Inspection required of joints upon completion.
6572c86f-e9b9-542a-992e-5072b69ab849 | note | Leak Test
f860c02e-2245-53ce-bb0f-17bd2c97f9f6 | note | ○ 1.1x design pressure.
189b96c2-4484-5e24-a500-0822a6c0c2a6 | tickbox | 2-hour test – Visual Inspection required of joints upon completion to verify no leaks.
99b677ce-3a69-5618-9cb3-8d950b6accad | note | ○ Has the pipework passed the testing requirements with no leaks?
3c19647f-14c1-54e8-8424-e903ef5c1f99 | note | ○ If no, proceed to item 4.2.
e2e2f63b-f74b-5a15-9eee-308e9e06edd7 | button | Acceptance | Yes,No,N/A
6f821ff9-9060-5765-ab6f-560a9fba9052 | note | Key - H
6e86834a-8065-5c43-a7d6-05be3b28e5df | note | MDR/VIVA - H
316e3ad5-587e-59f0-ab2e-d6e82b29dad5 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
b9d2fc37-606a-5c5b-905a-abc5b048c9b7 | tickbox | QF-129-01 – Hydrostatic Test Log Sheet
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4.3 - Repair
76ebf9bc-9f0c-5353-97b6-81e62e150b3d | note | Ref docs - SUN_ENG_P RO_012 Re-condition of Adhesive Bonding Socket - Joint repair
4982ab20-9b71-511e-9fcf-8bfa8f129a95 | note | Acceptance criteria - Has the leak been identified?
ddb97047-c6f4-5989-b4e6-6d4ad2e63cf4 | note | ○ Has the leak been repaired as per the manufacturer’s specification/approved methodology?
ab4bcf9b-2a34-5864-9dda-0b49b0a58063 | note | ○ Has the pipework passed subsequent testing requirements?
bc56fd7c-f5fc-5a1c-a2ad-8f6169dc4193 | button | Acceptance | Yes,No,N/A
47ba2257-e7b2-55d3-9318-726f18079f40 | note | Key - H
a4976d72-cb61-5eb1-bda6-83420e623f3b | note | MDR/VIVA - H
| signoff | AUTHORITY HOLDPOINT
| section | 5.0 Backfill
| checkpoint | 5.1 - Sand Backfill
c73ab87a-ddf7-53c1-9bcd-9b7a6328c7f7 | note | Ref docs - 239529-MG1668-15740-0400-SD-000010-NOV Bondstrand pipe installation guide - GRE
37bd37a6-3cca-5f49-9e40-8152b6cd09fb | note | Acceptance criteria - Has Sand Back fill been placed to 300mm above Pipe?
52c71583-3096-5df8-968a-cd4929f34c93 | note | ○ No compaction equipment to be used until 300mm above pipe.
cf90d740-9af1-5b79-8f95-37f85efb4662 | button | Acceptance | Yes,No,N/A
73ab7897-12ca-5d7a-9e13-1e3cc0df075e | note | Key - S
4a6cc8a8-0e9a-5bad-92e6-94065a7f614e | note | MDR/VIVA - S
| checkpoint | 5.2 - Select Fill Backfill
e91066dc-0e6c-5b32-8276-c12854580abc | note | Ref docs - 239529- MG1668-15740-0400-SD-000010-NOV Bondstrand pipe installation guide - GRE
5a994ac1-8485-565a-af1e-6dee59842d6e | note | ○ 235929-000- CV-SP- 00002 – Earthworks
425834b3-f996-5194-b8ff-7a9e2c56ffbe | note | Acceptance criteria - Has select backfill been placed in layers not exceeding 150mm loose thickness?
1206039d-ad40-50fe-82eb-dacb2d265088 | note | ○ No compaction equipment has been used between 0-300mm above top of pipe, light compaction equipment has only been used from 300-600mm above pipe.
8cf2ea21-09f4-5b4d-888e-b8681c961a36 | button | Acceptance | Yes,No,N/A
| checkpoint | 5.3 - Compaction Testing
b8c3c111-55dd-5f8b-b0bf-9c40019ff2c1 | note | Ref docs - 235929-000- CV-SP- 00002 – Specification for Earthworks
cce24e23-ed0f-543e-8737-69745b54ced2 | note | Acceptance criteria - Sand Fill - not less than 90% of maximum density or 70% of relative density, except that under paved areas the entire depth shall be compacted in 150mm layers to not less than 95% of maximum density or 80% relative density
f05cbe95-f09e-501a-9b58-cab4516c9116 | note | ○ Select Fill - Backfill under pavements shall be compacted to a dry density ratio of no less than 98% modified comp active effort.
979d99c5-d0c6-57df-9e61-69b0d4ceaa25 | note | ○ Testing Frequency: Minimum 2 field density tests for each 185 m2 of each compacted fill layer, but no less than 3 tests for total area
2d893ed4-9f1a-558e-b36c-d9c3abd5c61b | button | Acceptance | Yes,No,N/A
a9038a37-5466-5ad8-9d01-42daedc1b920 | note | Key - W
97e07f3c-cad4-5768-a95a-4170bd1b5a21 | note | MDR/VIVA - S
6b97d6dd-7c8d-503d-85a4-ede8245822e7 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e623dfe5-be91-5fff-ab70-3b9655ae2815 | tickbox | Geotechnical Test Report
| section | 5.0 Documentation Submission
| checkpoint | 5.1 - Subcontractor ITP
4fbaa0db-e332-57d3-b0f9-d61e4069d772 | note | Acceptance criteria - Has the subcontractor ITP been signed off and accepted by relevant parties?
f2826119-88c4-5752-87e8-e9589ef4dcac | button | Acceptance | Yes,No,N/A
4a5daf6f-e66f-596a-866d-7e3d078b8bd0 | note | Key - W
23ffdd2c-1a5c-500c-9d7e-bb535b963b4e | note | MDR/VIVA - W
0e078a37-2b29-5edb-bc64-6eec0d5b6636 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
5f7bb4d0-975c-5f3b-b789-fe4f6a6012fe | tickbox | ITP_SUN_23_ 003
| checklist | INF-HSEQ CC0398-ITP-033 HDPE Installation Rev C | itp | INF-HSEQ CC0398-ITP-033 HDPE Installation Rev C |  | 8b6fa8ca-e145-4ec9-bf05-10b77b725a76
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Set out
a6292148-9ef9-576b-876a-6a3228c3a892 | note | Ref docs - Isometric Drawings
30d49bf9-bf87-555a-9142-cfb638dd1a3d | note | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
777af535-d73e-522d-bad5-d1342c920d44 | note | ○ IFC and latest available revision used?
baaa4dce-60f0-5bda-bb77-1d18b5fbbbcb | button | Acceptance | Yes,No,N/A
69525a4b-a83f-5dba-96ec-4dd2ce98e8d5 | note | Key - H
75fc77d5-10df-514f-9046-8ff43be314e6 | note | MDR/VIVA - W
| checkpoint | 1.2 - IFC Submission & Approval
dec92c87-4a17-5301-85e3-96ad48b33c3a | note | Ref docs - Isometric Drawings
aa5aff82-7327-5e54-b1ee-405d91f53eb3 | note | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
5ea8d45b-c757-5bcd-867e-9e31a28d2dfc | button | Acceptance | Yes,No,N/A
10aa048a-4a2b-5e36-8120-c71c41325150 | note | Key - H
8b1beac1-ee1f-50da-b3a5-c32620ad7149 | note | MDR/VIVA - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.3 - Permits
75044550-e011-5827-934e-1047e5295b04 | note | Ref docs - Symal Safety Procedure
2f53dfb8-b636-5870-a70c-ddaa2e203e1f | note | Acceptance criteria - Have the below permits been created.
ee7b79b7-a422-58c3-ae16-3b4825f0da40 | note | – GPP
cbd7de83-1cfa-588c-925b-50faef882311 | note | – Working at Heights
c565a92e-678e-50c4-9a80-77ba93f14ced | note | – Hot Works
37da19c8-f2c7-5560-8e2e-85056d504ae6 | note | – Confined Space
2e83ef1d-c52e-57ac-9753-61d3bb87797d | button | Acceptance | Yes,No,N/A
998714d0-37b6-5647-9e40-20ece287f20f | note | Key - H
c72ad560-228d-5162-974b-ed1b850f30c6 | note | MDR/VIVA - W
| checkpoint | 1.4 - Determine Lot Size
95bc59c1-84dc-5ac5-b099-f966678d4f4b | note | Acceptance criteria - What is the lot size?
ca144e43-02b3-51ff-b28a-0a6b2f95dd4a | button | Acceptance | Yes,No,N/A
fb350a70-f360-5d3c-b8b8-9679832e847c | note | Key - S
8ffc48aa-2647-5c8b-ad40-bd4bfd8d7523 | note | MDR/VIVA - W
| checkpoint | 1.5 - Free Issue Materials
8cb1dd15-6c3a-538d-afa5-365a76ed69ec | note | Acceptance criteria - Have the free issue materials been accepted and checklist completed?
c317e274-bbb9-577f-86dc-67da2bc6e603 | note | ○ Have the materials and tag numbers/heat numbers been verified?
f9c138c1-88ab-50f2-a936-d57f53842991 | button | Acceptance | Yes,No,N/A
093b0a88-d19a-59b6-adf4-5bf09988dfce | note | Key - W
9bb19453-1ccf-564b-94f3-4cf0fc2c8209 | note | MDR/VIVA - W
67fcb396-d200-5540-ac10-f27f98454743 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
8ad617d5-1986-5509-84f0-9f17579cffd3 | tickbox | Material Inspection Checklist
| checkpoint | 1.6 - Welding Pre-Qualification
2bf4c607-8896-58fd-acaa-5801629b057c | note | Ref docs - Welder Qualifications and tickets. This ITP.
5fea360f-1e5a-5a47-ac70-0b5be4cc8390 | note | Acceptance criteria - Welding procedures, equipment to be used, welding qualifications and calibration of welding machines to be submitted and approved by the client, has this been completed?
ac4d6a55-642e-53ff-82bf-cb39707a4b99 | button | Acceptance | Yes,No,N/A
747ef420-5030-5a42-bd0e-516be4110254 | note | Key - H
17c5f370-36aa-56b8-99ea-d2c2feb6836c | note | MDR/VIVA - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.7 - Bedding and Backfill Materials Approval
c0a6fb32-ddb1-5920-a2b1-f3516f94df7b | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8
4809543e-a02c-554b-89b6-6acf92f3d9d2 | note | Acceptance criteria - Has bedding and backfill materials been approved for use?
84aa6386-810f-5d2d-9bb1-87e4326e754d | button | Acceptance | Yes,No,N/A
08f5bcb6-89d6-59ce-b4c7-8a1a27b30d97 | note | Key - H
2fbac27b-b6a9-5d80-adcf-37f5b7c5bcc9 | note | MDR/VIVA - H
| signoff | AUTHORITY HOLDPOINT
| section | 2.0 Excavation and bedding
| checkpoint | 2.1 - Service Location
5dd1271f-23b8-57bf-b446-9814b79b0d35 | note | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
d6f50350-0a38-56fa-8ba9-2f88f5bc559a | note | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
50020be2-4d60-5d34-af90-12534be4650a | button | Acceptance | Yes,No,N/A
06e33099-3b99-5515-b2ff-33bc3bde8db8 | note | Key - H
8b080e68-d17c-585e-b428-a14b0b5581ba | note | MDR/VIVA - S
| checkpoint | 2.2 - Excavation
801990cc-3d8f-59f9-b825-f3869fc6a830 | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.12
f09d4ed9-97f1-5213-8001-c610012d5571 | note | Acceptance criteria - Excavation shall be to depth adequate to provide full specified bedding depth of 100mm.
80567725-2c70-564e-aa8b-74b8e8aeff10 | note | ○ Minimum trench width as per manufacture specifications pg. 17 is 1.25 x OD + 300mm.
2027e1e2-2bd3-50c6-a6ba-07fc74ba4ef1 | note | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
febf78d5-0a75-5b94-9d54-5db964304530 | button | Acceptance | Yes,No,N/A
d972d095-782b-5e8d-98c3-b8c23a12ae2a | note | Key - W
67b8223a-7f02-56a3-8264-df70c1327889 | note | MDR/VIVA - S
| checkpoint | 2.3 - Bedding material
b7189e56-3b2b-5ee4-b19b-14767440222f | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8
095e3a5d-62ff-5ad4-90b6-0e52cf25ea14 | note | Acceptance criteria - Has the bedding material been installed as per the manufacturer’s specification?
d80a253f-5c86-56bd-8687-46da61181271 | note | ○ Conforms IFC drawing (if applicable)? Bedding depth minimum 100mm Overlay depth minimum 300mm.
8119dad3-bb9b-5890-bb41-bc909f1a03f4 | button | Acceptance | Yes,No,N/A
11eaa216-7440-5906-83fe-91890f345c6e | note | Key - S
c3d230db-b83b-51d3-84bf-0d5de65b2fef | note | MDR/VIVA - S
353e2ab0-a278-5b21-8afb-d3ccabcea2b4 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
97102a25-7ae9-5a93-867e-2d4d0b33cfd0 | tickbox | Delivery Dockets
| section | 3.0 Welding, Laying & Backfill
| checkpoint | 3.1 - Above ground fabrication
13e70ec3-9f05-5cde-8787-47f36f06e782 | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL, PIPA- POP014- Assessment- of- Polyethylene- Welds-Issue- 1.1 ISO-21307 PWS-WP-01 Butt Fusion Procedure
044f2efa-8f96-553e-9ae2-b8a6e36e076f | note | Acceptance criteria - Have the lengths been welded as per the manufacturers spec and welding duration?
792d69d2-a93a-5a76-9305-88d79ed00a0c | note | ○ Has the welding procedure in the reference documents been adhered to?
f1c179ac-91ca-5acf-951d-01e92be43848 | button | Acceptance | Yes,No,N/A
8e2ac93d-dc16-5e31-a1e9-d8fd817a46cc | note | Key - W
507a1234-5cb6-5d1a-8d8d-f5949b4e5bef | note | MDR/VIVA - S
36a93b90-1638-597b-86c6-d05d48b7ac6a | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
5ad5572a-0763-54d9-a4ab-27d014293ad5 | tickbox | Welding Checklist
| checkpoint | 3.2 - Lifting into trench
927b8a00-fbf3-5eaf-8885-bb34f958d942 | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.2.1 Item 12.2.7
a3d8b46d-b20b-5512-bdc8-f12156f44842 | note | Acceptance criteria - Before lowering in, caps shall be placed on open ends, flanges, etc., which shall remain in place until piping connection can be made. Particular attention shall be given to the need to protect pipes from damage due to loads from heavy plant, has this been completed?
1accccc6-7ea0-50fb-b458-153b63e6841d | note | ○ Have pipes been laid to true line and level?
904741bc-6a1b-5318-af63-3f471fa507d1 | note | ○ Has MDR been notified before the laying of pipework?
d62cec42-0de8-580f-8d6e-50d469b4018a | button | Acceptance | Yes,No,N/A
7cbbe5ca-33e6-5f19-9957-212222bd1bfe | note | Key - W
1126f779-e6bb-5990-b1bd-d8f7684f6c79 | note | MDR/VIVA - S
c12b6519-cf09-56eb-b367-95b785ecbf11 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
3f7fe797-bc43-5e76-81a0-e7ca1039ce51 | tickbox | Survey compliance report
| checkpoint | 3.3 - In ground fabrication
591ddb6f-e93f-54de-9eb3-179ff7d1a52a | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL, PIPA- POP014- Assessment- of- Polyethylene-Welds-Issue- 1.1 ISO-21307
5f0e4d86-1969-5f27-b671-9a7f2192165e | note | Acceptance criteria - Are the EF couplings if required sitting outside of the ground of the trench as to ensure that water can’t enter the coupling?
961276a7-50dd-5f15-a812-dc9bfae1be38 | note | ○ Have the welds been welded for the appropriate amount time?
aec4b034-ff4d-5531-b124-4d9ae48281d8 | button | Acceptance | Yes,No,N/A
4917ec55-1396-50d4-b79b-c308a73ae303 | note | Key - W
acf00bce-1e19-5184-8822-0554dcfeb02f | note | MDR/VIVA - S
865341f0-4693-5d82-99c3-504049e0f458 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
dffaebd4-3d7e-5581-9774-0ad92cc3322a | tickbox | Welding Checklist
| checkpoint | 3.4 - Haunching
3ddf224c-a27c-5800-87ea-107b764ab78f | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
1796658e-948c-5f28-ae59-df5a5cab6238 | note | Acceptance criteria - Has the backfill material shall be approved soil without large stones, organic matter or substances which may cause damage to the piping?
e72688b0-3e7e-56d7-9d8f-160c3606b1b0 | button | Acceptance | Yes,No,N/A
28735f09-b4b7-5cef-afbe-615496c8ff64 | note | Key - W
e6087daf-51f2-55b6-9831-1d9f03c015f9 | note | MDR/VIVA - S
| checkpoint | 3.5 - Back fill
1ea0ec76-0e8f-5779-a9a2-a9e0af7424d8 | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
7003f0aa-cc27-5e8d-ae29-195677c96071 | note | Acceptance criteria - Has Sand Back fill been placed to 300mm above Pipe?
6337ae5d-cea5-55fb-9853-88883afdcbdc | note | ○ No compaction equipment to be used until 300mm above pipe.
24fce5f4-70c5-5b13-9fc6-35346599ae9e | note | ○ Has select backfill been placed in layers not exceeding 150mm loose thickness?
624262a4-c8ca-518b-aff9-32bdd7f9493b | note | ○ No compaction equipment has been used between 0-300mm above top of pipe, light compaction equipment has only been used from 300-600mm. above pipe.
6a27772f-bfdd-55fe-a79c-e24ba8224043 | note | ○ Note: Backfill around joints/welds can not commence until testing has been completed.
f50ffb4f-d297-55bb-9c9a-9a35d82bdea7 | button | Acceptance | Yes,No,N/A
cfe7c527-e468-553a-a1ed-7cf28ad659f2 | note | Key - W
93fa47ff-08a9-5940-a3d3-1c3853e81de4 | note | MDR/VIVA - S
| checkpoint | 3.6 - Compaction
4b82d837-137c-5c1b-8ea3-f83f1e287d12 | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
01d655e2-7d8e-5d74-af47-858ce5275e08 | note | Acceptance criteria - Sand Fill - not less than 90% of maximum density or 70% of relative density, except that under paved areas the entire depth shall be compacted in 150mm layers to not less than 95% of maximum density or 80% relative density.
1ca12511-58cc-521d-ae03-fb70045a30d3 | note | ○ Select Fill - Backfill under pavements shall be compacted to a dry density ratio of no less than 98% modified comp active effort.
8e8b0f3f-eb4c-5053-8da5-079bb7499378 | note | ○ Backfill to be in 250mm compacted layers.
7d7135b6-8e3b-5d78-9b8e-44820056eb82 | note | ○ Testing Frequency: Minimum 2 field density tests for each 185 m2 of each compacted fill layer, but no less than 3 tests for total area
469f0599-3475-5556-adcc-0d41e3ac84ec | note | ○ Has compaction testing been completed as per the project specifications?
8b69cb19-e15c-583b-8722-4517438d0306 | button | Acceptance | Yes,No,N/A
33039fd4-02dd-55c0-84d1-ea9e3da26f3e | note | Key - W
2c3a4d13-0a05-5970-957e-f8008aa9535f | note | MDR/VIVA - S
| section | 4.0 Testing and Conformance Check
| checkpoint | 4.1 - Test Pack
30824e05-debf-5e60-938c-814660902142 | note | Acceptance criteria - Has a test pack been provided prior to testing? Test pack to include.
62d6e9c7-7edd-5e39-91d1-fc5adfaf7bbd | note | – Test Procedure
51ff042f-0a29-516b-bcf6-a1bea87e067b | note | – Test Map
e16b36d9-23da-57f4-b0ff-0d4f1b56fdfb | note | – Equipment Calibration
6effca6d-f44b-5dbe-9d15-f98a2b356981 | note | – Equipment Details
dbf4d63d-2f04-535b-a028-9bc3d3cfcb1d | note | – Exclusion zones if require
9bc90446-ae4b-5fb9-beee-22a23970a7e4 | note | – Provision of testing log template
6d862293-e7f6-5770-a4d7-0069725300db | button | Acceptance | Yes,No,N/A
89b277c1-8107-565a-ba0b-69e78baaf697 | note | Key - H
d17ac13b-2345-53a7-a6c1-d2f221e03e52 | note | MDR/VIVA - H
d15978e7-8139-5df6-b186-a2bac1948c7a | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
d383484b-be8b-5400-92e7-03dd49eebfbe | tickbox | Testing Log
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4.2 - Hydrostatic Testing
44710851-cffb-5d14-b9b0-9f29ef3f9e3e | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 13.2
a0485ed1-30e6-5734-a709-df1f41ee1dec | note | Acceptance criteria - Is the line a Pressurised Line? If yes refer to the below.
cd84b084-1c51-53dc-a0bc-234165d27e48 | note | ○ Testing Equipment is calibrated within 12 months from a NATA certified laboratory.
c13307b6-59ef-53cf-a12f-1fe3d3302085 | note | ○ Has the pipework been tested at 30 bar for 2 hours specification for the required duration?
cddb09b1-3ca7-5c99-9025-8292c5b3b681 | button | Acceptance | Yes,No,N/A
dee9065c-451b-5918-b7e7-d0792a06db39 | note | Key - H
d835d3d0-1167-557e-a89a-e92057801461 | note | MDR/VIVA - H
2cec035e-ae1d-53a1-9fdc-f8b46d6c7947 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
3882ad51-6729-5921-8f45-c9c2c398b6cd | tickbox | Testing Log
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4.3 - Leak Testing or Air Testing
4d4ac72e-dda0-5242-b72a-66a2238ec2d2 | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 13.3
c5387118-571d-5b2d-a99d-0fc7c603d618 | note | Acceptance criteria - Is the line an atmospheric line?
ca083e23-c85d-5562-9304-d449080f6ab5 | note | ○ Atmospheric lines to be “full of liquid” tested shall be filled with water for at least 24 hours before visible inspection of the complete test system by the inspection team, water level in the test system shall be checked and marked at the start of the test and rechecked after twenty-four (24) hours during visible inspection of the system.
9720ce4f-c3d2-50a7-9155-574a990d5c9a | note | ○ Concrete Sumps or other material that will absorb water shall remain full of water for minimum 24 hours prior to test running.
8a741547-20b9-5e48-b7ea-be6cb58c834c | note | ○ Note: Losses from seepage / absorption may not be higher than 0.5 l/m2 of wet surface during the first 6 hours.
a0d3eeb5-9464-5c4a-81ce-d4e148a8a63b | button | Acceptance | Yes,No,N/A
5a65c9ee-2f8d-5b51-837f-828fca8a9b5c | note | Key - H
dbb88179-0c43-5119-81e0-77392dc1454c | note | MDR/VIVA - H
6071cc12-29eb-5d08-bd83-2fae1dcead4c | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
0c34a150-6216-5fc9-ac47-a2eeb5f80264 | tickbox | Testing Log
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4.4 - Survey
e8246ccc-f6f9-580e-b9f1-83dfbe7d7a96 | note | Acceptance criteria - Tolerances in alignments shall be limited to +/- 25 mm vertically or horizontally, unless otherwise specified on engineering drawing, has this been completed?
c10007d5-d281-5d23-82a4-f7d2ef418539 | note | ○ As-built Drawings
13ad40cf-4054-5ba2-b867-0b78ff1c4537 | button | Acceptance | Yes,No,N/A
128a51a3-a63d-5f41-84f6-a12fff51e13d | note | Key - W
12730de3-ec15-50db-84cc-7a9ea9a6e5d2 | note | MDR/VIVA - W
335ce6f0-7253-5aa0-a55c-88937ee10211 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) - As-built Survey
| checklist | INF-HSEQ CC0398-ITP-034 Carbon Steel Installation Rev C | itp | INF-HSEQ CC0398-ITP-034 Carbon Steel Installation Rev C |  | 0946edd3-a462-4b17-a35e-b93e00dd186c
| section | 1.0 Pre-start activities
| checkpoint | 1.1 - Set out
414ca677-dc92-58d0-8b6d-25074380cd86 | note | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
1e2ef3ea-f6a8-531f-b12f-58efd3c434d5 | note | ○ IFC and latest available revision used?
5f14acec-88b0-5d7a-ad1a-cd44288832a7 | button | Acceptance | Yes,No,N/A
16ecb757-55b7-5e4f-a7dc-a2b6601206bd | note | Key - H
5c47a2ea-5776-50ca-ac36-feb0fab7248e | note | MDR/VIVA - W
| checkpoint | 1.2 - IFC Submission & Approval
3b4e695d-bb66-5bc4-9c4f-76b2e9aceb2a | note | Ref docs - Isometric Drawings
d92a8349-488c-5728-a859-737604a1a4bd | note | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
47b3f934-2fce-589c-a321-1bd30d422a24 | button | Acceptance | Yes,No,N/A
2d5f3756-105e-5cc6-a04d-65955528ff38 | note | Key - H
37b36da5-8481-59c5-bcd0-ced661fbc836 | note | MDR/VIVA - H
06278bb9-6755-540b-a1cd-69e8a02e8eab | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
1df0313b-8e97-5cda-aa7d-dd753dc8e818 | tickbox | Isometric Drawings
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.3 - Permits
7936c0ad-2d5c-509e-ba01-2f8f0ca221d2 | note | Ref docs - Symal Safety Procedure
0dc3dc10-f277-5090-82d8-5505316dc9ad | note | Acceptance criteria - Have the below permits been created.
f17ee10d-469f-528c-8b0a-15959d768ee2 | note | – GPP
593b9fae-8bea-5c7c-b0e5-5f56e84bc4b7 | note | – Working at Heights
43cd8f0f-575b-5ebc-b046-523b9c3dfb9a | note | – Hot Works
5265ebf6-c143-568d-b0e4-b653298bc4e8 | note | – Confined Space
009b61af-dfa8-58cf-aee9-907ff4511d55 | button | Acceptance | Yes,No,N/A
0ddd6ddd-71df-5c93-b3e4-fb161cf4163c | note | Key - H
42cdd9ef-16af-59a2-91c3-58162cfa4145 | note | MDR/VIVA - W
| checkpoint | 1.4 - Determine Lot Size
8d580e88-f213-5a83-9c25-e878b3a3ecdb | note | Acceptance criteria - What is the lot size?
b2635b00-fa87-5f32-b51b-0955337b3c43 | button | Acceptance | Yes,No,N/A
b114c22d-ce82-5cc6-8c35-fcd9bbaacc23 | note | Key - S
b20974c2-4c8e-57c4-acb7-7093e920e3b0 | note | MDR/VIVA - W
| checkpoint | 1.5 - Free Issue Materials
61365588-4fa3-55c3-83ff-7be96fdd6040 | note | Acceptance criteria - Have the free issue materials been accepted and checklist completed?
84370636-cfd5-577b-8b68-2c04928fde6f | note | ○ Have the materials and tag numbers/heat numbers been verified?
cebcc50b-7962-586f-8613-bafd7c2ae07e | button | Acceptance | Yes,No,N/A
6dea74d1-3f74-5db2-99d8-d8069da0923e | note | Key - W
15f73246-c7a6-5ae1-ab4d-69c0090a7078 | note | MDR/VIVA - W
d2349358-c3a2-586f-b996-984c3129b247 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
4ad592f7-af52-5f72-86a6-2a814d860d57 | tickbox | Material Inspection Checklist
| checkpoint | 1.6 - Pre-Qualifications
e4a2eb2e-3ee1-531e-98de-f92479ec8754 | note | Ref docs - Welder Qualifications and tickets. This ITP.
dfa5cf95-b0cc-5e8a-bcba-c2c4c8f19697 | note | Acceptance criteria - Welding procedures, equipment to be used, welding qualifications and calibration of welding machines to be submitted and approved by the client, has this been completed?
9cea0a23-05d6-5f97-bb4f-d953ffa09553 | note | ○ Has the training records for the STOPAQ applicators been provided?
4418465e-9792-5c41-884c-fcc6d513c7a4 | button | Acceptance | Yes,No,N/A
94b70614-6f97-5ca0-bc2c-966afde6bb09 | note | Key - H
3fe58905-8b27-504d-977d-245c3706cca7 | note | MDR/VIVA - H
c276e91a-a0d0-5db8-b60e-612fd5967851 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
86328624-91f6-57d5-9ade-754e4f779150 | tickbox | Welding Qualificaitons
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.7 - Bedding and Backfill Materials Approval
cbdfb958-dd63-5bbb-ad42-623add996c2c | note | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8
4a72b740-9a92-5eaa-9dea-d2c053027ea2 | note | Acceptance criteria - Has bedding and backfill materials been approved for use?
82c0636c-a445-510c-a12f-23eac6f67703 | button | Acceptance | Yes,No,N/A
685c1b5a-9669-5c09-bde3-0f59201453f1 | note | Key - H
f17c64bd-c35b-5e18-b6ab-35d44e4e6e52 | note | MDR/VIVA - H
9340c59b-7e72-55c4-934f-7d3d5d760d61 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d028a8f1-0e4d-55a6-a54f-8539f1ad3340 | tickbox | Material Approval
| signoff | AUTHORITY HOLDPOINT
| section | 2.0 Excavation and bedding
| checkpoint | 2.1 - Service Location
73088be7-9e4b-5d8d-913c-f005b2e8a72c | note | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
da79b004-3b69-5776-a9ba-11a315cf8003 | note | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
415f0258-e2f7-57e4-b5fc-39de63ca7d79 | button | Acceptance | Yes,No,N/A
d11e7058-eae5-50fe-90a9-32bb9ab1be6b | note | Key - H
793ef610-f807-5502-a51d-2d542ac76380 | note | MDR/VIVA - S
| checkpoint | 2.2 - Excavation
1b93e24e-9721-58a1-b702-d3a3b96281b6 | note | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.12
c6402caf-0bd5-580e-ad19-2f02aacfee4f | note | Acceptance criteria - Excavation shall be to depth adequate to provide full specified bedding depth of 100mm.
989b3354-6823-598a-bd87-4d6002810f6f | note | ○ Minimum trench width as per manufacture specifications pg. 17 is 1.25 x OD + 300mm.
119ea929-0e68-5f4d-b474-dd2fd9ce3214 | note | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
2ab8db07-350c-5dff-8497-7f0c1be497fb | button | Acceptance | Yes,No,N/A
6a1413ac-6120-5100-8550-832c95614525 | note | Key - W
d4c4b22a-b179-5068-9d11-8f60d9251fd2 | note | MDR/VIVA - S
| checkpoint | 2.3 - Bedding material
ed1636d4-42e0-588b-9b25-cd915270aaa9 | note | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8
853a0b42-6f02-5aac-8fb1-5439b7eeb979 | note | Acceptance criteria - Has the bedding material been installed as per the manufacturer’s specification?
dc7d98e8-fd2b-5483-a1c5-bfd0792cf623 | note | ○ Conforms IFC drawing (if applicable)? Bedding depth minimum 100mm Overlay depth minimum 300mm.
840003cc-e635-5701-a143-c835b3aac9f2 | button | Acceptance | Yes,No,N/A
ebcb7ddc-4804-5539-b326-c53253a4bba5 | note | Key - S
d56cc03a-9fe4-5729-9ce1-aac9f390b806 | note | MDR/VIVA - S
3545a6a2-2a82-5543-b705-d67b4c14d4c6 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
40a493fd-fc73-56ff-b76a-11c82c4aca50 | tickbox | Delivery Dockets
| section | 3.0 Fabrication
| checkpoint | 3.1 - Welding
c294a51d-6f54-5130-90f6-eb670c14e7e4 | note | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL, 235929-RE-ENG-INT-0003-WIITP – P11U, 235929-RE-ENG-INT-0003-WIITP – P11P RE-ENG-INT- 0072-PR
465ee7ce-78b9-5f9b-a628-3ba97cc5a5aa | note | Acceptance criteria - Have the lengths been welded as per the manufacturers spec and welding duration?
809ff6b1-6d07-56ad-b118-fd4277e06e74 | button | Acceptance | Yes,No,N/A
3fbd0f91-d6ce-5bb4-98fe-7e484c7bf8e7 | note | Key - H
dab1c000-e60f-5d7d-8e8c-c8dbab41a417 | note | MDR/VIVA - W
c2164181-e3e5-5cf8-bf5a-043ea46d69f0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ec7e59e8-fd34-5653-88cf-ec8e46ce3bd9 | tickbox | Carbon Steel Subcontractors ITP
cfaeccec-037c-5a5a-ac7a-ecbd12b7947e | tickbox | Welding Log
| checkpoint | 3.2 - Non-Destructive Testing
486a2b0c-a70a-5d36-bb12-7e04d0c41229 | note | Ref docs - 235929-RE-ENG-INT-0003-WI, 235929-RE-ENG-INT-0003-WIITP – P11U, 235929-RE-ENG-INT-0003-WIITP – P11P
a7a61130-a36d-576a-8592-aa416af83f9d | note | Acceptance criteria - Have the welds been tested as per the ITP’s referenced in the isometric drawings?
b443529e-8a04-58bb-b5a5-d1f82d910efa | button | Acceptance | Yes,No,N/A
1120661a-67c7-54c2-b686-9022051c9962 | note | Key - H
ff5dff05-a015-5c5d-a941-629f4aece781 | note | MDR/VIVA - W
7d3ff64f-f547-59cc-a508-2fcc22ba5410 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e545d2cf-966b-5866-a54d-54122c96ea11 | tickbox | Carbon Steel Subcontractors ITP
| checkpoint | 3.3 - Coating and wrapping
8bf95acc-370c-5182-864a-b7c36a80070d | note | Ref docs - 235929-RE-ENG-INT-0003-WI, 235929-RE-ENG-INT-0003-WIITP – P11U, 235929-RE- ENG-INT-0003-WITP – P11P, Isometric Drawings, RE-ENG-INT-0045-PR
82ba2df6-08c4-5cca-b807-35c31573ac31 | note | Acceptance criteria - Has the application procedure been provided to MDR and approved?
b92bc546-f68e-511c-9f11-77f51a78aca1 | note | ○ Have the welds been wrapped as per the drawings and specification?
e08cbf14-f7b7-5978-9ac7-2e0598e6fdb2 | button | Acceptance | Yes,No,N/A
cddb41ac-92a2-57fa-a381-c5ac971b34c7 | note | Key - H
4bfcee3d-db0b-5ca0-b7a3-b7f5a751462b | note | MDR/VIVA - W
27da277a-a01f-5702-aad1-b809ff1e741a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d34aa907-7af7-536a-802d-404894677a4a | tickbox | Carbon Steel Subcontractors ITP
| section | 4.0 Laying
| checkpoint | 4.1 - Lifting into trench
3020b60f-2a20-52ee-8482-ba2733929e5f | note | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL Section 12.2.1 Item 12.2.7
0ebca3e8-b4e0-5995-a6dc-b31d69c47550 | note | Acceptance criteria - Before lowering in, caps shall be placed on open ends, flanges, etc., which shall remain in place until piping connection can be made. Particular attention shall be given to the need to protect pipes from damage due to loads from heavy plant, has this been completed?
6107e8d1-45af-579a-98d2-b28b7b303cdb | note | ○ Have pipes been laid to true line and level?
cc886c0c-d974-50a1-88f1-4a4bbbc407ca | button | Acceptance | Yes,No,N/A
2e9f9d7e-1632-5758-96ac-4976acbb047d | note | Key - H
48bee62c-eb6b-56d7-a4ba-a3141c69c12a | note | MDR/VIVA - S
| checkpoint | 4.2 - Haunching
853ff899-9390-5b9c-9d97-19b9c9c8f666 | note | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL
5bb92813-67f3-56b6-b3a8-bf427cb12253 | note | Acceptance criteria - Has the backfill material been haunched appropriately around the pipe?
96cf41b5-b226-5b5c-b787-6ed21b678413 | button | Acceptance | Yes,No,N/A
7b8372d3-6171-5afb-8ba0-0da9215f819e | note | Key - W
0d6435e9-4738-5e3a-96b6-c2cf33abce91 | note | MDR/VIVA - S
| checkpoint | 4.3 - Pressure Testing
715e27fa-ff5a-5bd5-a1f3-4f5de9d2724b | note | Ref docs - 235929-000-CV-SP-00006 Section 13.4
d4829924-eecb-546f-8b28-2e9f3be92144 | note | Acceptance criteria - Is Air Testing or Hydrostating testing being completed?
f0575c3c-2da0-5ade-a2dd-94b4afce478a | tickbox | Air Testing
af80b008-f334-552a-84bf-6ca854c2deee | tickbox | Hydrostatic Testing
5dc71d95-776c-5c33-9c70-f9e119557e77 | textbox | What is the test pressure?
1dc7d2d9-f2e3-5445-831e-cf9e26916495 | note | ○ Has Testing been conducted to all joints and inspected to confirm no leaks?
27fa593f-fe4d-5e25-87c1-edc660c550a2 | button | Acceptance | Yes,No,N/A
bff961a8-4f9e-5f1f-88f6-592b49071a48 | note | Key - H
be926e3f-3800-5ce5-b1d6-70e95496f49c | note | MDR/VIVA - W
71d2ce08-9026-5fc9-8332-3765b7ba9488 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ed5904ef-587c-5458-b14f-cb7361161eae | tickbox | Testing checklist
| checkpoint | 4.4 - Backfill Materials
be659b9e-7c0b-5f8f-a4f7-4c7627e2bd79 | note | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL
0959da6b-0395-57e0-9d97-777ab07a1d6a | note | Acceptance criteria - Has Sand Back fill been placed to 300mm above Pipe?
ccd55caf-a398-5f89-8484-eba78cac6eac | note | ○ No compaction equipment to be used until 300mm above pipe.
ff5fcc12-b943-551e-8573-9939e1da334c | note | ○ Has select backfill been placed in layers not exceeding 150mm loose thickness?
66b5b3ce-ca1d-5e48-9c8b-2d8b27123528 | note | ○ No compaction equipment has been used between 0-300mm above top of pipe, light compaction equipment has only been used from 300-600mm. above pipe.
ffb66a1f-570b-5f80-9c7e-751caf0c1935 | button | Acceptance | Yes,No,N/A
83a8d920-af65-5333-b1d8-ac5849cef5c6 | note | Key - W
22c456ff-938b-5283-b10d-c6a1817a0241 | note | MDR/VIVA - S
| checkpoint | 4.5 - Backfill and Compaction
5d1da675-3610-5f40-beb3-a1261a4d17c4 | note | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL
57f84272-9aa3-550e-ae51-c48a1ee51404 | note | Acceptance criteria - Sand Fill - not less than 90% of maximum density or 70% of relative density, except that under paved areas the entire depth shall be compacted in 150mm layers to not less than 95% of maximum density or 80% relative density.
e59a1a36-5d06-55cc-a2c6-d42811dc859e | note | ○ Select Fill - Backfill under pavements shall be compacted to a dry density ratio of no less than 98% modified comp active effort.
480854a0-65cb-54b9-83b0-a0cb506e7a48 | note | ○ Backfill to be in 250mm compacted layers.
a260f2aa-49ca-5118-9188-ed734407a01b | note | ○ Testing Frequency: Minimum 2 field density tests for each 185 m2 of each compacted fill layer, but no less than 3 tests for total area
e16bd1ac-11ae-54ea-aae9-1673a5f8507c | note | ○ Has compaction testing been completed as per the project specifications?
96fa03c8-7a24-5525-b8e3-f1056e5019d0 | button | Acceptance | Yes,No,N/A
46c8f2e3-495d-55b1-8237-e875090a51ff | note | Key - W
94d0a05e-08e8-5d4c-95fe-f5c5408a3bb1 | note | MDR/VIVA - S
224a8dba-bfd7-5f6b-9f42-48191f4b6cb2 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
4f4a6cd8-092f-521a-94f8-fdd7b33f3688 | tickbox | Compaction Testing Results
| section | 5.0 Testing and Conformance Check
| checkpoint | 5.1 - Test Pack
e2a98f6d-59dd-5c22-9dd3-182a57980a79 | note | Acceptance criteria - Has a test pack been provided?
f1d9cf5e-27ac-5e86-a5fa-5bbe7744895b | note | ○ Test pack to include.
f7a2af4e-4e44-580d-a964-41ec8b9161c1 | note | – Test Procedure
3afb6982-b28d-5c79-a7ce-2291127b05dd | note | – Test Map
f5aa3906-c8b4-5f00-afa5-4e2d551fd044 | note | – Equipment Calibration
ce701d07-e07f-57c3-9507-940b90a5e4e1 | note | – Equipment Details
e2f5bb24-9a06-5725-925a-f4ea5a191725 | note | – Exclusion zones if require
423d8eec-6474-5252-9305-149d9f2bd3f2 | note | ○ Provision of testing log template
bc28ded6-eca5-59f7-bd74-6a9e752dda06 | button | Acceptance | Yes,No,N/A
cca49944-4970-53c1-9353-c2ea58f6df5a | note | Key - H
f9841f43-4346-5704-bc67-ef173fd1f9f9 | note | MDR/VIVA - H
ab617d9b-2f39-5d7a-82fa-bc63bf3036cb | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
914d8a34-6b14-5776-a3c3-1f4c4153b5e5 | tickbox | Testing Log
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 5.2 - Survey
2a5fb68a-c9ae-5c0a-9219-14d3c39ba437 | note | Acceptance criteria - Tolerances in alignments shall be limited to +/- 25 mm vertically or horizontally, unless otherwise specified on engineering drawing, has this been completed?
fa08bc86-b55e-52ed-9d4d-63b6278d14d2 | button | Acceptance | Yes,No,N/A
2b143989-0709-5519-9296-7f7c8c55bc99 | note | Key - W
67902516-9bdf-585f-9805-553d9100a5bd | note | MDR/VIVA - W
5d8b0057-907f-516c-aeeb-62d02d72637a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
35a0e63e-6b0d-5b7b-aa6b-ddbb1eedf264 | tickbox | Survey as-built
| checkpoint | 5.3 - Quality Submission
2a979cfd-fae0-582e-9348-94db278ed327 | note | Acceptance criteria - Have all QA documents in-line with the specification been provided to MDR for review?
6ad83100-20ef-5234-9588-0073c634af13 | button | Acceptance | Yes,No,N/A
78b53b3d-e239-5cde-9ae9-ecd3ed391ca9 | note | Key - H
e4d21162-3d8d-505d-9c3e-1471fcc8a926 | note | MDR/VIVA - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0398-ITP-035 Concrete Pile Cropping Rev A | itp | INF-HSEQ CC0398-ITP-035 Concrete Pile Cropping Rev A |  | 4c4a6751-f535-4b4a-a697-a5d955c6f6ee
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Starter Bars
8ae24b3d-abce-5ec3-a865-da3d22f551ae | note | Acceptance criteria - Are starter bars (if exposed) in suitable condition:
26aae61d-2e11-5bc2-8468-d6ce6b5c6b60 | note | – Straight
012b3866-40be-52a2-8ae8-c5bba30a2dfa | note | – Free from excessive rust
da809df4-11ed-55ca-9580-ad82b8752848 | note | – Correct height projections
f747c67d-98e0-5e95-b947-4f033c769e31 | button | Acceptance | Yes,No,N/A
b648de6a-d547-58ea-aa33-9dc2bb839aab | note | Frequency - Once per Pile
8bf1e468-0fd0-5880-873b-68e44c04f331 | note | Key - S
| section | 2.0 Pile Cropping
| checkpoint | 2.1 - Set out
547f3e8a-9c95-53c6-9279-ec3ac70702f9 | note | Ref docs - DWG No. GRN-92002-030002 – 10
7a97ffcd-c497-5834-ab89-9a8989418304 | note | Acceptance criteria - Pile cut off has been marked by survey
16891ff0-f0d8-5aca-a0b4-ea99bd4bdea6 | button | Acceptance | Yes,No,N/A
32415fad-52df-55de-9551-5d7437b240d9 | note | Frequency - Once per pile
ea87b81d-777d-5230-beec-105541b3cec9 | note | Key - W
| checkpoint | 2.2 - Pre-Cutting (if required)
e49d1463-e486-50ab-9dcd-8ba4792b90cb | note | Acceptance criteria - Has the pile been pre-cut along survey marked level i.e. ring cut method
87296c93-4e49-505e-837e-62f45d55a68a | button | Acceptance | Yes,No,N/A
6f185c69-5e93-501e-b2a8-f79cc06c5f79 | note | Frequency - Once per pile
00abd880-eecb-5802-9f7e-6875a3e1f36f | note | Key - S
| checkpoint | 2.3 - Irregular Concrete
764a1a55-27f2-5386-9703-ac4da874dcc8 | note | Acceptance criteria - Large uneven/jagged concrete sections to be removed to create flat concrete cut off level
d90861ba-1252-5b52-98d7-e507ecc8f546 | note | Frequency - Once per pile
10c8b0f0-c2ca-5cac-8a90-7fb2aad3a8dc | note | Key - S
| section | 3.0 Conformance check
| checkpoint | 3.1 - Tolerance
a730d33a-9f35-5641-bde1-b78330e193fa | note | Ref docs - DWG No. GRN-92002-030002 – 10, As per civil (235929) drawings
a4970c45-9438-592d-b7aa-d90ca2f68587 | note | Acceptance criteria - Survey to check actual pile cut off level is within +-+-25mm of cut off level.
e469f67c-a8e9-53ff-bcad-9e7658341987 | button | Acceptance | Yes,No,N/A
1beded09-da3b-5934-9a83-5b8f9e0da0e0 | note | Frequency - Once per pile
94c247b9-392e-570c-b7ca-c0cb7b147bc4 | note | Key - S
| checkpoint | 3.2 - As Builts
8fe34c38-2987-583d-9455-7320780f7cba | note | Acceptance criteria - Survey to pick up cut off levels for as-builts
69d2f9bd-cbaa-5645-9baa-4cfcb2c102f5 | button | Acceptance | Yes,No,N/A
b57b76f9-0680-5eb7-94a2-6e5c4eb6ff82 | note | Frequency - Once per pile
eb59b1ea-608a-5ad2-ac26-b338b34c4cd4 | note | Key - S
| checklist | INF-HSEQ CC0398-ITP-037 Earthing Installation Rev C | itp | INF-HSEQ CC0398-ITP-037 Earthing Installation Rev C |  | 7a0a6c07-608b-4b35-a60a-50d0dad50f36
| section | 1.0 Pre-start activities
| checkpoint | 1.1 - Set out
8cee6730-a2af-57b1-9b57-a7060567d2b3 | note | Ref docs - Composite Drawings
f9db8eba-ea63-5a3b-b231-a62e4b8425d3 | note | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
9cd90a20-55f5-5ed1-8e51-afbaaaabb4ef | note | ○ IFC and latest available revision used?
38bfef6c-4477-56ff-b7bf-2e48acf3c825 | button | Acceptance | Yes,No,N/A
ccab05ea-96f2-5d9b-8845-685986d487cf | note | Key - H
4736233e-544c-5c6d-9c9f-7c43296ff3e4 | note | VIVA - W
| checkpoint | 1.2 - IFC Submission & Approval
48ae4f29-13bc-5989-b102-f90696dad5c3 | note | Ref docs - Composite Drawings
096dd421-f790-5fdd-b740-14fabb48a408 | note | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
730ae177-d0a9-5ecc-8931-d7ed6e7a5bbd | button | Acceptance | Yes,No,N/A
425d137c-e481-54b7-baac-c7f140c87657 | note | Key - H
4520f176-6193-5385-af2c-2ea0c5485497 | note | VIVA - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.3 - Permits
8643866f-3b27-5c58-abcb-607e9424f0ce | note | Ref docs - Symal Safety Procedure
cc5f3ad8-fd9e-59de-a80c-50fbf3185263 | note | Acceptance criteria - Have the below permits been created.
62f01cff-b9fb-5db5-a10a-704c3b1a713c | note | – GPP
cfa9dec5-9be5-5741-8033-b68e5534d884 | note | – Working at Heights
0be84294-74d3-5805-afad-4ba0450238f1 | note | – Hot Works
a1987483-24bf-55a4-8842-87af73d1479b | note | – Confined Space
ea83f727-45e6-5108-8083-72e0ec6ad20d | button | Acceptance | Yes,No,N/A
defa0d4d-5c33-58d2-9e91-f8ef1fed82fd | note | Key - H
4043a63c-c6bc-5d89-b965-68229e6ffbb0 | note | VIVA - W
| checkpoint | 1.4 - Determine Lot Size
278c45ec-97a7-58c9-ac20-fd4bfa25fb30 | note | Acceptance criteria - What is the lot size?
eef4a63b-c72e-5ac2-a0b9-e21eb7301941 | button | Acceptance | Yes,No,N/A
77204dd3-a107-585b-a5e4-284846c25127 | note | Key - S
9f59d620-efb9-5df2-a905-30e42032d1bf | note | VIVA - W
| checkpoint | 1.5 - Materials
126b8a65-2968-50cf-8671-35425da66613 | note | Acceptance criteria - Have the provided materials been accepted, and checklist completed?
11f792d8-9c8e-54ba-a08a-b1d0846c9ca3 | note | ○ Have the materials and tag numbers/heat numbers been verified?
80741666-14ab-577f-967f-a2eb3ddb637c | button | Acceptance | Yes,No,N/A
ee94d348-599c-5e06-9e57-3a2b4f92428f | note | Key - W
01ff3918-4f7c-59a6-8323-5dd349a05a49 | note | VIVA - W
5d4ad777-f65b-52a4-abe0-ccda3623b65b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
b3168178-9984-5c7f-89b6-0e87e2c916cc | tickbox | Material Inspection Checklist
| checkpoint | 1.6 - Electrical and Earthing Pre- Qualification
4b91c8eb-c2ee-5a09-9668-41699dcfd468 | note | Ref docs - Welder Qualifications and tickets. This ITP.
a412595e-b980-5377-a87a-dd96c803b364 | note | Acceptance criteria - Welding procedures, equipment to be used, welding qualifications and calibration of welding machines to be submitted and approved by the client, has this been completed?
c8e50075-a9a8-5b90-b3b8-b9435ffbfd2e | button | Acceptance | Yes,No,N/A
4b7f81a9-4fea-5c02-a633-aed49cca798f | note | Key - H
fd60531e-9225-54c2-a328-1eb0c9676d5d | note | VIVA - H
549b317b-2bfb-5e43-84be-89e06899345c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d759a7aa-28f7-5428-8682-3bff9b89a98f | tickbox | Calibration Certificates
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.7 - Bedding and Backfill Materials Approval
436174e2-eaea-5ba2-85c5-ccc504afad72 | note | Acceptance criteria - Has bedding and backfill materials been approved for use?
05f36b85-69b2-57a6-ab82-85178e69e938 | button | Acceptance | Yes,No,N/A
20b32423-f7a9-56c5-9906-1e4c08531f2b | note | Key - H
6094a024-b76e-5a0f-b0cc-54ecf6e84fa9 | note | VIVA - H
50e886ac-692b-5d7d-b1b0-677900b02e8a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
0be29c63-0b82-5db8-a99b-ca4f7ec8709d | tickbox | Material Approval
| signoff | AUTHORITY HOLDPOINT
| section | 2.0 Excavation and Bedding
| checkpoint | 2.1 - Service Location
a6a4cd41-ff67-5b2d-814d-812a925ed46e | note | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
b72222ef-31fd-5235-84d2-e67c3bf48616 | note | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
6660690b-af66-5259-bc7d-dfd50158f4a9 | button | Acceptance | Yes,No,N/A
aa9b01ea-8147-58f4-ac16-a6c9b3a7641c | note | Key - H
1f4566f1-36c9-54ad-b24b-7e1d1a0b6e43 | note | VIVA - S
| checkpoint | 2.2 - Excavation
3fd93b6e-8747-57f5-8edd-a0c324789b22 | note | Ref docs - 235929-000-CV-SP-00002 EARTHWORKS
495bbc0b-ed7d-5190-9ee0-ff5060f3ec4d | note | Acceptance criteria - Trench depth into buried ground 500mm width to provide sufficient width for earthing to reach design depth.
c3773a7f-7038-5d6c-88bd-6b5425a681ca | note | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
1e5db9d1-aa8c-5dfa-b5a7-928cc4db3959 | button | Acceptance | Yes,No,N/A
ebb7ae07-bfcb-5a95-ad3f-8ca8b259c18b | note | Key - W
5b793bf8-7b11-50f8-a3e8-59c629a88987 | note | VIVA - S
| section | 3.0 Laying/Welding/Handover
| checkpoint | 3.1 - Earthing Installation
1d2b95cb-4390-5980-a304-8d45ab7fc01e | note | Ref docs - Viva Energy Earth Grid Connection Checklist (001) - ITP
01dbcbc2-d472-5e1d-b3da-665f236bebcd | note | Acceptance criteria - Have works been undertaken as per the subcontractor’s checklist?
368df9fc-11ad-5460-a7ff-8c4dea9f8e7f | button | Acceptance | Yes,No,N/A
40ad3313-e035-5d46-8810-0c94ba2f6d40 | note | Key - H
ff7894d3-826d-5955-b2a8-e830f08ddb67 | note | VIVA - W
| checkpoint | 3.2 - VIVA electrical inspection
7772b47b-699a-5e49-9c0f-1e6a2f22c281 | note | Ref docs - New Item
9c0cbd6e-4d47-5f69-9cc5-eebcca38149b | note | Acceptance criteria - Has the electrical inspector from VIVA been notified to attend the project site and review the installed earthing?
243f7759-ac4f-5381-8a93-e2e425613cde | button | Acceptance | Yes,No,N/A
f6416a4c-6330-5a24-bc9f-cc9c58ae11ea | note | Key - H
48e1ff56-6e99-54ab-bcce-f995099c8b6c | note | VIVA - W
| checkpoint | 3.3 - Earthing Network
78c81d56-ab20-58d5-a501-0d549b383be5 | note | Ref docs - 239529-CO-FM-00003 – Electrical Earthing by Area
ad308061-8072-553d-9f1a-2e4df92be13e | tickbox | Has earth Grid installed at correct depth of cover?
bc035c23-b5ea-5126-8dc3-8d814b3d8986 | tickbox | Have earth rods/connections/ferrules are of the correct type, length and material and located as per the approved drawing?
b48f7b01-e8e3-5422-940b-f97933c91c99 | tickbox | Has the cleanness and secureness of all earth rods/connections/ferrules been checked?
cd286451-cd68-551a-bfbb-41f0f673a3e0 | tickbox | Are all identification labels being correctly fixed and visible?
d3698155-4d3b-52ad-84c4-90f3e70062b1 | tickbox | Are all cable clamps are secured correctly, coated with anti-corrosive coating?
da88522c-746b-5a9c-b980-3711e14ba93c | tickbox | Are all cables of the correct size and type?
c2cae75b-1bd2-53fd-986f-299cae0622f6 | tickbox | Are all exothermic welds being acceptable?
db16fb47-13c9-568b-9903-e8f5cfaa24f0 | tickbox | Has the individual earth path / bar resistance been recorded?
92f8d563-eca5-5549-a8ea-c703fbd1d8b6 | tickbox | Has the overall grid earth path resistance been recorded?
1a2439eb-5827-5814-a495-76eb37f3937f | tickbox | Has the anti-corrosion material been applied?
d84bfc1b-9f3d-5ca7-b0d3-b10d5d051ccb | tickbox | Have 3.0m tails been extended as per the project requirements
45692619-9886-52c5-b1ab-642068c4038e | button | Acceptance | Yes,No,N/A
fb08ad92-3d23-5bbf-bcc0-b28d71599733 | note | Key - W
fe854fa9-3616-501a-94c4-1ab64d7ded74 | note | VIVA - H
95791d8c-9a9b-528a-8132-601b24dca2f0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
57a38e06-0052-5c5d-93f7-d4e0674b48af | tickbox | Earth Grid Connection Checklist (Rev 1)
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.4 - Electrical Earthing by Area
1afbdddf-69a1-5ff5-bd83-4f0c4fc5ec31 | note | Ref docs - 235929-CO-FC-000034 – Electrical Earthing by Area VIVA Energy Earth Grid Connection Checklist
bedd8cc5-af96-5a02-a58b-c925bdcff87a | note | Acceptance criteria - Has the equipment earthing in area earthed via earth bosses or studs been installed as approved installation drawings and specification?
b3efdd5a-2565-53a4-a62a-34234df11773 | note | ○ Have all earth bosses and studs been tightly fitted with shake proof washers and coated with project specified protection?
94d60ad9-2d51-5ca9-b0d2-df77460c8f8e | note | ○ Are all earthing conductors correct type and size not less than minimum size specified in approved installation drawings?
3e51b72b-91c3-5b1f-8bfc-4ac80cbdd0a2 | note | ○ Are all earthing conductors properly installed and protected?
4721d462-f575-586c-a40a-81f4005d7805 | note | ○ Has earth resistivity testing been completed?
0b67eee8-5928-5471-8bce-81c1e5bf14ac | note | Structure Steelwork Earthing:
4c4fddbf-f9c3-538d-b358-f5b44c870dc0 | note | ○ Has all structural steelwork that is bolted and provided with equipment earth bonding connected to the main earthing system where required?
e5d3d158-7ced-5ff4-b948-ba58a504e195 | note | ○ Have all earth Bosses/Earth Points been cleared paint /rust free prior to connection?
13daae97-2f9a-5bd7-959e-cb70d2d46cb9 | button | Acceptance | Yes,No,N/A
4c1cd6fd-f03c-5c6e-bdff-4b1252ea620f | note | Key - H
4114626f-72ed-5db8-a2ae-2bd2c71359a2 | note | VIVA - H
6d8e831b-e53d-5591-bdc5-aac6c6022df4 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Testing Checklist
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.5 - Backfill
487668b8-16b3-53a4-b9c3-e6f22fedf167 | note | Ref docs - 235929-000-CV-SP-00002 EARTHWORKS
659566b9-c039-53ff-8ca4-79f1d32bae6b | note | Acceptance criteria - Has backfill been completed to provide a compact and even surface?
cc414001-3505-511d-8ccd-d4c416442e68 | note | ○ Has testing been completed prior to backfill?
cbe10000-05db-58cc-9b3b-a9ba19a2449d | note | ○ Has all third party inspections been completed prior to backfilling?
8c897e66-c8d4-5f84-a29a-b14e1d31057f | button | Acceptance | Yes,No,N/A
4018d55e-932d-5c31-959d-29376e550a55 | note | Key - S
6a3762fa-2805-55d6-8410-6501bea5ce81 | note | VIVA - W
| checkpoint | 3.6 - Clean-up of site
243c4a29-69e7-54f9-a307-2031f2764eb7 | note | Ref docs - 235929-000-CV-SP-00002 EARTHWORKS
f3956859-b308-5440-8888-6834a83739b3 | note | Acceptance criteria - Have the areas affected by the works been restored to a condition similar to that which existed prior to the commencement of the work?
26725281-f51d-5428-afb0-927acb7d577f | button | Acceptance | Yes,No,N/A
554f47ba-8a5d-5aea-9752-d8eb324484ce | note | Key - S
7493cd86-c956-5d86-82b8-c74b01dfde1d | note | VIVA - S
| checkpoint | 3.7 - Identification and recording
90af6f27-0d17-5a94-8097-9ccfb60500af | note | Acceptance criteria - Have the actual installed location and depth of the earthing, and location of pits, been accurately recorded on an as built?
6d3a8327-ee7d-548d-86b3-db7ecfdc9ae9 | button | Acceptance | Yes,No,N/A
d2d51ca3-206d-5f51-8100-a5c9f88815b4 | note | Key - H
dd4e0b01-2fc7-5f87-ac04-1713251b13b0 | note | VIVA - H
5e90900a-3596-508c-a3f2-92f1d97fac5a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
798d6317-ef59-5dda-8c92-976b88b7370c | tickbox | As built
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.8 - Work is complete and complies with design plans / drawings / specs
ec21e9b3-5d1d-5848-99ed-4e9c836516c6 | note | Acceptance criteria - Redline mark-ups As-Built Survey: Earthing to conform to the required depths and locations.
90ad3371-c0ee-5df7-b6a8-ed80c752254a | button | Acceptance | Yes,No,N/A
22dda464-5331-511e-914a-0cc0527fe875 | note | Key - H
65c49590-c187-5ea8-a1c3-a7d44798e24c | note | VIVA - H
8df9d0d1-bfbc-5ae1-a3b2-e35ad5bf1bd5 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
73f1bef4-f865-5873-b180-46a67b44ace4 | tickbox | As built
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.9 - Certificate of electrical safety
14d30253-0ebb-534e-b20c-a681e54211b7 | note | Acceptance criteria - Electrician to supply Certificate of electrical safety for earthing installation
0ef0eb60-e21e-521b-8016-faa0c1457ce4 | button | Acceptance | Yes,No,N/A
effdc95a-54bd-551b-9b74-5e57b43b9bc0 | note | Key - H
658d1851-ee8f-574b-89c7-38ff328fdef5 | note | VIVA - H
98e74aa0-7bdd-5f80-8c89-9baeec6f09ea | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Certificate of electrical safety
| signoff | AUTHORITY HOLDPOINT