## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | INF-HSEQ CC0398-ITP-021 Concrete Pavement Constructions Rev 0 | itp | INF-HSEQ CC0398-ITP-021 Concrete Pavement Constructions Rev 0 |  | 63b89fec-ae32-4be6-b458-8741033dd22a
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Determine Lot Size
e3cff05b-62e3-548e-873b-9babb06eedf1 | note | Ref docs - IFC DRAWINGS
f38181a0-f49c-591f-9652-6bec78581062 | note | Acceptance criteria - Lot size Lot Size = Each pour section per day (location or m2)
bf343427-f7f5-5d99-8533-bd3188a4b23b | note | Acceptance - Marked Plan
c2f09575-55d4-58d2-8113-dd8187168f8a | note | Key - S
45451835-d6ca-56eb-8edb-32b1570c14c7 | note | MDR/VIVA - S
803299bf-52ef-5ea2-9c26-3c0bdb180049 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
7b84fcf0-fbb1-5c1c-b874-8f3d415acdf1 | tickbox | Lot Map
| checkpoint | 1.2 - Survey set-out
05297db0-51cc-5eb0-b90d-f590d0a32eb0 | note | Ref docs - IFC DRAWINGS
090f1ed6-b79e-51ae-96ae-cf1cef1d7fdd | note | Acceptance criteria - Has the work area been set out for line and level?
0cb80111-8eab-5407-9e9d-6543332fec8a | button | Acceptance | Yes,No,N/A
5dc82db9-ee09-53e1-bc28-717bdf031569 | note | Key - S
80ce9576-50f5-5e80-b721-6fc220a42c1d | note | MDR/VIVA - S
39d1fb4d-07aa-5413-af08-fe53863f2dc0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - As Per IFC Drawings
| checkpoint | 1.3 - Material Submission / Approval
b6747361-8246-5737-9e23-9334c1164f8b | note | Ref docs - AS 3600 235929-000-CV-SP-00007
eafbd3de-d6a0-5cef-840a-ae772af9ab9d | note | Acceptance criteria - Has the mix design to be approved prior to placement. Material properties meet project specification, AS 3600, AS 1379?
07b079d1-3b51-5693-903c-66c9e7d85e9a | note | – Minimum Concrete strength 25MPa or as specified in Drawings?
0b477870-6c30-5aa8-a39a-be801d8de8d0 | note | – Steel Reinforcement certificates of conformance provided?
49c36947-dc00-5cfe-8137-d2771833698c | note | – Do admixtures shall conform with AS 1478.1 and are permitted if used in accordance with manufacturer’s instructions?
bcdc7b84-9c0b-51f5-accf-5e81ec9def8c | note | – Are all admixtures free of calcium chloride?
4d55281a-bee2-5833-9032-762cf9f5ee8e | note | – Has jointing materials & Sealants been approved?
87cb8a7d-ec7f-598e-acee-ff5903d38f41 | note | – Has vapour barrier material been approved
03b107ce-66ac-5cdc-926e-f27425645853 | button | Acceptance | Yes,No,N/A
1d5a276a-0555-554d-b4d4-25d2bd614e55 | note | Key - H
36ae1bfc-fc45-500c-92f8-f1aba0251e7b | note | MDR/VIVA - H
c68c8274-d42d-5237-bf7a-fa4a9c5484b5 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
35d82958-a622-5059-b450-bf490bd5fc31 | textbox | Mix Design Number
0c8b3203-dee3-5e82-973c-c5942737e269 | tickbox | Material Compliance Certificates
e9056f80-97e0-540e-ab1b-81f49e26023b | textbox | Idocs Approval Reference
| signoff | AUTHORITY HOLDPOINT
| section | 2.0 Form Work
| checkpoint | 2.1 - Vapour Barrier Installed
5c73229c-b620-5a95-89fc-5d717bc951c0 | note | Ref docs - 235929-000-CV-SP-00007 Section 6.2
980b17d9-1238-5377-a45f-2c6c818ac90f | note | Acceptance criteria - Approved vapour barrier installed on surface of crushed rock base?
c7b8f9ae-038e-53be-a12a-06e598c4c4d0 | note | ○ Are all lap joints minimum 300 mm and sealed with duct tape?
0950f71d-3066-5014-baf4-ba02cc0ccf3c | note | ○ Are major punctures in the vapour barrier patched of taped?
ec015ecb-4d95-5612-bee1-ea0a3943b56c | button | Acceptance | Yes,No,N/A
091e37c3-2b63-5e7e-a845-95c21f101fae | note | Key - W
c1cc0ad8-a311-5e6c-938a-6b76c1ca0390 | note | MDR/VIVA - W
| checkpoint | 2.2 - Formwork Setout and positioning correct
8d283459-6982-5f15-bc8e-583927cb4849 | note | Ref docs - IFC DRAWINGS 235929-000-CV-SP 00008
115eab0c-077d-5dd9-a82f-e269a09f78ea | note | Acceptance criteria - Is formwork checked for potential loose sections, ensuring no movement upon placement of concrete?
91538d04-3476-534e-9408-29a3493fabb5 | note | ○ Is formwork in line with survey markings?
e8d7274b-e2b8-534e-8dd2-6983e766785d | note | ○ Have chamfers (if required) been attached to formwork in level manner?
ceaf839f-aa8d-5fe8-af2a-739fbbe02a09 | button | Acceptance | Yes,No,N/A
1e491d5b-aca2-5c8f-ab9f-9b42a4c9a567 | note | Key - W
62dc63c9-69e8-5154-a378-f3bea5dab6ec | note | MDR/VIVA - W
| checkpoint | 2.3 - Concrete jointing
b3b10119-54a4-5b49-b785-f7a4f58c9ae1 | note | Ref docs - IFC DRAWINGS
099b54ad-52a1-569b-a51d-3d8b725dd05c | note | Acceptance criteria - Have construction joints to be installed as detailed and in locations nominated on IFC Drawings and notes using approved materials?
bdde3652-ea21-5f87-8a73-65ad2016dc81 | button | Acceptance | Yes,No,N/A
a4530fe8-1784-5ae3-8cd6-805f5bf9c4b0 | note | Key - W
11435d09-6246-5a71-94d5-ac2694a940ed | note | MDR/VIVA - W
9fe4de70-7f70-5159-9aea-6eae7666c614 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
3be33c12-09b6-5af3-bbb9-c6c6f47d8c12 | tickbox | Delivery Dockets
| section | 3.0 Reinforcement
| checkpoint | 3.1 - Steel reinforcement Supply
596611d2-349d-5564-aba8-6131b917c3d5 | note | Ref docs - IFC DRAWINGS
490de5b7-f5cf-5065-81a7-a5294dbec2cb | note | Acceptance criteria - Has correct reinforcement been delivered?
7fbd18bd-20e3-5a5f-b0d1-e7b791b218de | note | ○ Is reinforcement free from rust and other contaminates that may affect bonding?
6ffcd710-4570-5070-b145-eb016a04732f | button | Acceptance | Yes,No,N/A
fde47089-42b8-5b59-b22e-6ef58e4a16ee | note | Key - S
1398b4e6-fbf2-501d-a17c-c5d0d0807d7a | note | MDR/VIVA - S
c9e870a7-a94d-5668-a94f-604615940649 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
10e84119-9dd3-5bd7-afeb-18185749ec38 | tickbox | Incoming material checklist
2f0d6a97-55c0-5f6f-9002-b54f99a410b8 | tickbox | Delivery Dockets
| checkpoint | 3.2 - Steel reinforcement installation
695fca6d-c286-5e12-928c-ac819baf513b | note | Ref docs - AS3600 17.5.3 235929-000-CV-SP-00009, IFC Drawing 235929-000-CV-01-92002- 010002
030ebe87-80d1-5fe0-849d-0f3376784f39 | note | Acceptance criteria - Is steel installed as per the latest IFC drawings?
4545e27d-0a10-5db7-8e8c-40b747b814d8 | note | ○ Does steel reinforcement conform with AS 3600:17.5.3?
c2d7b78b-dd4b-5a6f-9ad4-f347e4d4a4f3 | note | ○ Does cover to unformed surfaces comply with IFC drawings?
61134d37-8574-534e-a6b7-f13c9de72e80 | note | – – – – – – – – – – – – – –
cf830b17-dadd-51e3-bcf9-e333a04c24e2 | note | 17.5.3 Tolerance on position of reinforcement and tendons
a63f590f-7278-506a-a523-bccc9bd5f230 | note | – – – – – – – – – – – – – –
5338e11e-d263-5eb3-9687-97e195e89399 | note | The deviation from the specified position of reinforcement and tendons shall not exceed the following:
5118ff21-4350-5e63-91d6-0239a540b1da | note | (a) For positions controlled by cover –
4ad4fbda-3157-5693-b368-7437f4991ffd | note | (i) in beams, slabs columns and walls… -5, +10 mm;
47960318-0d4f-59ab-8d36-b011e46a2306 | note | (ii) in slabs-on-ground… -10, +20 mm; and
c9dd6df3-5bf6-5bcf-8fa6-ade7755f367a | note | (iii) in footings cast in the ground… -10, +40 mm,
b83d74df-2249-5f35-86a3-1f03b402ff58 | note | where a positive value indicates the amount the cover increases and negative value indicates the amount the cover decreases.
efa2ade2-8ad2-5069-ae99-820bc521d76b | note | (b) For positions not controlled by cover, namely –
fe3ce8b0-8842-5517-a288-1d04de832405 | note | (i) the location of tendons on a profile… 5 mm;
e053e7aa-e639-55d2-9d69-a16e3def80c5 | note | (ii) the position of the ends of reinforcement… 50 mm; and
aeb82a67-8a10-5a69-9002-8c14862484b2 | note | (iii) the spacing of bars in walls and slabs and of fitments in beams and columns… 10% of the specified spacing or 15 mm, whichever is greater.
efad0451-85ce-5de9-bf87-db674f675166 | note | – – – – – – – – – – – – – –
66ec8bf3-0d3f-52a4-8136-e103c38906fe | note | 8.0 CONCRETE COVER
e2c9f875-221a-5084-aa6c-bd1d98ed6795 | note | – – – – – – – – – – – – – –
9a7bceeb-a83f-59e8-b12c-8aa4d6f87771 | note | 8.1 CONCRETE COVER SHALL BE IN ACCORDANCE WITH AUSTRALIAN STANDARD AS 3600 OR THE VALUES STATED BELOW, WHICH EVER IS GREATER.
713d63aa-0146-591e-bd80-7d6c74837e2f | note | ○ PAVING (TOP) = 30mm
c06a971d-d9a5-57f0-880c-03745d4fe50c | note | ○ PAVING (BOTTOM - AGAINST GROUND) = 50mm
16d70702-3330-59c9-9fd0-4688e5b6695a | note | ○ FOUNDATIONS CAST AGAINST FORMWORK (INCL. EXPOSED WEATHER FACE) = 45mm
27e4f6b9-baaf-55bc-84c8-f2bba851952f | note | ○ FOUNDATIONS CAST AGAINST GROUND = 65mm
7ca613d0-6576-5306-a5c3-54b4083768bc | note | ○ EXPOSED TO WASH DOWN WATER AND/OR PROCESS SPILLAGE = 50mm
e423a939-bfe6-50d3-8f7f-e00bca284967 | note | ○ CAST ON LEAN ON CONCRETE = 45mm
74d4d96a-76bb-5675-a5bd-ff1f3cb0ba33 | note | ○ CFA PILES = 70mm
9acea169-5d6c-5ee0-9d2a-807605d6c72c | note | – – – – – – – – – – – – – –
38f7886a-05ce-55ca-ae65-fdfb625b5d3c | button | Acceptance | Yes,No,N/A
472fb123-d047-5bab-9d63-d603931fa535 | note | Key - W
6ceb1360-5531-5f3f-873c-245b2e359aad | note | MDR/VIVA - S
| section | 4.0 Concrete Pavement Placement
| checkpoint | 4.1 - Pre-pour Inspection
915a36ae-3d62-51c8-804b-31483dc5c526 | note | Ref docs - 235929-000-CV-SP-00007, Appendix 7.1 Pre-Concrete Placement Checklist
1ae11140-780e-5fee-8a65-a859dbb918c2 | note | Acceptance criteria - Has a pre-pour inspection checklist completed prior to placement?
ba2da0b7-d5f9-564e-aa35-be6e3805fdde | button | Acceptance | Yes,No,N/A
4227106c-d573-511b-8cbb-3ea27c32bc04 | note | Key - H
a1c20725-9f46-5bbc-9da3-5d88a04b2de5 | note | MDR/VIVA - H
c630142f-31a5-5df6-ad1e-c3197161b870 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
1df05ce8-1c30-5f44-a2da-88cc0cc2e44c | button | Pre-Pour Checklist Attached? | Yes,No,N/A
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4.2 - Placement
ea394a95-fe9e-5ccb-abc9-10ea3fe60295 | note | Ref docs - 235929-000-CV-SP-00007, Appendix 7.3 Concrete Truck Record
d70a2301-12b5-5267-8596-f9817a029b00 | note | Acceptance criteria - Concrete shall not be placed when temperature is less the 5°C or greater than 36°C. Between 32°C and 36°C admixtures and placing requirements must be met.
eecf61b5-2dc9-538a-a731-1abd8eb94d10 | note | ○ Concrete shall be transported, handled and placed to prevent segregation, loss or leakage of materials.
50fc55b9-4fb5-5dc2-8b75-92fd15dfa74a | note | ○ Concrete shall not be dropped from a height greater than 2m.
94322f4b-834d-5bb5-80cb-af829e4c7190 | note | ○ Concrete shall be discharge within 90 minutes of dispatch from plant.
02f2902d-a46a-5118-ada9-16259d82fd7c | note | ○ For continuous pours, the maximum time lag between truck loads shall not exceed 25 minutes.
e3377e4f-58e5-5b00-aa70-073bdfaa3d27 | note | ○ Concrete shall be thoroughly vibrated to ensure no honey combing, voids or surface defects occurs and compaction is achieve throughout structure.
06f72c08-7c33-5083-b031-1a8179efeb16 | note | ○ Water shall not be added to achieve slump greater than specified. If additional water is added, slump test to be performed after water is added.
549023c8-a482-5e6e-b73c-ead2e3ecab1a | button | Acceptance | Yes,No,N/A
a258f9f8-9268-5fa0-8644-050b8b1ea373 | note | Key - S
0b6dcc43-2025-516d-85c6-6bd0e78f73da | note | MDR/VIVA - S
ff521fc1-8b0e-53e7-9c6b-91e4dbab48ff | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
992be8cd-46cc-5170-94fe-54590539e86b | tickbox | Concrete Truck Pour Record
8ce629c2-6deb-51bd-bf73-a03a5cabce25 | tickbox | Concrete Delivery Dockets
| checkpoint | 4.3 - Slump Test
8f4ebecb-36e7-5475-be99-38c0141f2ebd | note | Ref docs - Section 5.1.1 235929-000-CV-SP-00007
79a0d9df-9055-5b40-9bdc-c09f7beb213d | note | Acceptance criteria - Slump must be within tolerance of designed slump. Testing shall be +- 15% of stated approved mix design slump.
09dcde1e-5a6b-5283-a752-942e2ff50e59 | button | Acceptance | Yes,No,N/A
e11fef28-af9c-504d-b78e-cebef3e4d1b7 | note | Key - W
f349b48d-a8fc-5f48-b47a-1f1d8075d8ab | note | MDR/VIVA - S
69c14d9f-2dc9-5494-bcd7-ddd9a3c3d4db | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
353ba9dc-9fba-5c0f-bec1-474c8fea0370 | tickbox | Concrete Test Report
| checkpoint | 4.4 - Strength Testing
4d549bff-afd8-5321-ac19-cc0e5b59aa7c | note | Ref docs - 235929-000-CV-SP-00007 Section 6.8
45a56bc1-88d5-5e59-8ab5-9626e79cbc1d | note | Acceptance criteria - Samples to be taken from chute. 5 cylinders collected per sample – 1x 7day, 3x 28day, 1x reserve.
ea859ff3-b7cd-578d-ab15-1ada3bff0847 | note | ○ 1 test for the first 20m3
a34400fd-01fa-5b2a-90d4-fab14e5e9212 | note | ○ 1 test per 40n3 thereafter
7e6bc7da-1832-5b82-a0cf-c4d757c9dcda | note | ○ Frequency reduce to 1 test per 80m3 for pours over 400m3
79a87dad-7b15-5aca-9522-3869c3c80abf | note | Acceptance
20a78d21-e9b3-5b77-9f0c-7744c1dd6d04 | note | – – – – – – – – – – – – – –
0f21931c-f040-57ce-8e3f-30d2a796fd5e | note | No. of Samples ¦¦ Vol. of Pour (m^3)
6359218e-d0cc-56c5-9ad3-e741bf230721 | note | – – – – – – – – – – – – – –
c4307d14-b7cd-558b-995f-b34717a2642b | note | 1 ¦¦ <20
a5a2f058-8c8f-5baa-8ff3-0ea7db124254 | note | 2 ¦¦ 20-60
95cc7908-facb-5de5-b36c-420677228eb2 | note | 3 ¦¦ 60-100
6ad80ded-1a09-5d83-bb74-296a2bd1ed72 | note | 4 ¦¦ 100-140
0eaf698f-46c2-5bc8-9145-59fd9038dcdd | note | 5 ¦¦ 140-180
f0c60f26-4b4e-57d6-9473-442843b690e6 | note | 6 ¦¦ 180-220
80560e6b-6bcd-570f-87b8-0359d60273ad | note | 7 ¦¦ 220-260
990b723a-ef94-5fc2-8e9a-fc03b6c6fde4 | note | 8 ¦¦ 260-300
d34f342e-7510-5eb5-b111-b6bcb3513323 | note | 9 ¦¦ 300-340
6dbca2ff-18a2-5e1f-a9ac-401e0ae53877 | note | 10 ¦¦ 340-380
adea7023-0b6e-5a13-822d-fe661ee46981 | note | – – – – – – – – – – – – – –
a1f0e421-f05d-5d39-859a-4c6609f1085c | note | Key - H
f9047c88-33dd-5d76-990c-8ad6dbd4b70b | note | MDR/VIVA - S
d7a05f16-60d2-5d5a-a55d-a1f42157aede | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
6188e887-fdf5-57d7-8842-418bdc42eb9d | tickbox | Concrete Test Report
| checkpoint | 4.5 - Curing of Concrete
581741fa-ffea-53c6-83a1-9abe95c6b509 | note | Ref docs - 235929-000-CV-SP-00007 Section 6.5
e74a8979-8910-5a29-b687-f8f576bea9ce | note | Acceptance criteria - As per the approved Curing Methodology.
df107372-20c1-5158-be23-872dabd172e6 | note | – Applied once bleed water has gone
7a96f1d2-24f2-5dcf-ae60-dff034acea1b | note | – Continuous uniform film achieved
99a96a89-c3d3-553a-91e6-e0fe63ef10e8 | note | – Rate of 5m 2/L
764e527f-dd27-5b87-8c77-e1b71a271396 | note | ○ Has curing been conducted as per approved curing methodology?
a18330b3-b63e-5ec9-ba4a-bd5b0dc272e4 | button | Acceptance | Yes,No,N/A
cb2e51ed-8bb2-5c93-aba9-bb1c5c770642 | note | Key - H
b097c186-91e6-5cfc-95c7-c014105daa77 | note | MDR/VIVA - W
fb7e8181-9dfd-5075-bf6a-d26ff0fb563c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
f7414eda-c9a9-5889-8790-1938c4e7058b | tickbox | Approved Curing Technical Data Sheet
| checkpoint | 4.6 - Colouring of Concrete
e72906b2-fe5a-5b0d-bfe5-e44050234211 | note | Ref docs - 235929-000-CV-01-92002-010015 Note 9
363a2d10-2458-5e7c-ba71-2ae3a3b794fc | note | Acceptance criteria - Concrete paving above conduit, shall be pigmented:
9a76b413-90a7-54db-abd7-7a5b817438ff | note | – Red for electrical;
1e0178ca-a874-5d19-b1b3-1b521ae29602 | note | – Green for instrumentation.
ff27678c-1910-5dc0-bd21-0a411fb004eb | note | ○ The method to be used is the dry shake, with oxide minerals after bleeding.
d1d25368-6441-5634-84e4-7b9e444f65e0 | note | ○ Pigments shall be used in accordance with the material manufacturer's specifications
73aaea01-e6ee-5421-aa33-790c126ea2f6 | button | Acceptance | Yes,No,N/A
e4e71429-4fdd-5abe-870c-76d910e01eca | note | Key - H
ff3b52e2-aa6a-5fd1-b27f-319143738c22 | note | MDR/VIVA - W
d8348763-e1eb-5be2-bf00-c8d74693d8b3 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
be61b032-4d75-5653-9480-6dd88c805b51 | tickbox | Material Approval
3c1e20bb-ad19-5f1f-b0c7-a648cb319865 | tickbox | Delivery Dockets
| checkpoint | 4.7 - Concrete Finishing
113965a6-b35a-5c7f-8185-ea35cebc6a55 | note | Ref docs - 235929-000-CV-SP-00007 Section 6.4
8a668b9b-447b-5062-a95a-fec7be42d00f | note | Acceptance criteria - Finish concrete per schedule below:
54567ab9-a602-56f7-9b4b-7ea12553ac2e | note | – Exterior slabs (i.e. foot traffic): broom finish.
499014b1-5716-552f-8f9e-d2c0df81461d | note | – Other approved non slip finish (i.e. stipple finish)
97bdb90a-df4f-578c-837a-45dd8ad1649b | button | Acceptance | Yes,No,N/A
f1cb240c-52ab-5503-a4d4-8ebc990c868d | note | Key - S
e91ff60c-a30b-57ad-972f-3992b771f70b | note | MDR/VIVA - S
| checkpoint | 4.8 - Formwork Stripping
1b127e7b-b7b1-5751-bf82-5b5a708fc0c3 | note | Ref docs - AS 3600 Table 4.4
e69b09b2-cdf5-5428-aef4-e949bf496c69 | note | Acceptance criteria - Minimum Initial curing requirement for 25MPa concrete:
79ef44bd-a4e9-56f9-878b-d32473300a61 | note | ○ Cure continuously for at least 3 days or minimum average compressive strength of 15MPa
ba3a5a33-291f-5dde-9970-a44d7c9c97af | note | ○ Has the formwork been removed in the same sequence as concrete placement to achieve similar concrete surface coloration?
921faeca-32f3-5c25-aac8-09369c86b408 | button | Acceptance | Yes,No,N/A
6b02bf20-0cae-52e6-a893-98805c0b4514 | note | Key - H
3415d278-4b6c-5ac1-9bf0-16b4ad23e672 | note | MDR/VIVA - W
| checkpoint | 4.9 - Saw Cutting of contraction joints
b3584f8c-4087-5948-adae-4bc70b8d08fe | note | Ref docs - IFC Drawings 235929-000-CV-SP-00007 6.4.4
1267435d-0168-57d6-882d-a319369264f9 | note | Acceptance criteria - Should the joint detail differ from design this shall be changed only with written approval by the Client.
504069d3-2226-5e28-b98d-7b1cc8822355 | note | ○ Saw cut joints shown on the Construction Drawings within 12 hours after placement.
95abdc03-7a98-5b25-8fd4-63450d4da462 | note | ○ The cut depth shall be 25% of the slab thickness.
a650b7ff-b4a2-5aaf-bcd0-f6912c160e5c | button | Acceptance | Yes,No,N/A
1258bb37-3d15-51f0-ae15-312980dded05 | note | Key - H
e92ed812-89e3-54fd-90bd-17007a324dd3 | note | MDR/VIVA - W
28f3b31f-8ee3-5ea1-9996-2a4ccf8eb462 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - RFI (if applicable)
| checkpoint | 4.10 - Post Pour inspection
fa8580ea-6edf-5d51-bdf4-a7362f56ed9c | note | Ref docs - 235929-000- CV-SP-00007
f4db46ac-1d43-5918-b0e0-b0a50f60a1ab | note | Acceptance criteria - All abovementioned works have been completed in-line with the drawings and specification and backfilling around structure can be completed (if applicable)
be608834-ba0c-576f-90f4-c10c635a1d27 | button | Acceptance | Yes,No,N/A
6aa9178c-1006-51e2-8680-efd41b2f1096 | note | Key - H
9f3c5a85-d1ca-5c2d-b538-341f4e586fd8 | note | MDR/VIVA - H
760951c0-c71a-5265-8cc1-94fce2f746e8 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
234dc14d-0c2a-5a12-88f6-7d773f4b8f30 | tickbox | Post-pour Checklist
| signoff | AUTHORITY HOLDPOINT
| section | 5.0 Completion
| checkpoint | 5.1 - As Built
a50a5d8d-0fc5-5922-8606-30c6d8a606a2 | note | Ref docs - YJRP-SPE- CC-M-0001
50f89dbd-0b41-5d4c-a750-14d7a41ee597 | note | Acceptance criteria - As built to be submitted after pour, showing set out, RLs, grades and any cast-in elements
1cb37836-715c-51d1-982c-19b821b09989 | button | Acceptance | Yes,No,N/A
ace517df-e1fd-56f9-b5ba-f1d7be4af77c | note | Key - S
c85a96e0-2524-5b10-a70a-51ebb47339ee | note | MDR/VIVA - H
6b872cd9-76d3-5757-b73b-be2fe76120b0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
4c4ac923-7050-53b9-aa9c-8dd13b0e9df2 | tickbox | Survey Conformance report
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 5.2 - Concrete Test Results
c49956b4-65e2-5375-a44d-80429af0f613 | note | Ref docs - 235929-000-CV-SP-00007, AS3600, AS1379, AS3610
e52813d6-d550-5f91-a97d-684002b78c9f | note | Acceptance criteria - Submission of 28 days results. Results meet requirements of 25MPa.
81177830-4201-5da5-b3ac-bf4b4d807677 | button | Acceptance | Yes,No,N/A
7c1bce3f-4988-54e3-99ea-7f254bbad6f1 | note | Key - H
9027f07b-bcb6-5e8c-9ad5-dc1919d85067 | note | MDR/VIVA - S
5ffd51fe-1035-5958-94ef-5a1bde40cfad | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
afefde41-bd67-5d64-a317-0f01f07ebea1 | tickbox | NATA endorsed test report
| section | 6.0 Crack Repairs (if applicable)
| checkpoint | 6.1 - Cracking repair methodology approval
6944e8d1-36b3-55ad-88cf-dc3bccfdb229 | note | Acceptance criteria - Contractor to submit a concrete crack repair methodology to MDR prior to commencing any crack repair.
6d2fea31-0f32-59d3-879e-e379bd8e6cd5 | note | ○ Has this been approved?
104f13ab-83cc-5653-abc2-bac0de31c0b3 | button | Acceptance | Yes,No,N/A
00450c35-382e-5b48-9fcb-899ee5c3510b | note | Key - H
ce587645-5945-5e12-9d2c-6e921c3a8a53 | note | MDR/VIVA - H
eaa3a7ee-9576-501f-bf6b-91e813534432 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
62802349-7d34-59c6-a9a8-bada7bc2fa6f | tickbox | Concrete Repair Method Document
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 6.2 - Crack Repair
8a5287bf-7fb6-5a94-8826-4178bf02c7e0 | note | Acceptance criteria - Has concrete crack repair been undertaken as per the approved method?
629f0d33-74c4-55ab-a297-0628c85149a1 | button | Acceptance | Yes,No,N/A
b1a356c0-4ed6-57f8-8285-8d2222ca9d74 | note | Key - H
ca801b5c-83ee-516e-ad20-83040eb49dee | note | MDR/VIVA - H
| signoff | AUTHORITY HOLDPOINT