## Foundations
INSPECTION & TEST PLAN
|  | Contract Name: |  |  |  |  | Rev:
|  | ROCKET LAB NEUTRON SEPARATION TEST RIG Civil and Foundation Works |  |  | Hold Point (H) |  | 0
ITP - 002 Reinforced Concrete Foundations |  |  |  |  | Submit (S)
Approve(A)
TASK | SPECIFICATION REFERENCE | TEST REQUIRED | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA | UCCL | Client
Materials
Concrete Mix Design | Rocket Lab Neutron Separation Test Rig, Structural Specification clause 2.7 and 2.8.1 | Ready Mix Test certificates accordance with NZS 3104 - supplier, 3X random test cylinders for each 75m3 placed on site NZS 3112, part2 , clause 3. | UCCL, Engineer | Prior to work commencing on site • Blinding / Site concrete 10 MPa • Foundation pads 30 Mpa | Ready mix testing shall comply as per Structure specification clause 2.7 pg. no. 15. All other concrete shall be from an approved and fully audited ReadyMix plant clause 2.8.1 pg. 16. Calcium Chloride shall not be used. Maximum aggregate size shall generally be 19 mm. The aggregate used, and overall mix design (including the use of any additives) shall meet the provisions of section 2 of Alkali Aggregate Reaction (C&CA). Evidence may be required in support of this by the Engineer. Use of low alkali cements or aggregates from an alternative source may be required where the proposed aggregate contains deleterious material. | H | H
Reinforcement Steel | Rocket Lab Neutron Separation Test Rig, Structural Specification clause 1.7 | Manufacturer's certificates | UCCL, Engineer | Prior to Ordering | All reinforcement shall be Grade 300E and 500E complying with AS/NZS 4671. Grade 500E reinforcement shall be manufactured by a micro-alloy process by an Pacific Steel. Coiled and re-straightened bar will not be accepted under any circumstances. Hard drawn steel wire reinforcing mesh shall be Grade L complying with AS/NZS 4671. Ductile 500 Mesh shall be Grade E complying with AS/NZS 4671. Mill certificates meeting New Zealand Standards must be provided to the Engineer for all reinforcing steel used on the project. Specification clause 1.10 pg. 8 | H | H
Cast in Items - Nuts, Bolts and Anchor bars | Rocket Lab Neutron Separation Test Rig, Structural Specification clause 3.6.8.4 pg.28 | Supplier Documentation | UCCL, Engineer | Prior to Ordering | Bolts, Nuts and Washers shall comply with AS/NZS 1252.1/2. All bolts shall be hot dip galvanized to AS/NZS 1214. Provide documentation demonstrating compliance to the relevant Standard (refer Section 5.3) prior to delivery of bolts to site. | H | H
Pre Construction Site works
Form work | Rocket Lab Neutron Separation Test Rig, Structural Specification clause 2.8.5 pg.16 | Visual Inspection | UCCL | Prior and after being used | Fairface formwork shall be so constructed as to provide straight and true angles and so as to produce cast surfaces within a tolerance of ±5mm on the given dimensions. Plywood formwork shall be sealed with not less than two coats of polyurethane varnish on the concrete face. Diesel oil-based products are not permitted. Timber formwork which is not being used for the next seven days shall be cleaned, oiled and stored flat. It shall be protected against gross changes of moisture by use of a tarpaulin or similar waterproof cover enclosing the top and all four sides completely. | W | W
Reinforcing | Rocket Lab Neutron Separation Test Rig, Structural Specification clause 2.8.5 pg.16 & Clause 1 | Visual Inspection | UCCL, Engineer | Prior to pre-pour inspection | A copy of the completed pre-pour checklist is to be given to the Engineer prior to the Engineer observing the finished Section of work. 48 hours notice is considered a minimum. The Contractor shall furnish a fully completed Producer Statement. This certificate shall cover all work completed under this Section of the Specification. | H | W
Concret Pouring and Curing | Rocket Lab Neutron Separation Test Rig, Structural Specification clause 2.9 to 2.11 pg17 | Visual Inspection | UCCL | During and upon concrete pour | All concreting shall conform to NZS 3109, Section 7. Concrete shall not be pumped without the Engineer's approval. Where such approval is given, only a standard “structural” concrete mix design may be used.If it is found to have free fallen more than 1.5m, concrete will be rejected. Vibrators shall not come within 12mm of the face of the formwork. All concrete shall be cured as defined in NZS 3109, Clause 7.8. The use of a plastic curing compound shall be as agreed with the Engineer specifically for each occasion before it is used. | H | R
Prepour Inspection
Pre pour inspection | Rocket Lab Neutron Separation Test Rig, Structural Specification clause 2.5 pg15 | Pre pour inspection sheet | UCCL | Prior to placing structural concrete | Pre pour inspection sheet to be completed prior to placing concrete. Engieeer to be notified of pours for inspection at least 48 hours prior to placing concrete. | H | H
Post Construction
As Built & Final Design Documentation | Rocket Lab Neutron Separation Test Rig, Structural Specification clause 3.6.8.11 pg29 | Surveying | UCCL | For Each Foundation | Confirmation From Engineer on as built records. As-built HD bolts postion prior to pouring slab - as reqested by Engineer. | H | R
Completion Inspection inc. Construction Defects Report | Rocket Lab Neutron Separation Test Rig, Structural Specification clause 2.24 to 2.26 pg21 | Completion inspection on each foundation by Engineer | Engineer/ UCCL | For Each Foundation | Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out | H | R