## Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Defect / Issue to be rectified |  | ADD new defect / issue to be rectified [RENAME CHECKLIST TO LOCATION & DETAILS OF DEFECT] | 6cbd9a50-cfec-432f-b80a-1db719ea5e1e
| checkpoint | Upload photo of defect / issue to be rectified. Add comments if necessary.
| checkpoint | Has issue been rectified / defect been closed out? Upload photo
bab1d5a9-a3d7-58ff-a01f-4224a18aac6b | note | Only PASS once issue is rectified / defect is closed out
| checklist | Document Attachment ITP (V.220421) |  | Document Attachment ITP (V.220421) | e920e8f0-713b-4328-b734-38c95e331992
| checkpoint | Documents/Drawings attached for reference - Pass once attached
| checklist | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff |  | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff | c22a9754-a0b6-4fc5-a29c-253334e07aac
| section | Sprinkler Rough-In
| checkpoint | Latest consented drawings checked & referenced
4c86029a-d781-58d4-ab05-31be3edee4f8 | textbox | Drawing & Revision #
0c9e405c-eb3b-5fb4-a1bc-b3def20dbb1d | tickbox | Area clear, tidy and accessible
7e882623-d0b9-5543-949f-3565c5f582d1 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Supports spacing & fixing as per AS2118
| checkpoint | Pipework installed as per drawings
| checkpoint | Concealed space sprinklers installed
| checkpoint | All ends blanked off/plugged for testing
| checkpoint | Pipes left out
79f285fd-b900-5728-b3a6-8ef5464c2e30 | note | Fail=Missing, Pass=Complete
21bfabe2-8679-570d-8ffd-0a2ea9d0abb2 | button | Pipes left out - installed | Yes, No
| section | Sprinkler Fit-Off
| checkpoint | Latest consented drawings checked & referenced
26126db9-8fcc-5f1c-aebf-4ae0acc68ed4 | textbox | Drawing & Revision #
4cb73ded-86bb-5ad4-96a0-7a4a0807f0cc | tickbox | Area clear, tidy and accessible
b55ca0c7-ad8c-5225-aaff-fccf38678e0c | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Ceiling grid levelled
| checkpoint | Sprinklers installed as per drawings
| checkpoint | Sprinkler Type & temperature as per drawings
| checkpoint | All escutcheon plates installed
| checkpoint | Areas not fitted-off
201d8a31-e059-541f-a7dc-3e638b620821 | note | Fail=Missing, Pass=Complete
768379e9-5ac8-5d6c-9168-efd23450b506 | button | Areas not fitted-off - completed | Yes, No
| checkpoint | Client Sign Off Sheets Complete
| checkpoint | Painting carried out
| checkpoint | Pressure Tested (refer ITR 401) - Completed
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
c78964f1-4cd6-5270-9558-15c0c49bdc13 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
b0a55528-8942-598b-9eb1-ced28ae84dfd | button | Area left clean & tidy | Yes, No
0b1ff88a-e14e-52be-8250-4ed037b84d1f | tickbox | Leemark Sign-Off
b97fd727-cc11-517c-bd3b-9c4b7947da9d | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-30-ITR-301.1 Sprinkler Control Valve |  | LM-FOR-30-ITR-301.1 Sprinkler Control Valve | 9f9412ee-a4f2-4e98-b42e-f52886816162
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
63eae8b6-4db3-5755-8c22-4f910cfc456b | textbox | Drawing & Revision #
cfc6d0f8-9e2c-5dbd-ab40-e3084654de18 | tickbox | Area clear, tidy and accessible
55fcae69-bf4d-5e3c-9f91-8083f34f8342 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
| checkpoint | All supports are completely installed, spaced and bolted down box / assembly secured
| checkpoint | All roll grooved couplings / flanges are properly tightened
| checkpoint | Valve station drain is properly connected to risers drain and building hydraulic drainage
| checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
| checkpoint | All specific signage is installed lock shut / lock open including FSV number of M/V’s
| checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
| checkpoint | Correct type solenoid, flow switch, couplings etc installed
| checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
| checkpoint | Confirm GFA on solenoid activation/ flow switch/ MV activation
| checkpoint | Control Valve is positioned between 1150mm to 1800mm
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
413b9e40-01d4-5593-9c2c-908a2c419af4 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
c1a7b2bc-2eec-57c7-9469-626316ed584d | button | Area left clean & tidy | Yes, No
f1904748-7bb3-5423-bf4a-7fdabd166ea9 | tickbox | Leemark Sign-Off
df0af5be-4991-51bc-a377-c5d2a4300bab | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-30-ITR-301.2 Alarm Control Valve |  | LM-FOR-30-ITR-301.2 Alarm Control Valve | 6697f33b-66ac-4f2d-95be-2906fb39e344
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
e3cf3bd3-6e2a-57a0-805a-58f6e637fe70 | textbox | Drawing & Revision #
31daee6c-311b-5a94-acee-8508c8b48fb5 | tickbox | Area clear, tidy and accessible
53d79436-49e7-5856-a429-811da5898308 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
| checkpoint | All supports are completely installed, spaced and bolted down
| checkpoint | All roll grooved couplings / flanges are properly tightened
| checkpoint | Correct size and specification of Alarm Valve is installed in accordance with the approved drawing/plan
| checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
| checkpoint | Correct size of alarm line is installed, adequately supported and alarm gong is properly piped to drain
| checkpoint | Correct size of orifice is fitted and piped to drain when system is with retard chamber
| checkpoint | Main waste & test valve is fitted and piped to drain
| checkpoint | Correct type and model of Direct Brigade Alarm device is fitted
| checkpoint | Correct model and range of Pressure Switch is fitted
| checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
| checkpoint | All signalling devices (Monitored Stop Valve, DBA, Low Pressure Switch), are wired back to FIP
| checkpoint | Control Valve associated pipe works paint touch-up repair is completed
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
f95e0b10-d8d9-560d-abe9-3efc14231090 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
8439c4c1-a4fe-5d3d-8146-77d60391f331 | button | Area left clean & tidy | Yes, No
eca00539-7d4a-5d65-830a-9a0361c0820c | tickbox | Leemark Sign-Off
aa83bd7f-3dce-5320-97e6-05cc938bb076 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test |  | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test | 57d0dffe-0218-4b15-bcd4-89d60c5d7bf5
| section | Guidelines
| checkpoint | Guidelines understood - Pass once read
a4c68d39-4aa1-502d-8720-0028fa1b9a7a | note | Guidelines: Fire Sprinkler Systems – 1600kPa or 400kPa above the maximum static pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
2557f4ff-a9c5-5837-b5f0-f6ab3de565fb | note | Fire Hydrant Systems (Low Rise) – 1700kPa or 15 times the design pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
bb560cb1-0dad-5a28-8ad2-0810647c5812 | note | Fire Hydrant Systems (High Rise) – 1050kPa at the highest hydrant in the pressure stage being tested If pressure reading is being taken at the booster, determine the height difference in metres between the top hydrant and the booster and add 10kPa per metre of static pressure to this figure with a minimum test pressure of 1700kPa If in doubt please seek clarification from the Construction Supervisor or the Design Manager
| section | Rough In Only OR Rough In & Fit Off Together
| checkpoint | First Sighting - Pass once entered
801dbdfe-c273-5ee5-be62-6f4c647f5001 | textbox | Date
d73faad3-b770-5b06-a32b-3c5d4552a003 | textbox | Time
581682b4-cd9e-5a83-a961-4ca694e0ff1f | textbox | Pressure
fa356fe3-e4cf-529c-a66e-56312dc121ff | button | Photo(s) taken | Yes, No
2777f205-e525-50f1-bdcd-acd3a6bc7245 | button | Leemark Sign-Off - Attach below | Pass, Fail
17eea8ea-5b4c-5487-b428-0837caf89997 | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
| checkpoint | Second Sighting - Pass once entered
7970433a-c86e-5d1e-8dd7-477e8a6b61cb | textbox | Date
da78add1-0ff2-5e7f-9f30-e0c290db91c0 | textbox | Time
89d36721-2f5e-5bc5-a7e4-3c8e1958137c | textbox | Pressure
184d0cea-0cf1-5b85-8e05-6780e9926884 | button | Photo(s) taken | Yes, No
2e12dfd5-1a55-511e-9bb3-a1d363e67b61 | button | Leemark Sign-Off - Attach below | Pass, Fail
5aa044f4-bb22-5442-bf90-7fdf4d7e06bd | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
| section | Fit Off (if required ie if not covered by the above section)
| checkpoint | Subsequent Sighting - Pass once entered
be264ba9-c1c4-5ad2-84ab-14a07cbb7399 | textbox | Date
a07174b4-eb73-52b7-beac-2388bdeecc6c | textbox | Time
311b1850-7da4-5b6a-bec1-d0c54866f7b7 | textbox | Pressure
2954b052-9a96-55ba-beb0-3f60dba38d95 | button | Photo(s) taken | Yes, No
874dbd26-6c8c-5ae1-8f64-00693fe804c3 | button | Leemark Sign-Off - Attach below | Pass, Fail
f0717548-ff52-5ef4-9efe-57bc95c6d675 | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
fef67b80-09e7-5b11-88c1-1c4d9a2acd7f | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
8572316f-9f44-5f4d-9ebe-a1aa8f995ebe | button | Area left clean & tidy | Yes, No
c1d2be28-36ca-5022-9cfb-be4d83605ce6 | tickbox | Leemark Sign-Off
f33cc38b-e6aa-5579-b409-283fb1cd80f0 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-40-ITR-302.1 Fire Pump Installation |  | LM-FOR-40-ITR-302.1 Fire Pump Installation | f87f199d-2f08-47e7-8be2-981ebb86ede0
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
7ba988c4-1210-5056-9030-cbf3f4ef36de | textbox | Drawing & Revision #
5895aa87-e2aa-5d57-8786-040586a0955b | tickbox | Area clear, tidy and accessible
c81ac5a1-0324-5879-93cf-44cbf0d4b6e2 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Pump installation arrangement including suction and discharge pipe works are in accordance with the approved drawing/plan
| checkpoint | Pump clearance is 1000 mm on all four sides and 600 mm between pumps
| checkpoint | Concrete plinth/foundation height is minimum 150 mm from FFL and 150 mm wider on all four sides of pump base
| checkpoint | Pump base is sitting squarely and bolted down Vibration mounts are properly anchored on plinth or inertia plinth
| checkpoint | Pump suction and discharge pipework are completely installed and connected Supports are adequately provided
| checkpoint | Control panels installed and bolted down, MFB have clear access around pump controller 1000mm Arc
| checkpoint | Suction isolation valve installed is OS & Y type
| checkpoint | Non-return valve is installed and located upstream of the isolation valve in pump discharge line
| checkpoint | Pump circulation-relief valve for electric driven pump is installed and piped to drain or tank return line
| checkpoint | Heat exchanger cooling water harness for diesel driven pump is installed and piped to drain or tank return line
| checkpoint | Pressure gauge with gauge cock is installed min 2Ø downstream of discharge flange or reducer
| checkpoint | Pressure reductions installed on manifold x2 for each stage with M/V’s and Annubar for each stage
| checkpoint | Exhaust connected to pump and installed to approved discharge location
| checkpoint | Full tanks have been filled with Diesel; Electric Pumps AND Controls ready for energisation
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
a043cdf2-6f97-57e5-a4c7-0a29af97a6ce | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
73e8840c-8302-5f8b-b2f5-f4e0847470e4 | button | Area left clean & tidy | Yes, No
095172ec-d6f0-5e1a-ab1f-18289c0b96e2 | tickbox | Leemark Sign-Off
bb323f9b-d4c0-51e7-9f4c-d3dadcd36a61 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-40-ITR-302.2 Hydrant Installation |  | LM-FOR-40-ITR-302.2 Hydrant Installation | 609196ca-80f0-43dc-9726-997e4bf35cc1
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
cdd41034-ea2d-5ba7-9561-5cca67ba7a78 | textbox | Drawing & Revision #
ae91f4d7-e76a-524c-b787-8a7b81d1f4aa | tickbox | Area clear, tidy and accessible
4a781a3a-5731-56e3-976d-b9db0cad8997 | note | Attach Photos/Comments below if any issues & send report to Builder
ec5c5125-4bea-5694-9cf1-8b9207f44c84 | textbox | Hydrant No.
| checkpoint | Hydrant supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plan
| checkpoint | Hydrostatic pressure testing of installed supply pipe works completed and accepted
| checkpoint | Hydrant valves and associated pipes and fittings used are in accordance with the approved specifications and applicable codes/standards
| checkpoint | Fire Hydrant and associated fire water main isolation valves locations are in accordance with the approved drawing/plan
| checkpoint | Hydrants stand pipe is adequately supported and bolted down. Concrete surround block provided for external hydrant
| checkpoint | Hydrant valve is between 750 to 1200 mm from finish floor/grade level
| checkpoint | Valve outlet is facing away from the wall and not more than 35O below its horizontal axis. Minimum 300 mm clearance around the valve outlet
| checkpoint | Minimum 1000 mm clear space in front of valve outlet is provided
| checkpoint | Valve handwheel clearance is minimum 100 mm clear of any obstruction at fully open
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
e8ee2502-d6b5-5081-aee6-a70e0d39c72b | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
f46232f3-f028-5cd9-91ed-89c80964b0f3 | button | Area left clean & tidy | Yes, No
1aa5ca8e-5a39-5e16-b97f-407b5536fad3 | tickbox | Leemark Sign-Off
1d791761-cca4-5e58-9384-f6da145828f3 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-40-ITR-302.3 Hose Reel Installation |  | LM-FOR-40-ITR-302.3 Hose Reel Installation | 48447b43-3714-4f2f-b567-7b721185d414
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
beccd307-5e64-513d-be22-d0a82afd43dc | textbox | Drawing & Revision #
49527502-66c4-546d-9c79-451c625cf136 | tickbox | Area clear, tidy and accessible
c2d3e043-8b0c-5267-8263-c0b31080a3c9 | note | Attach Photos/Comments below if any issues & send report to Builder
4a7e9c81-d300-59ac-9cec-217ca7855fa3 | textbox | Hose Reel No.
| checkpoint | Hose Reel supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plans
| checkpoint | Hydrostatic pressure testing of installed pipe works completed and accepted
| checkpoint | Hose Reel and associated valves, pipes and fitting used are in accordance with the approved specifications and applicable codes/standards
| checkpoint | Hose Reel located along normal path of travel to nearest exit and readily accessible
| checkpoint | Verify and confirm hose length to be 36-metres or 40-meters
| checkpoint | Hose reel spindle is 1400 mm minimum to 2400 mm maximum above floor level. Stop valve is 1000 + 100 mm above floor level
| checkpoint | Minimum radial clearance of 100 mm between the reel rim and cabinet/cavity to the sides, above and below
| checkpoint | Minimum 100 mm clearance around the stop valve handwheel/handle
| checkpoint | Any defects found on the hose reel assembly have been corrected
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
035dd4b7-8868-5e99-b7a2-54d67698db42 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
6cd0001c-b2a8-5178-a18e-3265737fef86 | button | Area left clean & tidy | Yes, No
33ead7f9-a7d2-5d55-aba7-4def99bf4178 | tickbox | Leemark Sign-Off
0b2f874e-953f-58eb-897c-e3c6e5e8aa51 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-40-ITR-302.4 Tank Installation |  | LM-FOR-40-ITR-302.4 Tank Installation | 180daf0f-4655-4394-aac3-d034d84d2d76
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
ea817d6c-8a94-55fb-9d58-bec16ba87ffa | textbox | Drawing & Revision #
35172532-b69f-529b-bc37-ae4cdabb36b3 | tickbox | Area clear, tidy and accessible
605a0c9c-5bcd-50c4-9584-4c70b57d1396 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Tank installation/construction is completed including associated pipe works in accordance with the approved drawing/plan
| checkpoint | Tank is free from dents, buckling, cracks, and internal is clean and free of any debris and construction materials
| checkpoint | Tank internal liner (if provided) is complete and properly bonded to tank wall/shell
| checkpoint | Tank quick infill line including associated infill valve and isolation valve installed and adequately supported
| checkpoint | Tank suction isolation valve is fitted in the correct position and operational in accordance with the approved drawing/plan
| checkpoint | Tank suction vortex inhibitor is fitted in the correct position and elevation in accordance with the approved drawing/plan
| checkpoint | Tank overflow is fitted in the correct position, elevation and properly piped to drain Adequate drain available
| checkpoint | Tank drain/sludge isolation valve is fitted and blank off
| checkpoint | Tank external water level indicator is fitted and operational
| checkpoint | Tank internal and external access ladders are fitted & secured
| checkpoint | Tank access hatch is fitted and provided with lockable cover
| checkpoint | Ball float for infill pilot line is fixed tightly, close to the manhole and away from the discharge path of tank infill
| checkpoint | Tank is located with minimum of 600 mm clearance around tank perimeter and roof line
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
b60f143d-c07a-5068-bfed-9b4f46e59220 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
86c85bff-be0a-5094-a846-d2864f35143b | button | Area left clean & tidy | Yes, No
04a330a0-9f27-5ae7-8f8b-a8377944ebb2 | tickbox | Leemark Sign-Off
9d3b327b-b68f-5c5d-bea4-c1703bf409ca | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-40-ITR-302.5 Booster Assembly |  | LM-FOR-40-ITR-302.5 Booster Assembly | 693ad28a-1405-43ad-9b19-70a25704e0bb
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
02a046fc-2268-5eab-b905-10f082b2855d | textbox | Drawing & Revision #
4e595ccf-9bee-588e-bb0e-8c0ed5e1ff50 | tickbox | Area clear, tidy and accessible
cb69792d-9f95-51f4-9e24-c1885692a9a7 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | All pipework are installed in the correct position and alignment in accordance with the approved drawing/plan
| checkpoint | All pipework have been pressure tested and accepted in accordance to approved pressure testing procedure
| checkpoint | Fire Brigade Booster is located within sight of the main entrance to the building
| checkpoint | Concrete plinth provided for the booster location and hard stand for fire brigade pumping appliance
| checkpoint | Feed Hydrant is located within 8 metres from fire brigade appliance hard stand
| checkpoint | Fire water storage tank suction point (Storz) is located within 4 metres from fire brigade appliance hard stand
| checkpoint | Fire water storage tank suction point (Storz) is located within 10 metres from fire brigade booster inlet connection
| checkpoint | Centre distance between feed hydrant and booster inlet connection is 450 mm minimum and 5 m maximum
| checkpoint | The height of Feed Hydrant Outlet and Booster Inlet Connection is minimum 750 mm and maximum 1200 mm from FFL
| checkpoint | Valves face minimum 150-mm from door and valve handles are 100-mm from cabinet sides
| checkpoint | The number of feed hydrant outlet installed is equal to number of fire brigade booster assembly inlets
| checkpoint | The required number of fire brigade booster inlets installed is suitable for the system requirement or minimum of 2 inlets
| checkpoint | Full flow non-return valve of correct size is installed in the proper location
| checkpoint | Approved type of cabinet enclosure is installed as required
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
10d7b352-bdb3-51b8-82a9-a3efcadb8304 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
64cd79a9-19e8-5205-823a-a11b45096632 | button | Area left clean & tidy | Yes, No
35f5e669-b281-5bc1-b50d-5d6b277d2ff5 | tickbox | Leemark Sign-Off
dd5863b3-a96d-5963-8841-ad56e58cb9ca | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421) |  | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421) | fcc17755-0217-4dd7-afb8-a89a7108c3e8
| section | Fit-Off
| checkpoint | Latest consented drawings checked & referenced
4c9fe21e-c8ba-51af-a6b6-ac181799e0a2 | textbox | Drawing & Revision #
65489623-1de5-5a61-b65d-4e5e2e58ed84 | tickbox | Area clear, tidy and accessible
0ffeb54d-9e4b-5f30-aaf6-741352a3a878 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Have all devices been installed in the correct position with no obstructions
| checkpoint | Have all detectors been installed in the correct position and addressed
| checkpoint | Have all input/output modules been installed in the correct position and addressed, with all enclosures sealed
| checkpoint | Have all magnetic door holders been installed correctly
| checkpoint | Have all input/output devices been installed and addressed for security fire trips
| checkpoint | Have all input/output devices been installed and addressed for mechanical fire trips
| checkpoint | Have all input/output devices been installed and addressed for AS 1668 Fan Controls
| checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after fireworks
| checkpoint | Have all cables and conduits been installed in the correct position for devices
| checkpoint | Have all devices been terminated for testing purposes
| section | Cable Feeds
| checkpoint | Have all cable feeds been connected to the first device
| checkpoint | Have all cable feeds been connected to the last device
| checkpoint | Have cable feeds been connected at the panel
| section | Visual Check
| checkpoint | Check that no other services are run with or attached to fire detection cables
| checkpoint | Check that no cables have been damaged
| checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
| checkpoint | Check that all address tags and labels are clear and readable
| checkpoint | Have devices and address been noted on “As Constructed Drawings” for handover
| checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
| checkpoint | Has photographic evidence been taken and recorded for all penetrations?
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
8927abec-dd91-51be-8d95-92d6633174a5 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
ed02e78a-5e03-529f-ac61-96cabc61772c | button | Area left clean & tidy | Yes, No
961fc0c9-7527-55f3-b631-774419ecc963 | tickbox | Leemark Sign-Off
5c2fcbcb-a73c-53ba-897e-4bc87e64137e | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-50-ITR-303.1 Fire Panel Installation |  | LM-FOR-50-ITR-303.1 Fire Panel Installation | eb3dec30-6087-44a9-96f4-ae9811ff822a
| section | Fire Indicator Panel
| checkpoint | Latest consented drawings checked & referenced
2b520512-a6b4-5c00-86bf-eb1126185f22 | textbox | Drawing & Revision #
c882904c-e04d-50e0-8064-46401f748fc4 | tickbox | Area clear, tidy and accessible
23de8cb7-b93c-59b1-a97c-deecddf48499 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Are visual indicators and controls not less than 750 mm from the floor
| checkpoint | Are visual indicators and controls not more than 1850 mm from the floor
| checkpoint | Connected to Brigade - Is the fire indicator panel clearly visible and readily accessible within the designated building entry point or the fire control room
| checkpoint | Not Connected to Brigade - Is the fire indicator panel in a secure location and clearly visible and readily accessible to authorized personnel
| section | Accessibility
| checkpoint | Is the fire indicator panel obscured by a door (if No, continue to CLEARANCE)
| checkpoint | Is the door marked in a contrasting colour to the general colour scheme with the words “FIRE PANEL” in letters not less than 50mm high
| checkpoint | Is the door absent of locks
| checkpoint | Where the door reduces the CIE sounder sound level below the CIE requirement, means are provided to give the required sound level outside the covering door
| checkpoint | A minimum clearance is maintained from the enclosure as shown
| section | Power sources
| checkpoint | Is the battery enclosure located such that the batteries are readily accessible for inspection
| checkpoint | Are the connecting leads to the battery clearly labelled to reduce the possibility of reverse connections to the battery
| checkpoint | The battery is not be tapped for intermediate voltages
| checkpoint | All connections are made using suitable connectors
| section | Sub-Indicator Panels
| checkpoint | The SIP shall only serve areas on one level of a building unless - Pass once below considered
07f2ffb0-9149-5c18-978d-b55585b22705 | button | (a) The SIP serves the entire building | Yes, No, N/A
2d153f4b-45d2-549d-8158-6bc4c73c36e8 | button | (b) All zones connected to the SIP are readily accessible without leaving the area served by the SIP; or | Yes, No, N/A
809fd165-f75d-5ee4-8f2a-b417191b2f91 | button | (c) The location of each zone in alarm at the SIP can be identified at the designated building entry point | Yes, No, N/A
7913de1a-136c-503a-b07a-7b31b9f0a4a0 | button | Where the SIP serves the entire building, it shall be installed in accordance with the requirements for an FIP | Yes, No, N/A
3f7f4242-80d9-5e64-973e-12d50af04109 | button | If the SIP serves a specific area, is it located at the main point of entry into that area | Yes, No, N/A
| section | Wiring
| checkpoint | The extra low voltage wiring of the fire detection and alarm system is be kept separate and distinct from all other systems
| checkpoint | The extra low voltage wiring of the fire detection and alarm system is installed in accordance with the requirements of AS/ACIF S009
| checkpoint | Other wiring is installed in accordance with the electrical safety requirements of AS/NZS
| checkpoint | Externally energized circuits at voltages in excess of extra low voltage, except the power source for CIE, do not enter any CIE enclosure
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
ea0acfe0-0620-50fe-8edc-8e27a4361378 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
b7a2f552-c7ba-5013-ba95-948a2c20ae9f | button | Area left clean & tidy | Yes, No
d41a53f0-de19-5968-b69d-a214bfbc698e | tickbox | Leemark Sign-Off
ed2c61f9-ebb2-53a6-ac24-4f9cef3ba6ab | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-50-ITR-303.2 Ewis Installation |  | LM-FOR-50-ITR-303.2 Ewis Installation | 0980cc49-4c90-4171-a0ed-7ef6efa8a8e9
| section | Cabling
| checkpoint | Latest consented drawings checked & referenced
d784685c-39ef-5104-88b6-ee81f8727f95 | textbox | Drawing & Revision #
343f4623-c336-5e9d-bf30-0ebe50f11381 | tickbox | Area clear, tidy and accessible
88c8164b-14ff-5561-929b-c17b67f13306 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Have all cable supports been installed in the correct position with no obstructions
| checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
| checkpoint | Have all cables been installed for speakers and horns
| checkpoint | Have all cables been installed for warden intercom points
| checkpoint | Have all cables been installed for emergency call points
| checkpoint | Have all cables been installed for strobes
| checkpoint | Have all cables been installed for background music inputs
| checkpoint | Have all cables been installed for microphone inputs
| checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
| checkpoint | Have all cables been installed in the correct position for devices
| checkpoint | Have all cables been joined through for testing purposes or fitted with end of line devices
| section | Cable Feeds
| checkpoint | Have all cable supports been installed in the correct position with no obstructions
| checkpoint | Have all cable feeds been installed in the correct position
| checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
| checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
| checkpoint | Have the modified cable trays been re-galvanized
| section | Visual Check
| checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables
| checkpoint | Check that no cables have been damaged
| checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
| checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
| checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
| checkpoint | Has photographic evidence been taken and recorded for all penetrations
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
cf64f9ab-f4da-5cc9-8a3a-a1e77ba9815d | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
1c403649-4c9c-56ea-9f38-d9abe926b57f | button | Area left clean & tidy | Yes, No
38e89389-e703-5b74-b9c0-385a42d4009c | tickbox | Leemark Sign-Off
c074a16e-fd4d-5562-b567-7f2d94d90e09 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off |  | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off | ffefec09-7402-4c7c-9c7d-d588059664f2
| section | EWIS Fit-Off
| checkpoint | Latest consented drawings checked & referenced
0f762fc6-3578-589f-8764-0de9f526d416 | textbox | Drawing & Revision #
8b39662d-2ae1-5410-acad-8f11626a3716 | tickbox | Area clear, tidy and accessible
145487e6-0f19-57a4-8844-42ea0e1128f0 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Have all devices been installed in the correct position with no obstructions
| checkpoint | Have all speakers / horns been installed in the correct location
| checkpoint | Have all warden intercom points been installed in the correct location
| checkpoint | Have all emergency call points been installed in the correct location
| checkpoint | Have all strobes been installed in the correct location
| checkpoint | Have all background music points been installed in the correct location
| checkpoint | Have all microphone points been installed in the correct location
| checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after warning system works
| checkpoint | Have all cables and conduits been installed in the correct position for devices
| checkpoint | Have all devices been terminated for testing purposes
| section | Cable Feeds
| checkpoint | Have all cable supports been connected to the first device
| checkpoint | Have all end of lines been fitted and measured
| checkpoint | Have cables feeds been connected at the panel
| section | Visual Check
| checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables or devices
| checkpoint | Check that no cables or devices have been damaged
| checkpoint | Check that all final device locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
| checkpoint | Have devices and readings been noted on “As Constructed Drawings” for handover
| checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
| checkpoint | Has photographic evidence been taken and recorded for all penetrations
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
defdd847-4fe4-51a5-ab02-274e6763d8e1 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
8e906a06-a652-52e6-949c-7a3ddedaabe6 | button | Area left clean & tidy | Yes, No
0aeab7df-3e66-58aa-86e0-452b73cc1600 | tickbox | Leemark Sign-Off
cf6a6f08-f545-50a7-9b27-f51c35aea053 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-50-ITR-303.4 Fire Detection Installation |  | LM-FOR-50-ITR-303.4 Fire Detection Installation | 4600c5cb-9094-4ab3-8fb7-c6dbe2da7bf4
| section | Cabling
| checkpoint | Latest consented drawings checked & referenced
3489af05-1e7a-5ba7-a45e-4074fffe8913 | textbox | Drawing & Revision #
1b45522f-d8dd-55eb-9f03-723b3a6beceb | tickbox | Area clear, tidy and accessible
4134f3c9-86e9-50fb-a08f-0a350a67c10e | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Have all cable supports been installed in the correct position with no obstructions
| checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
| checkpoint | Have all cables been installed for detectors
| checkpoint | Have all cables been installed for sprinkler valve sets
| checkpoint | Have all cables been installed for magnetic door holders
| checkpoint | Have all cables been installed for security fire trips
| checkpoint | Have all cables been installed for mechanical fire trips
| checkpoint | Have all cables been installed for AS 1668 Fan Controls
| checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
| checkpoint | Have all cables been installed in the correct position for devices
| checkpoint | Have all cables been joined through for testing purposes
| section | Cable Feeds
| checkpoint | Have all cable supports been installed in the correct position with no obstructions
| checkpoint | Have all cable feeds been installed in the correct position
| checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
| checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
| checkpoint | Have the modified cable trays been re-galvanized
| section | Visual Check
| checkpoint | Check that no other services are run with or attached to fire detection cables
| checkpoint | Check that no cables have been damaged
| checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
| checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
| checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
| checkpoint | Has photographic evidence been taken and recorded for all penetrations?
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
17c08620-0641-5aa8-b682-e77d5db03c9f | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
19db9ac1-7b5a-5a08-861f-66ae374bcd8b | button | Area left clean & tidy | Yes, No
b14b24a8-74f5-589a-a49f-724059ce7686 | tickbox | Leemark Sign-Off
d7b910e2-eb4e-52fc-9651-24c79ef8b414 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-50-ITR-303.7 ASD (Aspirated) installation |  | LM-FOR-50-ITR-303.7 ASD (Aspirated) installation | 031c02dc-9d97-46f1-b182-d99bacc977f5
| section | ITR Pre Commissioning Procedures (1)
| checkpoint | Pre Commissioning Procedures
a721100d-feb7-52d6-9a33-dd60ad1c919c | button | Check the location of installation is as per approved shop drawings and manufactures recommendations | Yes, No, N/A
1228415a-6ec5-57b0-b567-077b3622c449 | button | Check the Height of Panel is as per manufactures recommendations and in accordance with the relevant Australian Standards | Yes, No, N/A
a90b3e8d-54e3-5857-923e-091e87520d7b | button | Confirm operation of auto-reset from FIP is wired through GP relay | Yes, No, N/A
e97ea414-b130-530b-98fb-6303810c2527 | button | Check all wiring connections are tight and secure | Yes, No, N/A
9a11b365-e2cd-5fdb-be76-681782321415 | button | Check routing of the conduits are as per approved shop Dwg’s | Yes, No, N/A
068655d9-eb4c-5295-ab40-cfbb564ff45a | button | Check joints are properly glued /sealed and bonded to eliminate any potential air leaks | Yes, No, N/A
192d0645-d4ec-50b0-8ac8-72425b2fd671 | button | Check pipe joints at the inlet ports of the scanner are not glued but firmly fitted into air inlet socket to ensure there is no potential air leaks | Yes, No, N/A
ef0c3400-fa7c-5b97-b8a5-ad0c3c9abe6f | button | Check the sensing holes are drilled as per design | Yes, No, N/A
0e9c5d1a-5704-559e-8289-0cb3a3fc58d4 | button | Confirm the exhaust has been routed back into the sampling space | Yes, No, N/A
64828f37-d819-5f23-a8a5-c7f91a5dff98 | button | Confirm end caps have been installed un-glued to all pipes at a serviceable height and location | Yes, No, N/A
aa43c225-2faf-5fcb-a87d-bf05e6570793 | button | Confirm wiring is complete to Action, Minor Urgent, Fault & Fire relays and monitored via the FIP/SHDCIE. | Yes, No, N/A
| section | ITR Pre Commissioning Procedures (2)
| checkpoint | Pre Commissioning Procedures
006a92b6-5e14-52f3-8e4a-04e0cd8df13e | button | Power up the system, the aspirator starts up and air is flowing out of exhaust port , LCD screen is operational. | Yes, No, N/A
2fdf6551-88bb-544d-8cd8-6fd74e0bb45b | button | Induce smoke into the furthest sampling point from the head end unit | Yes, No, N/A
651463bb-5375-591d-804f-dfd0ab9e8e32 | button | Check that a Fire signal is being transmitted to the FIP within 60s of smoke entering the VESDA pipe | Yes, No, N/A
42fdb065-f267-5759-b060-cb2a56f37f89 | button | Check the correct signals are being transmitted to the FIP via Action, Minor Urgent & Fire Relays correctly. | Yes, No, N/A
2a148fdc-0ee4-50ce-9e22-bbee5d2060cf | button | Remove the power from the VESDA and confirm Fault is received at the FIP | Yes, No, N/A
94616ee1-e4be-5e55-83f1-5da5c317dc56 | button | Check the fire signal is conveyed to the fire Alarm system and BMS, if required | Yes, No, N/A
df0438e5-263c-50d5-92c7-c447fb0e9bff | button | Check the transmission of signals to operate ancillary devices, if required. | Yes, No, N/A
73ec3508-d376-5de6-bc4b-7e079ee3066e | button | Record all baseline data as required. | Yes, No, N/A
| checklist | Water Mist Fire Protection System – AS 4587-1999 |  | Water Mist Fire Protection System – AS 4587-1999 | 724f9dc3-e038-4b63-9a35-7d8f6288775f
| section | Details
| checkpoint | Do the plans accurately illustrate the hazard configuration?
| checkpoint | Are all components of the system in compliance with AS4587-1999
| checkpoint | Check all flow calculations and verify that the containers, piping and operational equipment are installed and sized in accordance with the plans
| checkpoint | Are dimensions of unclosable openings in accordance with the plans?
| checkpoint | Check protected area for openings other than those in Item 4
| checkpoint | Does the nameplate data on storage containers correlate with the submitted details?
| checkpoint | Check quantity and mass of containers
| checkpoint | Check protected area volume
| checkpoint | Check need for and adequate provision of, post-fire ventilation
| checkpoint | Physically check the pipework. Are pipe joints sound and is pipework adequately secured?
| checkpoint | Ensure that storage containers are disconnected
| checkpoint | Perform a full functional check of system (by operation of detectors) noting correct auxiliary electrical shutdown function (e.g. .....) doors released, dampers shut, airhandlers shut down, etc. (see Note 1)
| checkpoint | Ensure that any non fire shutdown plant capable of affecting system performance is operating during the test
| checkpoint | Ensure system release(s) operates correctly (see Note 2)
| checkpoint | Activate each detector head or system in turn by employing heat, products of combustion, etc. Ensure each manual alarm point operates and transmits
| checkpoint | Ensure that the detection and control equipment complies with AS 1670 and AS 1603.4 with respect to configuration and operation
| checkpoint | Ensure that visual and audible alarms operate
| checkpoint | Ensure that each alarm registers on CIE and mimic panels, if any
| checkpoint | Check that air-handling plant shutdown relay is activated
| checkpoint | Where multiple alarms are required for system operation, ensure that first and subsequent level alarms operate, including audible and visual indications, auxiliary equipment, and gas release mechanisms, if installed
| checkpoint | Check that directional valves are fitted where required and ensure that they operate correctly
| checkpoint | Reset the system and check all manual release devices
| checkpoint | Reconnect storage containers. Ensure that all caps, plugs and locking pins are removed and that the system is left in an operable condition (see Note 3)