## Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Add Site Diary Checklist |  | Site Diary | 5194f6c2-9695-4b35-a8f6-579d757a342e
| checkpoint | Areas of work accessible for the day
e048d81c-b120-5201-90b9-737dc818e2c4 | dropdown | Day | Friday, Saturday, Sunday, Thursday, Tuesday, Wednesday,Monday
8b06ec40-8a3c-5890-8eef-2138d0007662 | textbox | Date
220bbcf8-26f5-50d0-8333-a92a92c45817 | textbox | Year
2ee2d4ff-2e7a-5a32-abbd-16864834758c | textbox | Number of workers on site
f718a78d-8c75-581f-8ecc-f206357c4ca1 | textbox | HSR on site today enter name
67e1eae6-6cc5-54f1-9e71-af2e0d4466a4 | textbox | First Aider on site today enter name
300a822f-3c8d-5eb4-ace2-997e233cf07a | textbox | Injury on site today enter name
| checkpoint | Work area 1 details entered
47c51389-20da-5ede-8014-b3d862ef3eaa | textbox | Area
be2d3209-4753-5610-ab16-ae8739025b3a | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
8e3893b8-ed2f-5026-a09c-93c5cb077f2f | textbox | Comments
| checkpoint-no-value | Work area 2 details entered
c3bf60c1-b562-5b80-a516-8f9ebd4704ed | textbox | Area
4be3a27e-4b3d-586a-b513-ceb15fc40bfe | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
c2b720eb-8138-59ab-8725-672f980b9236 | textbox | Comments
| checkpoint-no-value | Work area 3 details entered
67ba33fd-a2e8-519a-9718-9602c1c22c34 | textbox | Area
d67e8a5c-0701-5122-8469-a3f875979c90 | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
e0c6f448-ea66-5571-ab37-d4e5b00d7eba | textbox | Comments
| checkpoint-no-value | Work area 4 details entered
a65ca3a0-57ef-5fca-9a21-6c58979e77b1 | textbox | Area
228c593c-8c7b-556a-a358-a302692731ee | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
be73872c-40d0-5fe1-95e7-28fc71abd66b | textbox | Comments
| checkpoint-no-value | Work area 5 details entered
5c62749c-d156-5f1a-a0db-c1bfbf345bbe | textbox | Area
fb2b9525-bedc-5e79-8595-7d9e44168dbe | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
0f36562c-85d2-5c15-b10e-0e0351ca42a0 | textbox | Comments
| checkpoint-no-value | Work area 6 details entered
df45fc36-050d-52a7-b4de-4c3dfd8b7dc1 | textbox | Area
ce639f3d-bbb2-5e33-bfa7-831d0f7f3ce4 | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
7a39984c-f43a-5db8-bbb8-67cb3b46d3ad | textbox | Comments
| checkpoint-no-value | Work area 7 details entered
f56b01be-ce67-517e-9201-21fbb9da80c2 | textbox | Area
cd1edc93-5190-52b7-8b91-cd4940a807f6 | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
0ce609f8-0e23-570c-84bf-8d4ab1c5a902 | textbox | Other
| checkpoint-no-value | Work area 8 details entered
87fec433-1b39-5b0c-85ab-47b3724894e7 | textbox | Area
497f30d6-7d3e-567a-9fde-26ab4d0ca912 | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
64afa6dd-5e29-541b-8f7a-b3eefebb69ef | textbox | Comments
| checkpoint-no-value | Weather conditions entered
e4a9dd83-8a46-5d40-9016-ecdf1143b19f | dropdown | Conditions: | Hot, Overcast, Rain, Showers, Windy,Fine
c4eca12e-6581-575e-a282-008a28f85230 | textbox | Min temp predicted
9f6d3c08-4655-5cb2-a2ec-d500dc6aaf2c | textbox | Max temp predicted
| checkpoint-no-value | Delays from inclemency
f4baf749-c7b9-5264-82f9-225bad01bac5 | textbox | Total Hours of delay
c7cb66ed-53d5-5a5a-8876-a70cef304006 | dropdown | Conditions: | , Heat, Other trades, Windy,Rain
| checkpoint-no-value | Delays from Builders or Others
afcd53cc-c4ba-599f-8ce0-c3160cb74e57 | textbox | Total Hours of delay
c19fccf4-46f7-5cda-af3d-ffd8ba800343 | dropdown | Conditions: | Concreter, Crane, Earthworks, Other, PT, Safety, Scaffold, Steel fixer, Union,Builder
| checkpoint | Attach Specific site photos for respective day
| checklist | Additional Tasks - add as required |  | Additional Tasks - add as required | dcdf0275-dc3f-4263-878a-aa81f9eb97a3
| checkpoint | Details of additional tasks - comment below
| checklist | Additional Tasks Checklist |  | Additional Tasks Checklist | 82c9a56f-b6cf-480a-8a54-ef8a5ee12e27
| checkpoint | Details of additional tasks - comment below
| checklist | Daysheets (Labour & Materials) (V.180521) |  | Daysheets (Labour & Materials) | bd7bbac1-bd94-49d4-a820-b10083b092cd
| checkpoint | Daysheet Completed & Ready for Invoicing
931dd1e9-e6f7-5970-96bc-c5fb9280165b | textbox | Date
3bff79c6-0816-52cd-9e1f-63cee682347c | textbox | Project
fadd42ae-e4b2-55ca-840e-a83ee3ddce8b | textbox | Location
a3f6da3f-5df2-56d2-b92e-0f3d0d2589e6 | textbox | Workers Name (Add hours in brackets)
6d361e0f-2263-54e3-b3ca-3bda46ad2f47 | textbox | Material 1 (Quantity & Description)
e983444b-af8c-5726-bee7-c484318a6209 | textbox | Material 2 (Quantity & Description)
d7bdc89c-6dca-5cc2-8bf8-22fc1c0e86b9 | textbox | Material 3 (Quantity & Description)
509caee7-e268-5f5d-ad4b-0812134a7dcd | textbox | Material 4 (Quantity & Description)
6e9d09c8-8a97-5a17-9cdf-0c0915621169 | textbox | Material 5 (Quantity & Description)
c20aadcd-5e8c-5e28-a24b-24f5efd5259f | button | Reviewed by Leemark Supervisor | No,Yes
44ff8f03-db9b-5a6b-ace2-12ab20bcdcb2 | tickbox | Signature of Builder's Supervisor Added
| signoff | Signature Added - Click Here
| checklist | Defect / Issue to be rectified |  | ADD new defect / issue to be rectified [RENAME CHECKLIST TO LOCATION & DETAILS OF DEFECT] | 6cbd9a50-cfec-432f-b80a-1db719ea5e1e
| checkpoint | Upload photo of defect / issue to be rectified. Add comments if necessary.
| checkpoint | Has issue been rectified / defect been closed out? Upload photo
bab1d5a9-a3d7-58ff-a01f-4224a18aac6b | note | Only PASS once issue is rectified / defect is closed out
| checklist | Document Attachment ITP (V.220421) |  | Document Attachment ITP (V.220421) | 8e1ed19a-5fe0-4ae2-84be-43922151e6d2
| checkpoint | Documents/Drawings attached for reference - Pass once attached
| checklist | dry fire ITP |  | dry fire ITP | 35bf854b-388f-4655-a2f4-57b6804a24e1
| checkpoint | Does the Emergency Lighting system operate manually and automatically via the RFP? RECORD VIDEO OF OPERATION
| checkpoint | Have all cables been cable tied to roof trusses / catenary wire with no sagging or obstructions? INSERT PHOTO
| checkpoint | Have all Smoke Alarms been installed in bedrooms within 3m of bedhead? INSERT PHOTO
| checkpoint | Have all cables been installed for sprinkler valve sets and mechanically fixed inside cabinet? INSERT PHOTO
| checkpoint | Have all cables been installed for Door Strikes and tested to ensure correct operation on Smoke Detector & Sprinkler Alarm?
| checkpoint | Does the main entry strobe operate on Smoke Detector & Sprinkler Alarms? RECORD VIDEO OF OPERATION
| checkpoint | Do the audible alarms ring independently when the relative SCV is operated for that property? RECORD VIDEO OF OPERATION
| checkpoint | If ASE is installed, does the ASE only trigger upon receival of all Sprinkler Alarms and not on Smoke Detection?
| checkpoint | Does the Heating System shut down on activation of smoke detector or sprinkler and operate manually via RFP? RECORD VIDEO OF OPERATION
| checkpoint | Have the Block Plans been installed next to the RFP and match the current zones and detectors installed on site accurately? INSERT PHOTO
| checkpoint | Has all patching and painting been completed or booked in to be completed? INSERT PHOTO
| checkpoint | Have the As-Installed been left inside the RFP? INSERT PHOTO
| checkpoint | Is there a completed copy of the discharge test in the Emergency Lighting Logbook on top of the RFP, if applicable to project?
| checkpoint | Have the newly installed Emergency Lights been labelled, if applicable to project? INSERT PHOTO
| checkpoint | Is there a FIRE label installed above the strobes? INSERT PHOTO
| checkpoint | Have the Installers Statements been filled out in the back of the Manual in the RFP? ATTACH PHOTO OF ALL PAGES
| checklist | Handover ITP (V.200521) |  | Handover ITP (V.200521) | b58f62e3-c183-496d-ad8f-f394c51aaaac
| section | Design
| checkpoint | Shop Drawings - Pass once completed
8e21ed16-657f-5808-9a2f-13421c82ad58 | note | By: Drawing Office
28b99707-a4b3-587d-9d0a-b305861ce9e4 | note | Verification Criteria
f6b85a84-ae1b-5766-9d5e-90c7c935e409 | note | AS2118.1-1999 Automatic fire sprinkler systems - Part 1: General Requirements
fb3877ea-9760-5cbd-bb00-03f6d16cefc1 | note | AS2118.6-2012 Automatic fire sprinkler systems - Part 6: Combined sprinkler and hydrant systems in multistorey buildings
d077a0d0-f94d-51cd-bc95-e266cf3b51f1 | note | AS2419.1-2005 Fire Hydrant Installations - Part 1: System design, installation and commissioning
211256e5-5e05-5cbb-8454-2e2cdf12c3ca | note | AS2441-2005 Installation of Hosereels
5ddbcbdd-12d6-5883-bf61-1bd90a87116a | note | AS2941-2013 Fixed fire protection installations – Pumpset systems
58eefbad-460d-5c85-b4e9-07ac3e989c0d | note | AS 1670.1-2004 Fire detection, warning, control and intercom systems - System design, installation and commissioning
a4aa7c01-3d8d-5b30-9751-bc34b265b61b | note | AS 1670.4-2015 Fire detection warning control and intercom systems - System design installation and commissioning
5e436985-e0a4-5be1-8e2a-0dd78a6c9701 | note | Project specification (TBC - Once known comment below)
efdb4b77-cd10-53a7-bc5d-86e1505edb60 | note | .. ..
d68be9a8-07f2-5eee-aca9-17543b662a85 | note | Quality Control Method
7a7eadf7-0236-5e3e-b01f-d71ab706495f | button | HOLD POINT - Leemark add signature below | Yes, No, N/A
d3581721-4c25-5383-88fd-0956f24d1e1f | button | Approved by Project Manager | Yes, No, N/A
a87ccb3b-5773-5136-ab38-4c0ffd1b9204 | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
552d7f8f-0dcf-5220-a750-2122a72ddb15 | note | Records: Aconex
| checkpoint | Hydraulic Calculations - Pass once completed
3b732027-3d2d-57a6-a8ba-f40e942ed527 | note | By: Drawing Office
d789e3fb-d86a-5672-aaf2-c26652dd6ebd | note | Verification Criteria
9bd24c06-00df-55c5-9371-e83b6de1ed25 | note | AS2118.1-1999 Automatic fire sprinkler systems - Part 1: General Requirements
9471a8f0-01ed-5473-a879-88901371b10f | note | AS2118.6-2012 Automatic fire sprinkler systems - Part 6: Combined sprinkler and hydrant systems in multistorey buildings
16ce0911-6e4b-5b16-b614-3971656d6f06 | note | AS2419.1-2005 Fire Hydrant Installations - Part 1: System design, installation and commissioning
f5674146-a754-5202-962e-d9cc6e96a323 | note | AS2441-2005 Installation of Hosereels
6a6146a3-65d4-591f-bf20-bd8787a8ab41 | note | AS2941-2013 Fixed fire protection installations – Pumpset systems
c0b4cf60-49f3-5b0c-bad8-7eb37b206ea2 | note | Latest revision FER. (TBC - Once known comment below)
c8073585-e0d6-5387-8e12-80815a83f27b | note | Project specification. (TBC - Once known comment below)
843c58b3-b3d3-5a7c-bd63-53992a052973 | note | Quality Control Method
333fead2-b9db-5d2d-addb-c9040544d004 | button | HOLD POINT - Leemark add signature below | Yes, No, N/A
f660ea01-0d4d-5d04-8362-b2aa3f66e157 | button | Approved by Project Manager | Yes, No, N/A
6cd29afd-07c7-57c1-9ea6-e37174e27763 | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
6a42ca05-52cd-560c-b588-b0ed59818902 | note | Records: Aconex
| checkpoint | Samples - Pass once completed
7a4c57e4-8827-547a-9f87-9d4ab95479e2 | note | By: Drawing Office
65ee3464-7a5d-59fa-90f1-8809f3ac97f9 | note | Verification Criteria: Part C.1 Samples & Details Part C.8 Fire Sprinkler System Part C.9 Fire Hydrant Pipe
742055d2-08d3-5256-a7ec-0c149cac637f | note | Quality Control Method
b7095eb4-2176-57eb-a042-6870088b4122 | button | HOLD POINT - Leemark add signature below | Yes, No, N/A
1d64f07c-422e-5c72-8fd4-aa7e32b8f2ad | button | Approved by Project Manager | Yes, No, N/A
751bf811-12f9-52a1-af17-86cba1ed4909 | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
f0a98a23-19ab-58f3-9db1-db1f04b98d7d | note | Records: Aconex
| section | Offsite Manufacture
| checkpoint | Pipework Fabrication - Pass once completed
18b0f321-bd67-57aa-a437-f6e21cc57721 | note | By: CWS
e35a2910-2f84-55aa-b9e4-4a161122163e | note | Verification Criteria: C.12 Pipework & Fittings
fe78dcfb-38de-515c-830c-6c3677a93f09 | note | Quality Control Method
b29069a1-5806-5656-957a-89d0c26dafa8 | button | Leemark Inspection Completed | Yes, No, N/A
5f543120-8fbd-506d-a6e3-3e745d2a3d95 | note | Records: CWS/ITR
| section | Installation
| checkpoint | Sprinkler - Pass once completed
1c56aecc-a6e8-5ee8-a9a7-ef8a0264e2a4 | note | By: Sprinkler Fitters
a37fd250-e671-5161-90aa-ffb57684311d | note | Verification Criteria: Part C.8 Fire Sprinkler System AS2118, 4118
16c3ecd9-9cff-5079-b0cb-fd963329c54b | note | Quality Control Method
b37d257a-b773-56a0-872e-e90b408e5eb9 | button | Leemark Inspection Completed | Yes, No, N/A
2ed5abf4-f895-523e-8a1f-b55a22853a97 | button | Witnessed by Project Manager | Yes, No, N/A
241fe270-051b-509b-b53e-bcd78008c049 | note | Records: Inspection & Test Record, 301/301.1 & 301.2
| checkpoint | Hydrant & hose Reels - Pass once completed
19230c38-871a-5008-9546-51b901d84191 | note | By: Sprinkler Fitters
50aca357-c828-5c05-b65a-d667bcb5f52e | note | Verification Criteria: Part C.9 Fire Hydrant Pipe & Hose Reel Installations AS2419.1/.2/.3 & 2441
5ff5129d-708f-565f-bf14-47edfe5b4c04 | note | Quality Control Method
a90ebfb4-63f8-56fa-913c-373984ee03aa | button | Leemark Inspection Completed | Yes, No, N/A
ff9469c9-6a09-57e6-8534-faa0e110e069 | button | Witnessed by Project Manager | Yes, No, N/A
4826fd02-592c-5945-95ae-62afc80884ee | note | Records: Inspection & Test Record, 302.2/302.3 & 302.4
| checkpoint | Alarms / EWIS - Pass once completed
fa104792-de17-57a5-ae83-ba1d0ffce0c3 | note | By: Fire Alarm Technicians
31d71fa6-c976-59e8-847e-a04cf5cde391 | note | Verification Criteria: Part B.12 Fire Detection & Alarm Installation, Part B.13 Emergency Warning & Intercommunication System AS1670
4698edf5-59e5-5e23-9d92-86dbc7bda5c7 | note | Quality Control Method
e1dcdcbd-46ad-5b23-8749-9f646a89c12e | button | Leemark Inspection Completed | Yes, No, N/A
485d7468-674a-5fea-894d-4834f02a1b71 | button | Witnessed by Project Manager | Yes, No, N/A
d658b17d-2dd9-5c3d-8e63-20f0a1329f6c | note | Records: Inspection & Test Record, 303.1 / 303.2 / 303.3 / 303.4 / 303.5
| section | Commissioning
| checkpoint | Hydrostatic Tests - Pass once completed
0bd86e47-5d8d-5980-ae1d-40c6c9797613 | note | By: Sprinkler Fitters
e33fceaf-6b67-5b77-84ee-e14899539ec1 | note | Verification Criteria: AS2118, 4118, 2419, 2441, 2941
3ab15ca4-7bf5-5cfb-a7dc-d6ec364d4e09 | note | Quality Control Method
370a6403-895b-51e9-86ae-095fbbe28f5f | button | Leemark Inspection Completed | Yes, No, N/A
d70dee45-343a-5f4c-8577-a363bc678c7f | button | Witnessed by Project Manager | Yes, No, N/A
a54bff67-684d-5d19-9295-10d96af0b889 | note | Records: Inspection & Test Record, 401
| checkpoint | Sprinkler Inspection - Pass once completed
87a429a0-e143-5c8e-9b50-849da90636da | note | By: Fire Safety Victoria
c7aaae11-5559-5256-a13f-0b51a54d2f59 | note | Verification Criteria: AS2118.1, AS2118.6
ebc353e6-4a18-56d1-bfec-3ae52a45bb0c | note | Quality Control Method
32149feb-02d1-5f1d-93f4-84ff3c6a5373 | button | Witnessed by Project Manager | Yes, No, N/A
63fbe6e7-9ee0-5dc3-a900-1d26e41895ce | note | Records: Certificate issued - Attached below as applicable
| checkpoint | Hydrant Inspection - Pass once completed
4e5520e0-8737-5ea4-8831-0f8404823ba2 | note | By: Victorian Hydrant Test & Plumbing
b574b2ab-65af-5054-909d-2c4c074fdeaa | note | Verification Criteria: AS2419, AS2118.6
26ccbada-d706-5ce4-908b-6991163c3e10 | note | Quality Control Method
c15638e3-3311-572f-88c1-bafe2716c186 | button | Witnessed by Project Manager | Yes, No, N/A
465ecdf7-3360-55ba-aa6b-095892e7c9c5 | note | Records: Certificate issued - Attached below as applicable
| checkpoint | Alarms / EWIS Inspection - Pass once completed
0662f9ec-7cb7-5708-87ad-5d720cbe4f1d | note | By: Fire Safety Victoria
0890b115-7270-5c9f-bf30-f48791ee9f3d | note | Verification Criteria: AS1670
d8877a42-1341-5694-a9b4-23a74d09f4d5 | note | Quality Control Method
06adcd4a-9629-5422-95a1-07cff1f00c03 | button | Witnessed by Project Manager | Yes, No, N/A
902eba8e-4707-5bb9-ad7f-42c00bd7c7ee | note | Records: Certificate issued - Attached below as applicable
| section | Completion
| checkpoint | As Installed drawings - Pass once completed
607fdf1d-8c12-5e15-9d63-4f70f007bb5d | note | By: Drawing Office
6c36bd21-564e-507d-afab-4ea75e3fbdde | note | Verification Criteria: AS2118.1, AS2118.6, AS1670
63736753-55a5-502a-acdd-1e7e2b7a5dc4 | note | Quality Control Method
8aaa2b52-7d0c-501b-ba53-8b4641f07720 | button | Document Submitted by Leemark | Yes, No, N/A
67232538-6f08-59c6-a148-8b432945680b | button | Approved by Project Manager | Yes, No, N/A
f9092ec3-8f25-5db2-a647-3d9a9a27050d | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
a02c682b-12dc-5f37-ac81-95afa517d633 | note | Records: Operation & Maintenance Manual - Attached below as applicable
| checkpoint | Manuals - Pass once completed
b7066152-a2f3-5428-a732-3a136e51c0dd | note | By: Drawing Office
7e47c988-f492-5d83-bb74-dff9f900fae4 | note | Verification Criteria: As per SOW
e2d81918-4ca4-5303-8550-7e6702ec2935 | note | Quality Control Method
34c275e8-7a02-59bd-a4ca-b4c378160c6e | button | Document Submitted by Leemark | Yes, No, N/A
2d41cd87-85cb-5bdd-9ec5-9100891f0a75 | button | Approved by Project Manager | Yes, No, N/A
d0905132-a5d6-5673-bbc5-f8c2003ea3b7 | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
3af63e93-ca29-5aa8-9856-a4818fc27076 | note | Records: Operation & Maintenance Manual - Attached below as applicable
| checkpoint | Test Data - Pass once completed
cb5ecc93-db21-590f-8120-aec4daf10569 | note | By: Site Foreman
b67e3f3f-f859-590b-b8ea-a4b3eb806ebd | note | Verification Criteria: Refer Commissioning part of this plan
d562f040-4326-51b0-8d1a-de482abddb3f | note | Records: Operation & Maintenance Manual - Attached below as applicable
| checklist | ITP/R Test Report Gaseous Suppression System (V.240521) |  | ITP/R Test Report Gaseous Suppression System (V.240521) | ed3527e7-2328-4bb3-afc8-07b67c84386f
| section | Installation Testing
| checkpoint | Latest consented drawings checked & referenced
5b57104a-56ba-51d5-b12e-af6d3a39ab81 | textbox | Drawing & Revision #
12aaa62d-0712-5e8a-a640-edbbf967e0dc | tickbox | Area clear, tidy and accessible
23252166-ad43-598c-8da1-5691b7e8cfc0 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Verify correct type, spacing and elevation of installed pipe supports and hangers
3435241f-b220-59d2-aadf-6585efaed6a5 | note | Acceptance Criteria: Installed to Approved Drawings
| checkpoint | Installation inspection of pipes and nozzle droppers/risers
542d335f-8de6-539e-a048-28fd509f974b | note | Acceptance Criteria: Installed to Approved Drawings
| checkpoint | All dirt traps must be capped and all pops temporarily plugged
1843a944-d0a3-53e9-a4de-9e4003b16833 | note | Acceptance Criteria: Installed to Approved Drawings
| checkpoint | Perform Pneumatic leak test of pipework in accordance with approved Test procedure and SWMS. Gradually apply pressure increments of 100 kPa for 15 minute holds
75c9d4e2-45a2-58b5-aa09-5c915b126a43 | note | Acceptance Criteria: Pressure drop should not exceed 20% of 300 kPa for 10-mins
| section | Installation of Cylinders, Manifolds, Valves, Actuation, Discharge Hoses & Nozzles
| checkpoint | Cycinders shall be adequately mounted and suitably supported according to approved installation plan
aa22c2ae-93a6-5d24-bc9f-44e5f0be8676 | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 8.2.3.12a
| checkpoint | Discharge manifolds and valves shall be mounted and adequately supported
e8534040-8f74-5e49-959f-e12e987a0479 | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 6.3.4
| checkpoint | Adequate quantity, correct code and location of discharge nozzles shall be installed according to approved plan
b97526e1-822a-54d6-aed0-3285e90debd4 | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 6.3.6.1
| checkpoint | Detection, actuation, alarm and control systems shall be installed and tested by “DRY FIRE” contractor in accordance to relevant code/standards
39174192-d228-595d-a30d-cd9d126f605e | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 6.4.1
| section | Enclosure Integrity Pre-Test Inspection
| checkpoint | Client to confirm that all services penetrations and/or openings are sealed prior to the test
6f5c9a97-2e78-51c4-ae8d-3cf28109ef09 | note | Acceptance Criteria: Builder Approval (Click to add signature Sign-Off below as required)
| checkpoint | Client to confirm that all HVAC fire rated dampers including OPR Damper can be closed prior to the test
aa7eb933-acac-5091-9a4f-b6e4269e891b | note | Acceptance Criteria: Builder Approval (Click to add signature Sign-Off below as required)
| section | Enclosure Integrity Test
| checkpoint | Perform both pressurization and depressurization fan test of the room and using the software program, confirm that holding time is equal or more than the required 10 minutes
8ce1445d-1196-5a03-b031-0a786432012e | note | Acceptance Criteria: Relief Damper Installed is sufficient
| checkpoint | Prepare full test report of each enclosure demonstrating the level of compliance achieved
72652afe-e74e-5d90-bd70-a9c9b4affce8 | note | Enclosure PASSED the hold time & venting requirements
| section | System Commissioning and Acceptance
| checkpoint | Prior to start of any test, ensure all extinguishant storage container release mechanism are disabled or removed
a0e7bfe8-c841-553b-af8a-7aea46ce4a73 | note | Acceptance Criteria: Release Mechanism Isolated
| checkpoint | Verify and confirm compliance to the approved design of distribution piping system, discharge nozzle sizes & orientations, storage containers quantity & locations and warning signs & notices locations
be2e11ae-6ff3-5f4b-b4b8-d07a8dbd058b | note | Acceptance Criteria: Installed to Approved Drawings
| checkpoint | With the operation of fire alarm system, verify and confirm operation of audible & visual alarms, plant shutdown interface, time delay & release mechanism activation/30s time delay / solenoid operated/ audible visual Alarm
fcea09e4-5a0c-5833-a116-97177ea97a74 | note | Acceptance Criteria: 30s time delay, solenoid operated , Audible/visual alarm operated
| checkpoint | Simulate discharge pressure switch operation and confirm gas released alarm indication at Fire Suppression Panel
1f8c18df-932c-5b59-b8e3-5fa748928795 | note | Acceptance Criteria: Indication at FIP
| checkpoint | After completion of system functional test, reset and reconnect all release mechanism onto storage container and return the system to full service condition
a53b1919-079c-5258-b7ce-ff36c88ff5b5 | note | Acceptance Criteria: Builder Approval (Click to add signature Sign-Off below as required)
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
f4684c11-06d7-5996-beba-eb3b991d6f3c | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
438736fc-6c03-5609-981a-307ed92d542f | button | Area left clean & tidy | Yes, No
c67616bc-ad4e-5162-a6f0-0c309b2170ed | tickbox | Leemark Sign-Off
e5c9317c-7180-57ff-a410-52bceb7f086f | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | ITP/R Test Report Pre-Action System (V.260521) |  | ITP/R Test Report Pre-Action System (V.260521) | 6d60f2e4-84c4-4a7c-9d05-412824028a43
| section | Installation Testing
| checkpoint | Latest consented drawings checked & referenced
844133e1-871d-52b9-9d9c-32bfa558ff44 | textbox | Drawing & Revision #
c38cc06b-4b78-5dac-ba2c-3f3aad3791fc | tickbox | Area clear, tidy and accessible
bb2d8abc-584e-5a44-aaad-6155d904c901 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Verify correct type, spacing and elevation of installed pipe supports and hangers
38886f8a-c065-5528-b142-28785172315f | note | Acceptance Criteria: Installed to Approved Drawings
| checkpoint | Installation inspection of trunk mains and range pipes
e1e2f940-7c79-55da-8172-cc614c2d3e6e | note | Acceptance Criteria: Installed to Approved Drawings
| checkpoint | All dirt traps must be capped and all pops temporarily plugged
3cf273de-5bd1-5447-ae9c-4eb8eabfe8b1 | note | Acceptance Criteria: Installed to Approved Drawings
| checkpoint | Inspection of installed sprinkler heads & baffle plates and flexible droppers
03208669-ef9f-5f19-941d-06c5d48ce641 | note | Acceptance Criteria: Installed to A.S 2118.1
| checkpoint | Perform Pneumatic leak test of pipework to ensure no loose joints or open pipe ends
04ad91d3-2786-52c3-9224-de413b86db00 | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 7.9.4
| checkpoint | Perform Hydrostatic Testing of pipework. Gradually apply pressure increments of 500 kPa for 15 minute holds until test pressure of 1400 kPa or 400 kPa above maximum static working pressure of the system is achieved and hold for 2-hours
462c1fee-beba-50f7-ae5d-6653beee28b6 | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 7.9.4
| section | Installation of Pre-Action Valve Sets & Ancillary Equipment
| checkpoint | Installation inspection of pre-action valve sets and ancillary equipment to ensure completeness, correct location, mounting
266bfe91-646f-5a78-9c3f-12dc83cd22c3 | note | Acceptance Criteria: AS 2118.1-1999 Clause 8.1
| checkpoint | Verify installation of alarm devices (e.g. DBA pressure/flow switch, low pressure switch) and solenoid valve for correct type and rating and proper interface connections to Fire Indicator Panel (FIP)
2969bb73-a1f2-53f4-866f-b3d19633b7da | note | Acceptance Criteria: Refer AS 2118.1-1999 Clause 8.10.1
| section | System Commissioning
| checkpoint | Perform a trip test on each pre-action valve by opening the alarm test ball valve and check operation of water motor alarm. Confirm operation of DBA pressure switch with correct indication at fire indicator panel
53aa6cf2-4942-5001-bb0e-816e85d86493 | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 15.4b, DBA -3 mins
| checkpoint | Initiate single or double interlock release activation and check operation of water motor alarm, DBA pressure switch and correct indication at fire indicator panel
b3b2b578-4e01-5610-8d7e-abfb49faeaca | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 15.4b, operational confrimation
| checkpoint | Record cut-in / cut-out pressure of air supply compressor and time to recharge the system pressure
8d13ae0d-2149-5847-9d52-fdbb9108a410 | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 15.4b, Time to recharge 30 mins
| checkpoint | Reinstate system and ensure valves are secured in its intended position, alarm and monitoring devices are in operational mode and system in ready to operate condition
9f01d373-0f6e-5f02-bc77-1c6ff9035e2c | note | Acceptance Criteria: AS 2118.1-2006Clause 15.6
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
a2dfd634-dbf3-57c8-9472-610c95428b57 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
481ec145-987c-596f-89ad-62c19ee25ddc | button | Area left clean & tidy | Yes, No
5288f8ea-689d-5b0f-bfee-44bc576c23a6 | tickbox | Leemark Sign-Off
beef6ff2-2bfc-54e8-b6c4-9250f968e97e | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-026 Penetration Installation |  | LM-FOR-026 Penetration Installation | 8b616245-8cd3-4ab4-b4e8-c3f336fe2674
| checkpoint | Latest consented drawings checked & referenced
81eb179b-f128-5570-8671-d7df13741f98 | textbox | Drawing & Revision #
33c10a2a-7565-55ae-b257-71be0178a1c9 | tickbox | Area clear, tidy and accessible
f57942fe-71cd-533e-873e-fdda4f24dd75 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Peno sleeve as per drawings - Please attach photos
| checkpoint | Peno sleeve as per drawings - Pass once completed and photographed
f88f95e3-b7ac-5ce9-9f0c-e32fa4826400 | textbox | Area (State area's worked in)
15a0b65e-81dc-5bbb-a85d-d3df5262e7f5 | dropdown | Substrate type | Concrete, Blockwork, Single layer of Plasterboard, Double layer of Plasterboard, Other (Specified below)
46e1383d-7866-5083-acae-724e7f40905b | textbox | Substrate type - if other (specify here)
469e0eb7-dc72-584a-996a-04b6aec765d6 | dropdown | Penetration type | PvC Pipework, Pex Pipe (HW/CW), Gas Pipe, Copper Pipe, Other (Specified below)
afb4f858-80db-5853-a8d9-44d30bd7b512 | textbox | Penetration type - if other (specify here)
f0da4e0a-ad3f-5f2a-b909-217fd8bae6b8 | dropdown | System Used | TBC w/CONQA, Other (Specified Below)
32bf7186-4238-570d-854c-8495494203bb | textbox | System Used - if other (specify here)
fdef9b94-2484-596b-ac0f-d4a8c9800035 | button | Labelled Attached | Yes, No
99fd04b4-9b31-5a5c-9ced-bbe6e5b63a18 | button | Attach photo(s) when complete | Yes, No
| checkpoint | Passive fire elements completed to specification/drawings & Area left clean/tidy
977b57a5-db8c-5d17-99e5-889fa1176689 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| checklist | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff |  | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff (V.171121) | d5ed2ae6-3b26-4a27-902d-9ba8cfd3be29
| section | Sprinkler Rough-In
| checkpoint | Latest consented drawings checked & referenced
664cb6f6-2306-552e-bf48-ae5351af600a | textbox | Drawing & Revision #
e5c07ca7-84ac-5c90-a48b-f59df54ae693 | tickbox | Area clear, tidy and accessible
9a6be319-4e3c-5ad8-8bff-6ec65b722680 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Supports spacing & fixing as per AS2118
| checkpoint | Pipework installed as per drawings
| checkpoint | Concealed space sprinklers installed
| checkpoint | All ends blanked off/plugged for testing
| checkpoint | Pipes left out
b1d15198-6c7c-5c4e-b4b1-d6fe411cb10f | note | Fail=Missing, Pass=Complete
d0d2d4c7-4017-52fb-b22c-113fa803d05b | button | Pipes left out - installed | Yes, No
| section | Sprinkler Fit-Off
| checkpoint | Latest consented drawings checked & referenced
b2a32d07-0e44-5883-b573-8650614c9a55 | textbox | Drawing & Revision #
5079c10d-7a6b-5395-ad4c-661e3f78c553 | tickbox | Area clear, tidy and accessible
656e2bcd-eabc-5451-a318-8c8c20961645 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Ceiling grid levelled
| checkpoint | Sprinklers installed as per drawings
| checkpoint | Sprinkler Type & temperature as per drawings
| checkpoint | All escutcheon plates installed
| checkpoint | Areas not fitted-off
7e2aa04b-a876-502f-8e9a-f8e4a8c2fe59 | note | Fail=Missing, Pass=Complete
70ca937b-d811-5e52-8c58-3e8709187611 | button | Areas not fitted-off - completed | Yes, No
| checkpoint | Client Sign Off Sheets Complete
| checkpoint | Painting carried out
| checkpoint | Pressure Tested (refer ITR 401) - Completed
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
8fbaaa0a-8c79-5691-835e-7694661b855e | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
4acbb0b3-01a3-577d-94fb-0c84ac58ba00 | button | Area left clean & tidy | Yes, No
d45072ab-879c-52bb-8bab-d23e9114cac0 | tickbox | Leemark Sign-Off
29eea887-ec22-540d-b7a5-6511d0239e0a | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-30-ITR-301.1 Sprinkler Control Valve (V.171121) |  | LM-FOR-30-ITR-301.1 Sprinkler Control Valve (V.171121) | a2fd6e92-d2b0-4502-b100-367c56bf2dcb
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
031996a9-5d4f-5ceb-a05c-d8365c194211 | textbox | Drawing & Revision #
2327840a-ae01-5bd1-96ad-738c537c5246 | tickbox | Area clear, tidy and accessible
5e5107b3-940d-5e72-bd1d-78ddd02f34da | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
| checkpoint | All supports are completely installed, spaced and bolted down box / assembly secured
| checkpoint | All roll grooved couplings / flanges are properly tightened
| checkpoint | Valve station drain is properly connected to risers drain and building hydraulic drainage
| checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
| checkpoint | All specific signage is installed lock shut / lock open including FSV number of M/V’s
| checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
| checkpoint | Correct type solenoid, flow switch, couplings etc installed
| checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
| checkpoint | Confirm GFA on solenoid activation/ flow switch/ MV activation
| checkpoint | Control Valve is positioned between 1150mm to 1800mm
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
a61dbf31-a0c8-5b28-8cce-751e746f97a1 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
e5dc7dfb-b9b4-5125-bb46-5f6919da65f8 | button | Area left clean & tidy | Yes, No
33d1eee0-6c9b-5deb-8d0c-ad4f072cd0aa | tickbox | Leemark Sign-Off
985819f1-a936-54b0-b1d2-6b3ac938e0c0 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-30-ITR-301.2 Alarm Control Valve (V.171121) |  | LM-FOR-30-ITR-301.2 Alarm Control Valve (V.171121) | b01f6875-19f6-4c9c-ab8f-1d1ba9b160c3
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
e2f7c154-fda3-5cad-86cd-a57bb1515507 | textbox | Drawing & Revision #
45abe4ce-ae72-53e7-a85d-6fd29f936516 | tickbox | Area clear, tidy and accessible
750da21c-329e-539a-a558-bf05fb7ce134 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
| checkpoint | All supports are completely installed, spaced and bolted down
| checkpoint | All roll grooved couplings / flanges are properly tightened
| checkpoint | Correct size and specification of Alarm Valve is installed in accordance with the approved drawing/plan
| checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
| checkpoint | Correct size of alarm line is installed, adequately supported and alarm gong is properly piped to drain
| checkpoint | Correct size of orifice is fitted and piped to drain when system is with retard chamber
| checkpoint | Main waste & test valve is fitted and piped to drain
| checkpoint | Correct type and model of Direct Brigade Alarm device is fitted
| checkpoint | Correct model and range of Pressure Switch is fitted
| checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
| checkpoint | All signalling devices (Monitored Stop Valve, DBA, Low Pressure Switch), are wired back to FIP
| checkpoint | Control Valve associated pipe works paint touch-up repair is completed
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
f84b20c7-dfc2-5955-9a40-f5ede67c0b5c | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
78b69c8f-adee-5d4b-a693-7550d7ee511a | button | Area left clean & tidy | Yes, No
e940673d-7010-5827-9abd-770524b7880c | tickbox | Leemark Sign-Off
c474c6c4-4d90-5af3-802b-9682d91c97e1 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test (V.171121) |  | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test (V.171121) | 49c4b18b-d8f0-4cdc-9d9d-1a19637371fa
| section | Guidelines
| checkpoint | Guidelines understood - Pass once read
7675f4a0-6f97-5ff3-8625-7be43d797ab1 | note | Guidelines: Fire Sprinkler Systems – –AS:2118.1 2017- 1600kPa or 400kPa above the maximum static pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
7fee6fd4-9e1e-5f6c-b207-dee603acb662 | note | Fire Hydrant Systems (Low Rise) – 1700kPa or 15 times the design pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
9f17401b-a3a7-5199-b88c-7abab99c1fc7 | note | Fire Hydrant Systems (High Rise) – 1050kPa at the highest hydrant in the pressure stage being tested If pressure reading is being taken at the booster, determine the height difference in metres between the top hydrant and the booster and add 10kPa per metre of static pressure to this figure with a minimum test pressure of 1700kPa If in doubt please seek clarification from the Construction Supervisor or the Design Manager
| section | Rough In Only OR Rough In & Fit Off Together
| checkpoint | First Sighting - Pass once entered
e17bdab2-119b-5951-9321-805d6dada841 | textbox | Date
352032bf-57ec-565f-bea0-6ee87938a765 | textbox | Time
08ba1a84-3609-5cbf-b4b7-5e66901a8453 | textbox | Pressure
1975a0a3-87ee-5f43-8395-0515fa7874f2 | button | Photo(s) taken | Yes, No
3c7ae15f-4045-5fd3-b1fd-82deceafc178 | button | Leemark Sign-Off - Attach below | Pass, Fail
0332dac3-cc52-526b-bf89-867d71728029 | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
| checkpoint | Second Sighting - Pass once entered
82278996-59d9-5ca6-905a-71de12925bcc | textbox | Date
d894402c-1a77-5d80-abb7-9620bac740ee | textbox | Time
147160b8-0c3f-5b54-9eff-b001657cebb8 | textbox | Pressure
972fa139-c80f-5e94-8b85-3ef6bbb3ef04 | button | Photo(s) taken | Yes, No
1ae255c5-42f6-50bf-9eb0-70f07abf6eb7 | button | Leemark Sign-Off - Attach below | Pass, Fail
475eca55-fef3-5c3c-a01d-2f3d44aa38b1 | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
| section | Fit Off (if required ie if not covered by the above section)
| checkpoint | Subsequent Sighting - Pass once entered
696b7229-e3fe-5604-bc09-3adac5e1fdb1 | textbox | Date
4aa79aee-e590-5ca8-9834-c28867c51f10 | textbox | Time
fbfd4ae1-fd5b-5d71-a30f-5ef5bd2f3f93 | textbox | Pressure
11aaeafe-2f85-5301-9cde-5d05b6d1dd20 | button | Photo(s) taken | Yes, No
abed6a55-2d4c-5fbc-bfe3-e32d296f3bff | button | Leemark Sign-Off - Attach below | Pass, Fail
3559c9bb-1644-546a-abf5-241c8c6aefce | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
a5dd776f-2387-52dc-a461-81cb3dd933c7 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
b3e83d4c-c71c-5612-820f-cf48420163d5 | button | Area left clean & tidy | Yes, No
424fad44-3d81-5f49-80c6-ea791f5e8a65 | tickbox | Leemark Sign-Off
1e0fa119-f3c6-5230-b0ca-1fa77c64297a | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-40-ITR-302.1 Fire Pump Installation (V.171121) |  | LM-FOR-40-ITR-302.1 Fire Pump Installation (V.171121) | de8a11d2-43ab-493d-bde6-37eebe977b4b
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
b48b8dfb-18b9-5d36-99f1-b113e04822cc | textbox | Drawing & Revision #
16b53e60-297e-5ce7-ba84-3cc387b36ffc | tickbox | Area clear, tidy and accessible
e759b49e-c464-540e-a6d1-ad78fdcf9b9d | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Pump installation arrangement including suction and discharge pipe works are in accordance with the approved drawing/plan
| checkpoint | Pump clearance is 1000 mm on all four sides and 600 mm between pumps
| checkpoint | Concrete plinth/foundation height is minimum 150 mm from FFL and 150 mm wider on all four sides of pump base
| checkpoint | Pump base is sitting squarely and bolted down Vibration mounts are properly anchored on plinth or inertia plinth
| checkpoint | Pump suction and discharge pipework are completely installed and connected Supports are adequately provided
| checkpoint | Control panels installed and bolted down, MFB have clear access around pump controller 1000mm Arc
| checkpoint | Suction isolation valve installed is OS & Y type
| checkpoint | Non-return valve is installed and located upstream of the isolation valve in pump discharge line
| checkpoint | Pump circulation-relief valve for electric driven pump is installed and piped to drain or tank return line
| checkpoint | Heat exchanger cooling water harness for diesel driven pump is installed and piped to drain or tank return line
| checkpoint | Pressure gauge with gauge cock is installed min 2Ø downstream of discharge flange or reducer
| checkpoint | Pressure reductions installed on manifold x2 for each stage with M/V’s and Annubar for each stage
| checkpoint | Exhaust connected to pump and installed to approved discharge location
| checkpoint | Full tanks have been filled with Diesel; Electric Pumps AND Controls ready for energisation
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
a6d2f41e-83fb-5041-ae58-4b76ba8d0123 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
cbf386ce-b5ae-5340-86ac-7bd996228d8e | button | Area left clean & tidy | Yes, No
9e2e6ec7-0c50-518e-a288-93b43c315a60 | tickbox | Leemark Sign-Off
50d546b1-47ad-5a0f-8423-a26eb4a1591f | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-40-ITR-302.2 Hydrant Installation (V.171121) |  | LM-FOR-40-ITR-302.2 Hydrant Installation (V.171121) | bda46fe0-9c77-49df-bbec-85d4dd68b537
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
ff1ebb66-c0fb-5128-814a-3cfcdc572d5b | textbox | Drawing & Revision #
473a3de3-0a52-51e1-8ff7-4d9181d66715 | tickbox | Area clear, tidy and accessible
0a6ed5e4-4e14-56c8-9e3e-dbb2d9774d87 | note | Attach Photos/Comments below if any issues & send report to Builder
59f9cfca-ea88-5bc2-81a1-299d5b94c2ce | textbox | Hydrant No.
| checkpoint | Hydrant supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plan
| checkpoint | Hydrostatic pressure testing of installed supply pipe works completed and accepted
| checkpoint | Hydrant valves and associated pipes and fittings used are in accordance with the approved specifications and applicable codes/standards
| checkpoint | Fire Hydrant and associated fire water main isolation valves locations are in accordance with the approved drawing/plan
| checkpoint | Hydrants stand pipe is adequately supported and bolted down. Concrete surround block provided for external hydrant
| checkpoint | Hydrant valve is between 750 to 1200 mm from finish floor/grade level
| checkpoint | Valve outlet is facing away from the wall and not more than 35O below its horizontal axis. Minimum 300 mm clearance around the valve outlet
| checkpoint | Minimum 1000 mm clear space in front of valve outlet is provided
| checkpoint | Valve handwheel clearance is minimum 100 mm clear of any obstruction at fully open
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
858b3ff8-679c-5786-8b32-66545b1fea39 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
079dfc80-fd79-542f-90ea-e8ae8c171c92 | button | Area left clean & tidy | Yes, No
bf639abd-2775-54de-8db7-18893848f770 | tickbox | Leemark Sign-Off
638bbcec-15bc-5265-b1ff-c808567c14bb | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-40-ITR-302.3 Hose Reel Installation (V.171121) |  | LM-FOR-40-ITR-302.3 Hose Reel Installation (V.171121) | 47763c80-b43a-42b7-ad2a-01d3e18823f6
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
766be16c-1765-5808-8442-f66c82ed0bb6 | textbox | Drawing & Revision #
51f6f79f-60d5-530a-bdf7-e6c78a3fe0ca | tickbox | Area clear, tidy and accessible
7fd7a9f0-e9d7-566b-b2d2-a290311647e6 | note | Attach Photos/Comments below if any issues & send report to Builder
2d644428-615c-50ae-8e00-475a211edbdc | textbox | Hose Reel No.
| checkpoint | Hose Reel supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plans
| checkpoint | Hydrostatic pressure testing of installed pipe works completed and accepted
| checkpoint | Hose Reel and associated valves, pipes and fitting used are in accordance with the approved specifications and applicable codes/standards
| checkpoint | Hose Reel located along normal path of travel to nearest exit and readily accessible
| checkpoint | Verify and confirm hose length to be 36-metres or 40-meters
| checkpoint | Hose reel spindle is 1400 mm minimum to 2400 mm maximum above floor level. Stop valve is 1000 + 100 mm above floor level
| checkpoint | Minimum radial clearance of 100 mm between the reel rim and cabinet/cavity to the sides, above and below
| checkpoint | Minimum 100 mm clearance around the stop valve handwheel/handle
| checkpoint | Any defects found on the hose reel assembly have been corrected
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
31b8cde2-6ffb-562f-a516-c692545293a3 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
a3fce89e-560b-5838-887a-e67bb388b8f7 | button | Area left clean & tidy | Yes, No
d6fde23e-3e6a-524f-98d4-3feba888f302 | tickbox | Leemark Sign-Off
cba21e20-7011-51cc-976a-dc376da6b6db | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-40-ITR-302.4 Tank Installation (V.171121) |  | LM-FOR-40-ITR-302.4 Tank Installation (V.171121) | 3d5b2edd-740a-4959-a3f6-11e9b510c1d2
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
6253daff-8279-5e3e-9f5d-1ad793106a26 | textbox | Drawing & Revision #
0538600c-205a-5631-9916-dd0e97e1b081 | tickbox | Area clear, tidy and accessible
3d22d99b-f930-535a-8fd2-1734bfc8b751 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Tank installation/construction is completed including associated pipe works in accordance with the approved drawing/plan
| checkpoint | Tank is free from dents, buckling, cracks, and internal is clean and free of any debris and construction materials
| checkpoint | Tank internal liner (if provided) is complete and properly bonded to tank wall/shell
| checkpoint | Tank quick infill line including associated infill valve and isolation valve installed and adequately supported
| checkpoint | Tank suction isolation valve is fitted in the correct position and operational in accordance with the approved drawing/plan
| checkpoint | Tank suction vortex inhibitor is fitted in the correct position and elevation in accordance with the approved drawing/plan
| checkpoint | Tank overflow is fitted in the correct position, elevation and properly piped to drain Adequate drain available
| checkpoint | Tank drain/sludge isolation valve is fitted and blank off
| checkpoint | Tank external water level indicator is fitted and operational
| checkpoint | Tank internal and external access ladders are fitted & secured
| checkpoint | Tank access hatch is fitted and provided with lockable cover
| checkpoint | Ball float for infill pilot line is fixed tightly, close to the manhole and away from the discharge path of tank infill
| checkpoint | Tank is located with minimum of 600 mm clearance around tank perimeter and roof line
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
fcfbbed9-a2b1-5cf8-8636-996504019419 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
aee91bbb-6e94-504a-9ba6-ef60610a59c5 | button | Area left clean & tidy | Yes, No
1872cca3-5dbc-5a60-8279-c20c2c6af89a | tickbox | Leemark Sign-Off
d87d144e-86ad-5e1e-9f26-777b524e2c6d | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-40-ITR-302.5 Booster Assembly (V.171121) |  | LM-FOR-40-ITR-302.5 Booster Assembly (V.171121) | 2686d752-a08e-4980-953a-0cc0b9dd45cc
| section | Installation
| checkpoint | Latest consented drawings checked & referenced
0666fe68-39d4-5b87-9319-5964f619469d | textbox | Drawing & Revision #
74afbd17-185b-5a38-910f-e1a22eb73de0 | tickbox | Area clear, tidy and accessible
33518840-c967-513d-891c-d6f8a147efae | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | All pipework are installed in the correct position and alignment in accordance with the approved drawing/plan
| checkpoint | All pipework have been pressure tested and accepted in accordance to approved pressure testing procedure
| checkpoint | Fire Brigade Booster is located within sight of the main entrance to the building
| checkpoint | Concrete plinth provided for the booster location and hard stand for fire brigade pumping appliance
| checkpoint | Feed Hydrant is located within 8 metres from fire brigade appliance hard stand
| checkpoint | Fire water storage tank suction point (Storz) is located within 4 metres from fire brigade appliance hard stand
| checkpoint | Fire water storage tank suction point (Storz) is located within 10 metres from fire brigade booster inlet connection
| checkpoint | Centre distance between feed hydrant and booster inlet connection is 450 mm minimum and 5 m maximum
| checkpoint | The height of Feed Hydrant Outlet and Booster Inlet Connection is minimum 750 mm and maximum 1200 mm from FFL
| checkpoint | Valves face minimum 150-mm from door and valve handles are 100-mm from cabinet sides
| checkpoint | The number of feed hydrant outlet installed is equal to number of fire brigade booster assembly inlets
| checkpoint | The required number of fire brigade booster inlets installed is suitable for the system requirement or minimum of 2 inlets
| checkpoint | Full flow non-return valve of correct size is installed in the proper location
| checkpoint | Approved type of cabinet enclosure is installed as required
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
1c30f14f-2dde-5c2c-a7a6-8c871001a199 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
22588b54-61ed-503a-9509-5021d518cfb9 | button | Area left clean & tidy | Yes, No
ff034178-d8b7-56b5-ac3e-a1bc3cb0d558 | tickbox | Leemark Sign-Off
651828ff-b004-5725-bf5b-bdc6ef6cc3ed | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-50 ITR 303.7 ASD (Aspirated) Installation (V.171121) |  | LM-FOR-50 ITR 303.7 ASD (Aspirated) Installation (V.171121) | 64642236-6b9b-43ac-affe-8a74975a36c4
| section | Pre-commissioning Procedures
| checkpoint | Check the location of installation is as per approved shop drawings and manufactures recommendations
| checkpoint | Check the Height of Panel is as per manufacturer's recommendations and in accordance with the relevant Australian Standards
| checkpoint | Confirm operation of auto-reset from FIP is wired through GP relay
| checkpoint | Check all wiring connections are tight and secure
| checkpoint | Check routing of the conduits are as per approved shop Dwg’s
| checkpoint | Check joints are properly glued /sealed and bonded to eliminate any potential air leaks
| checkpoint | Check pipe joints at the inlet ports of the scanner are not glued but firmly fitted into air inlet socket
| checkpoint | Check the sensing holes are drilled as per design
| checkpoint | Confirm the exhaust has been routed back into the sampling space
| checkpoint | Confirm end caps have been installed un-glued to all pipes at a serviceable height
| checkpoint | Confirm wiring is complete to Action, Minor Urgent, Fault & Fire relays and monitored via the FIP.
| section | Commissioning
| checkpoint | Power up the system, the aspirator starts up and air is flowing out of exhaust port , LCD screen is operational.
| checkpoint | Induce smoke into the furthest sampling point from the head end unit
| checkpoint | Check that a Fire signal is being transmitted to the FIP within 60s of smoke entering the VESDA pipe
| checkpoint | Check the correct signals are being transmitted to the FIP via Action, Minor Urgent & Fire Relays correctly.
| checkpoint | Remove the power from the VESDA and confirm Fault is received at the FIP
| checkpoint | Check the fire signal is conveyed to the fire Alarm system and BMS, if required
| checkpoint | Check the transmission of signals to operate ancillary devices, if required.
| checkpoint | Record all baseline data as required
| checklist | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421) |  | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421) | 2a846830-4cf8-4912-9fbd-eb9d6e63abc7
| section | Fit-Off
| checkpoint | Latest consented drawings checked & referenced
39415713-177b-5290-bb66-3662c6dead3a | textbox | Drawing & Revision #
0f585856-8ce5-5a68-9a8e-5a56787bb72d | tickbox | Area clear, tidy and accessible
50797ca4-5008-59ee-b0ed-6d71cae27a0b | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Have all devices been installed in the correct position with no obstructions
| checkpoint | Have all detectors been installed in the correct position and addressed
| checkpoint | Have all input/output modules been installed in the correct position and addressed, with all enclosures sealed
| checkpoint | Have all magnetic door holders been installed correctly
| checkpoint | Have all input/output devices been installed and addressed for security fire trips
| checkpoint | Have all input/output devices been installed and addressed for mechanical fire trips
| checkpoint | Have all input/output devices been installed and addressed for AS 1668 Fan Controls
| checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after fire works
| checkpoint | Have all cables and conduits been installed in the correct position for devices
| checkpoint | Have all devices been terminated for testing purposes
| section | Cable Feeds
| checkpoint | Have all cable feeds been connected to the first device
| checkpoint | Have all cable feeds been connected to the last device
| checkpoint | Have cable feeds been connected at the panel
| section | Visual Check
| checkpoint | Check that no other services are run with or attached to fire detection cables
| checkpoint | Check that no cables have been damaged
| checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
| checkpoint | Check that all address tags and labels are clear and readable
| checkpoint | Have devices and address been noted on “As Constructed Drawings” for handover
| checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
| checkpoint | Has photographic evidence been taken and recorded for all penetrations?
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
8e85bcca-d32b-52a1-b941-06fe7608e201 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
b065cc30-99fe-5cec-8827-d1a6b6fdad5a | button | Area left clean & tidy | Yes, No
22d35957-8f31-59cf-bb04-93e0fc0046c5 | tickbox | Leemark Sign-Off
9a355fb2-181a-5d47-bf26-426e0030bca8 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-50-ITR-303.1 Fire Panel Installation (V.171121) |  | LM-FOR-50-ITR-303.1 Fire Panel Installation (V.171121) | 7110dcdf-5130-459a-8af5-cd0a01533668
| section | Fire Indicator Panel
| checkpoint | Latest consented drawings checked & referenced
595d8463-6ddf-502d-a2e7-6db763ee9ecf | textbox | Drawing & Revision #
ba90e81a-a458-51b7-a627-a051c1499b87 | tickbox | Area clear, tidy and accessible
d0bcabb5-5a9c-5c94-8e2a-957f94610040 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Are visual indicators and controls not less than 750 mm from the floor
| checkpoint | Are visual indicators and controls not more than 1850 mm from the floor
| checkpoint | Connected to Brigade - Is the fire indicator panel clearly visible and readily accessible within the designated building entry point or the fire control room
| checkpoint | Not Connected to Brigade - Is the fire indicator panel in a secure location and clearly visible and readily accessible to authorized personnel
| section | Accessibility
| checkpoint | Is the fire indicator panel obscured by a door (if No, continue to CLEARANCE)
| checkpoint | Is the door marked in a contrasting colour to the general colour scheme with the words “FIRE PANEL” in letters not less than 50mm high
| checkpoint | Is the door absent of locks
| checkpoint | Where the door reduces the CIE sounder sound level below the CIE requirement, means are provided to give the required sound level outside the covering door
| checkpoint | A minimum clearance is maintained from the enclosure as shown
| section | Power sources
| checkpoint | Is the battery enclosure located such that the batteries are readily accessible for inspection
| checkpoint | Are the connecting leads to the battery clearly labelled to reduce the possibility of reverse connections to the battery
| checkpoint | The battery is not be tapped for intermediate voltages
| checkpoint | All connections are made using suitable connectors
| section | Sub-Indicator Panels
| checkpoint | The SIP shall only serve areas on one level of a building unless - Pass once below considered
224df418-8b6d-553d-baf8-9cb5360e069d | button | (a) The SIP serves the entire building | Yes, No, N/A
0272eb84-3d08-59e8-85c2-761de48cb115 | button | (b) All zones connected to the SIP are readily accessible without leaving the area served by the SIP; or | Yes, No, N/A
e70bfc1f-e1e7-5226-af72-fb49dae25657 | button | (c) The location of each zone in alarm at the SIP can be identified at the designated building entry point | Yes, No, N/A
7a431d19-71be-5f7d-86be-133adb1f1794 | button | Where the SIP serves the entire building, it shall be installed in accordance with the requirements for an FIP | Yes, No, N/A
223c9c09-dae4-5fa1-a547-f8b11a312b82 | button | If the SIP serves a specific area, is it located at the main point of entry into that area | Yes, No, N/A
| section | Wiring
| checkpoint | The extra low voltage wiring of the fire detection and alarm system is be kept separate and distinct from all other systems
| checkpoint | The extra low voltage wiring of the fire detection and alarm system is installed in accordance with the requirements of AS/ACIF S009
| checkpoint | Other wiring is installed in accordance with the electrical safety requirements of AS/NZS
| checkpoint | Externally energized circuits at voltages in excess of extra low voltage, except the power source for CIE, do not enter any CIE enclosure
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
5901b22b-0656-59ce-8788-baaa6da739e5 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
c58eddf1-bfdd-54cd-9460-cc7c3994576c | button | Area left clean & tidy | Yes, No
6328d84b-6f97-51f0-a4f4-dd50f85fee3e | tickbox | Leemark Sign-Off
7458a519-16f3-56e5-a483-53f8c643bb47 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-50-ITR-303.2 Ewis Installation (V.171121) |  | LM-FOR-50-ITR-303.2 Ewis Installation (V.171121) | d9c1460e-4b27-4c3f-9c93-eeb30a205db8
| section | Cabling
| checkpoint | Latest consented drawings checked & referenced
d28138c0-dcd7-5eb8-9b80-c3c61cc1a6e9 | textbox | Drawing & Revision #
a50b7f47-7216-5fc6-8bec-765457be82be | tickbox | Area clear, tidy and accessible
3c45c1a6-2d5c-5691-b6c8-8235b84d3911 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Have all cable supports been installed in the correct position with no obstructions
| checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
| checkpoint | Have all cables been installed for speakers and horns
| checkpoint | Have all cables been installed for warden intercom points
| checkpoint | Have all cables been installed for emergency call points
| checkpoint | Have all cables been installed for strobes
| checkpoint | Have all cables been installed for background music inputs
| checkpoint | Have all cables been installed for microphone inputs
| checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
| checkpoint | Have all cables been installed in the correct position for devices
| checkpoint | Have all cables been joined through for testing purposes or fitted with end of line devices
| section | Cable Feeds
| checkpoint | Have all cable supports been installed in the correct position with no obstructions
| checkpoint | Have all cable feeds been installed in the correct position
| checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
| checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
| checkpoint | Have the modified cable trays been re-galvanized
| section | Visual Check
| checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables
| checkpoint | Check that no cables have been damaged
| checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
| checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
| checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
| checkpoint | Has photographic evidence been taken and recorded for all penetrations
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
96e752c0-7d61-5c12-8964-f4a5e16d8d5b | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
f3c39177-ccfe-5676-ac36-aa50e75572b9 | button | Area left clean & tidy | Yes, No
cbbac449-61e7-556c-a5a9-b42c715f1682 | tickbox | Leemark Sign-Off
6ec1091d-8235-5143-affd-ca28f9430d14 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off (V.171121) |  | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off (V.171121) | c6c7dfea-14d5-469b-93d5-53db7cb48c8a
| section | EWIS Fit-Off
| checkpoint | Latest consented drawings checked & referenced
25a2aaa8-437d-5000-8552-2b947c58a481 | textbox | Drawing & Revision #
5b1bca4a-957c-51da-9295-ef805fa35a55 | tickbox | Area clear, tidy and accessible
9874e39f-e7e0-51f8-a474-bd2e9fb63a17 | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Have all devices been installed in the correct position with no obstructions
| checkpoint | Have all speakers / horns been installed in the correct location
| checkpoint | Have all warden intercom points been installed in the correct location
| checkpoint | Have all emergency call points been installed in the correct location
| checkpoint | Have all strobes been installed in the correct location
| checkpoint | Have all background music points been installed in the correct location
| checkpoint | Have all microphone points been installed in the correct location
| checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after warning system works
| checkpoint | Have all cables and conduits been installed in the correct position for devices
| checkpoint | Have all devices been terminated for testing purposes
| section | Cable Feeds
| checkpoint | Have all cable supports been connected to the first device
| checkpoint | Have all end of lines been fitted and measured
| checkpoint | Have cables feeds been connected at the panel
| section | Visual Check
| checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables or devices
| checkpoint | Check that no cables or devices have been damaged
| checkpoint | Check that all final device locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
| checkpoint | Have devices and readings been noted on “As Constructed Drawings” for handover
| checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
| checkpoint | Has photographic evidence been taken and recorded for all penetrations
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
1a9359da-4a24-52a6-9118-f7b27ba0df20 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
62a3d1f8-1ae3-556a-8728-a010318e4f2f | button | Area left clean & tidy | Yes, No
e1eedff4-ea64-509b-861c-5e6665d5b6cc | tickbox | Leemark Sign-Off
6e85ff60-b7fe-5cb0-8952-325112afe672 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-50-ITR-303.4 Fire Detection Installation (V.171121) |  | LM-FOR-50-ITR-303.4 Fire Detection Installation (V.171121) | 0e71116d-51bc-4d32-bec6-3eafe9c1e2eb
| section | Cabling
| checkpoint | Latest consented drawings checked & referenced
2454c99f-a05e-55f2-8932-8b30caa6e6cf | textbox | Drawing & Revision #
81480ff7-5a43-5c1e-a1c6-610f3bcb08d9 | tickbox | Area clear, tidy and accessible
ee9dad85-64f7-5435-bdf1-f9ee71f21cea | note | Attach Photos/Comments below if any issues & send report to Builder
| checkpoint | Have all cable supports been installed in the correct position with no obstructions
| checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
| checkpoint | Have all cables been installed for detectors
| checkpoint | Have all cables been installed for sprinkler valve sets
| checkpoint | Have all cables been installed for magnetic door holders
| checkpoint | Have all cables been installed for security fire trips
| checkpoint | Have all cables been installed for mechanical fire trips
| checkpoint | Have all cables been installed for AS 1668 Fan Controls
| checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
| checkpoint | Have all cables been installed in the correct position for devices
| checkpoint | Have all cables been joined through for testing purposes
| section | Cable Feeds
| checkpoint | Have all cable supports been installed in the correct position with no obstructions
| checkpoint | Have all cable feeds been installed in the correct position
| checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
| checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
| checkpoint | Have the modified cable trays been re-galvanized
| section | Visual Check
| checkpoint | Check that no other services are run with or attached to fire detection cables
| checkpoint | Check that no cables have been damaged
| checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
| checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
| checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
| checkpoint | Has photographic evidence been taken and recorded for all penetrations?
| section | Completion
| checkpoint | Works completed to specification/drawings - Attach photos of work below
97ab2ab4-b75a-5a37-8f4a-372407891f76 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
1c0b7aa3-57c3-50c4-9e41-cb4e26907d28 | button | Area left clean & tidy | Yes, No
f4075a03-647a-50c8-b9a3-09b1be46627f | tickbox | Leemark Sign-Off
4ac5444e-733e-549d-ba67-ce6e190dde39 | tickbox | Builder Sign-Off
| signoff | Sign-Off - click to Add signature(s)
| checklist | LM-FOR-50-ITR-304.1 Pre Action Systems |  | LM-FOR-50-ITR-304.1 Pre Action Systems | babf147b-5f31-4b9e-8eb6-afc253520592
| section | 1. ITR Pre-commissioning Procedures
| checkpoint | 1.1 Verify correct type, spacing and elevation of installed pipe supports and hangers.
| checkpoint | 1.2 Installation inspection of trunk mains and range pipes
| checkpoint | 1.3 All dirt traps must be capped, and all pops temporarily plugged
| checkpoint | 1.4 Inspection of installed sprinkler heads & baffle plates and flexible droppers
| checkpoint | 1.5 Installation inspection of pre-action valve sets and ancillary equipment to ensure completeness, correct location, mounting
| checkpoint | 1.6 Verify installation of alarm devices (e.g., DBA pressure/flow switch, low pressure switch) and solenoid valve for correct type and rating and proper interface connections to Fire Indicator Panel (FIP).
| section | 2. ITR Commissioning
| checkpoint | 2.1 Perform Pneumatic leak test of pipework to ensure no loose joints or open pipe ends
| checkpoint | 2.3 Perform Hydrostatic Testing of pipework. Gradually apply pressure increments of 500 kPa for 15-minute holds until test pressure of 1600 kPa or 400 kPa above maximum static working pressure of the system is achieved and hold for 2-hours.
| checkpoint | 2.4 Perform a trip test on each pre-action valve by opening the alarm test ball valve and check operation of water motor alarm. Confirm operation of DBA pressure switch with correct indication at fire indicator panel.
| checkpoint | 2.5 Initiate single or double interlock release activation and check operation of water motor alarm, DBA pressure switch and correct indication at fire indicator panel.
| checkpoint | 2.6 Record cut-in / cut-out pressure of air supply compressor and time to recharge the system pressure
| checkpoint | 2.7 Reinstate system and ensure valves are secured in its intended position, alarm and monitoring devices are in operational mode and system in ready to operate condition
| checkpoint | Final Inspection Builder
5266e169-163a-5d87-8ed0-ace697240f42 | textbox | Checked By:
666b44aa-93e7-5542-af33-5d6f7646c2a2 | textbox | Signature:
f27ce135-4a6d-5dcb-aa93-e6fd21a0e303 | textbox | Date:
| checkpoint | Final Inspection (Leemark)
7c5179d5-5ce4-5359-b236-08833430dd68 | textbox | Checked By:
e33feda4-cfa6-5043-92f7-fd182bc90e4f | textbox | Signature:
9e80f159-47f9-50e6-9689-f1dc5e9bf88f | textbox | Date:
| checklist | LM-FOR-50-ITR-304.2 N2 Blast System |  | LM-FOR-50-ITR-304.2 N2 Blast System | 4ca31256-cb0b-4536-b4c3-d70307992817
| section | 1. ITR Pre-commissioning Procedures
| checkpoint | 1.1 Verify unit is fixed into position using the anchor points
| checkpoint | 1.2 Verify all connections are complete to unit and compressor/s
| checkpoint | 1.3 Check for leaks – Listen for leaks and spray with soapy water around connections.
| checkpoint | 1.4 All power is connected and energised
| checkpoint | 1.5 Set Air maintenance devices on Pre Action Valves to 18psi
| section | 2. ITR Commissioning
| checkpoint | 2.1 Power is on the unit by making sure the touchscreen has turned on and the start and stop button is “Red” and the icon reads “Status: Off”
| checkpoint | 2.3 Make sure the outlet ball valve is valve off.
| checkpoint | 2.4 Skip this step if this is a FPS-1650, otherwise, slowly open the Air Inlet valve and allow pressure to build up to the internal regulator after the filters. Make sure pressure reaches 120 PSIG. Listen and feel for any major leaks.
| checkpoint | 2.5 "On the home screen of the touchscreen, press and hold the power button for 2 seconds until it turns “Green” and the icon reads “Status: Running”. Air will rushing through the system and N2 will start filling the tank"
| checkpoint | 2.6 Once the internal tank pressure reaches 70 PSIG, the system will go into standby mode at the end of the cycle.
| checkpoint | 2.7 "After the 5 minutes with the pressure maintained, slowly open the nitrogen outlet valve to the “Air Maintenance Device” and monitor for any leaks. The nitrogen generator will automatically run, and shutoff as needed based on the internal storage tank pressure."
| checkpoint | Final Inspection Builder
7953e6bf-13bb-5fba-abbe-b401865220c1 | textbox | Checked By:
5b0e242e-dcc3-5bc6-9798-6f1b0dcccfd3 | textbox | Signature:
ebf75578-39ce-52dd-821f-49bf149ced97 | textbox | Date:
| checkpoint | Final Inspection (Leemark)
beee132c-cec7-59ca-a525-72a6762a5206 | textbox | Checked By:
3f3a0a1b-9ba1-5cdf-b9b1-7fb83d4e8255 | textbox | Signature:
9ca9fe95-6b2d-57a1-8ead-2431e291ab2c | textbox | Date:
| checklist | SYS - PT - Ewis Installation |  | Ewis Installation | 5842fb1c-693d-4b50-918d-23bf062b2e50
| section | Cabling
| checkpoint | Have all cable supports been installed in the correct position with no obstructions
| checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
| checkpoint | Have all cables been installed for speakers and horns
| checkpoint | Have all cables been installed for warden intercom points
| checkpoint | Have all cables been installed for emergency call points
| checkpoint | Have all cables been installed for strobes
| checkpoint | Have all cables been installed for background music inputs
| checkpoint | Have all cables been installed for microphone inputs
| checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
| checkpoint | Have all cables been installed in the correct position for devices
| checkpoint | Have all cables been joined through for testing purposes or fitted with end of line devices
| section | Cable Feeds
| checkpoint | Have all cable supports been installed in the correct position with no obstructions
| checkpoint | Have all cable feeds been installed in the correct position
| checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
| checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
| checkpoint | Have the modified cable trays been re-galvanized
| section | Visual Check
| checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables
| checkpoint | Check that no cables have been damaged
| checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
| checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
| checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
| checkpoint | Has photographic evidence been taken and recorded for all penetrations
| section | Completion
| checkpoint | Sign Off below - pass once complete
| signoff | Sign-Off - click to Add signature(s)
| checklist | SYS - PT - Ewis Installation Fit Off |  | Ewis Installation Fit Off | e58f1048-d9b8-42aa-a210-83f3f483d9a4
| section | EWIS Fit-Off
| checkpoint | Have all devices been installed in the correct position with no obstructions
| checkpoint | Have all speakers / horns been installed in the correct location
| checkpoint | Have all warden intercom points been installed in the correct location
| checkpoint | Have all emergency call points been installed in the correct location
| checkpoint | Have all strobes been installed in the correct location
| checkpoint | Have all background music points been installed in the correct location
| checkpoint | Have all microphone points been installed in the correct location
| checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after warning system works
| checkpoint | Have all cables and conduits been installed in the correct position for devices
| checkpoint | Have all devices been terminated for testing purposes
| section | Cable Feeds
| checkpoint | Have all cable supports been connected to the first device
| checkpoint | Have all end of lines been fitted and measured
| checkpoint | Have cables feeds been connected at the panel
| section | Visual Check
| checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables or devices
| checkpoint | Check that no cables or devices have been damaged
| checkpoint | Check that all final device locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
| checkpoint | Have devices and readings been noted on “As Constructed Drawings” for handover
| checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
| checkpoint | Has photographic evidence been taken and recorded for all penetrations
| section | Completion
| checkpoint | Sign Off below - pass once complete
| signoff | Sign-Off - click to Add signature(s)
| checklist | SYS - PT - EWIS Panel |  | EWIS Panel | af03fb8d-5305-48b4-8c47-98f0e30c496f
| section | Fire Indicator Panel
| checkpoint | Are visual indicators and controls not less than 750 mm from the floor
| checkpoint | Are visual indicators and controls not more than 1850 mm from the floor
| checkpoint | Connected to Brigade - Is the fire indicator panel clearly visible and readily accessible within the designated building entry point or the fire control room
| checkpoint | Not Connected to Brigade - Is the fire indicator panel in a secure location and clearly visible and readily accessible to authorized personnel
| section | Accessibility
| checkpoint | Is the fire indicator panel obscured by a door (if No, continue to CLEARANCE)
| checkpoint | Is the door marked in a contrasting colour to the general colour scheme with the words “FIRE PANEL” in letters not less than 50mm high
| checkpoint | Is the door absent of locks
| checkpoint | Where the door reduces the CIE sounder sound level below the CIE requirement, means are provided to give the required sound level outside the covering door
| checkpoint | A minimum clearance is maintained from the enclosure as shown
| section | Power sources
| checkpoint | Is the battery enclosure located such that the batteries are readily accessible for inspection
| checkpoint | Are the connecting leads to the battery clearly labelled to reduce the possibility of reverse connections to the battery
| checkpoint | The battery is not be tapped for intermediate voltages
| checkpoint | All connections are made using suitable connectors
| section | Sub-Indicator Panels
| checkpoint | The SIP shall only serve areas on one level of a building unless - Pass once below considered
060da81a-13fc-46a6-b891-f9b6bad5f424 | button | (a) The SIP serves the entire building | Yes,No
ea41a7ef-7ec4-4f75-a460-3c2c0ab4c8ba | button | (b) All zones connected to the SIP are readily accessible without leaving the area served by the SIP; or | Yes,No
fe6d7a9f-a586-4369-ad3b-ccb567163454 | button | (c) The location of each zone in alarm at the SIP can be identified at the designated building entry point | Yes,No
297665f7-9691-4872-af25-869b0a61df76 | button | Where the SIP serves the entire building, it shall be installed in accordance with the requirements for an FIP | Yes,No
e0b90b7c-661b-4c3c-ab01-5daf952df503 | button | If the SIP serves a specific area, is it located at the main point of entry into that area | Yes,No
| section | Wiring
| checkpoint | The extra low voltage wiring of the fire detection and alarm system is be kept separate and distinct from all other systems
| checkpoint | The extra low voltage wiring of the fire detection and alarm system is installed in accordance with the requirements of AS/ACIF S009
| checkpoint | Other wiring is installed in accordance with the electrical safety requirements of AS/NZS
| checkpoint | Externally energized circuits at voltages in excess of extra low voltage, except the power source for CIE, do not enter any CIE enclosure
| section | Completion
| checkpoint | Sign Off below - pass once complete
| signoff | Sign-Off - click to Add signature(s)
| checklist | SYS - PT - Fire Detection Fit Off |  | Fire Detection Fit Off | 0ae99089-1130-457e-a795-7e53db4f6462
| section | Fit-Off
| checkpoint | Have all devices been installed in the correct position with no obstructions
| checkpoint | Have all detectors been installed in the correct position and addressed
| checkpoint | Have all input/output modules been installed in the correct position and addressed, with all enclosures sealed
| checkpoint | Have all magnetic door holders been installed correctly
| checkpoint | Have all input/output devices been installed and addressed for security fire trips
| checkpoint | Have all input/output devices been installed and addressed for mechanical fire trips
| checkpoint | Have all input/output devices been installed and addressed for AS 1668 Fan Controls
| checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after fire works
| checkpoint | Have all cables and conduits been installed in the correct position for devices
| checkpoint | Have all devices been terminated for testing purposes
| section | Cable Feeds
| checkpoint | Have all cable feeds been connected to the first device
| checkpoint | Have all cable feeds been connected to the last device
| checkpoint | Have cable feeds been connected at the panel
| section | Visual Check
| checkpoint | Check that no other services are run with or attached to fire detection cables
| checkpoint | Check that no cables have been damaged
| checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
| checkpoint | Check that all address tags and labels are clear and readable
| checkpoint | Have devices and address been noted on “As Constructed Drawings” for handover
| checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
| checkpoint | Has photographic evidence been taken and recorded for all penetrations?
| section | Completion
| checkpoint | Sign Off below - pass once complete
| signoff | Sign-Off - click to Add signature(s)
| checklist | SYS - PT - Fire Detection Installation |  | Fire Detection Installation | cd0c1554-b0a4-4c88-80dd-d0f706d16d55
| section | Cabling
| checkpoint | Have all cable supports been installed in the correct position with no obstructions
| checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
| checkpoint | Have all cables been installed for detectors
| checkpoint | Have all cables been installed for sprinkler valve sets
| checkpoint | Have all cables been installed for magnetic door holders
| checkpoint | Have all cables been installed for security fire trips
| checkpoint | Have all cables been installed for mechanical fire trips
| checkpoint | Have all cables been installed for AS 1668 Fan Controls
| checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
| checkpoint | Have all cables been installed in the correct position for devices
| checkpoint | Have all cables been joined through for testing purposes
| section | Cable Feeds
| checkpoint | Have all cable supports been installed in the correct position with no obstructions
| checkpoint | Have all cable feeds been installed in the correct position
| checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
| checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
| checkpoint | Have the modified cable trays been re-galvanized
| section | Visual Check
| checkpoint | Check that no other services are run with or attached to fire detection cables
| checkpoint | Check that no cables have been damaged
| checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
| checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
| checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
| checkpoint | Has photographic evidence been taken and recorded for all penetrations?
| section | Completion
| checkpoint | Sign Off below - pass once complete
| signoff | Sign-Off - click to Add signature(s)
| checklist | SYS - PT - Hose Reel Installation |  | Hose Reel Installation | c0e923da-829d-4ee3-b59d-d8eea2315b7e
| section | Installation
| checkpoint | Hose Reel supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plans
993d9383-31a4-411c-81ad-ab3abf859c21 | textbox | Hose Reel No.
| checkpoint | Hydrostatic pressure testing of installed pipe works completed and accepted
| checkpoint | Hose Reel and associated valves, pipes and fitting used are in accordance with the approved specifications and applicable codes/standards
| checkpoint | Hose Reel located along normal path of travel to nearest exit and readily accessible
| checkpoint | Verify and confirm hose length to be 36-metres or 40-meters
| checkpoint | Hose reel spindle is 1400 mm minimum to 2400 mm maximum above floor level. Stop valve is 1000 + 100 mm above floor level
| checkpoint | Minimum radial clearance of 100 mm between the reel rim and cabinet/cavity to the sides, above and below
| checkpoint | Minimum 100 mm clearance around the stop valve handwheel/handle
| checkpoint | Any defects found on the hose reel assembly have been corrected
| section | Completion
| checkpoint | Sign Off below - pass once complete
| signoff | Sign-Off - click to Add signature(s)
| checklist | SYS - PT - Hydrant Installation |  | Hydrant Installation | 4d489af0-30c2-4464-a144-f22b5ced22f5
| section | Installation
| checkpoint | Hydrant supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plan
e6c8e8ba-3051-4738-a997-0613ae0f34b4 | textbox | Hydrant No.
| checkpoint | Hydrostatic pressure testing of installed supply pipe works completed and accepted
| checkpoint | Hydrant valves and associated pipes and fittings used are in accordance with the approved specifications and applicable codes/standards
| checkpoint | Fire Hydrant and associated fire water main isolation valves locations are in accordance with the approved drawing/plan
| checkpoint | Hydrants stand pipe is adequately supported and bolted down. Concrete surround block provided for external hydrant
| checkpoint | Hydrant valve is between 750 to 1200 mm from finish floor/grade level
| checkpoint | Valve outlet is facing away from the wall and not more than 35O below its horizontal axis. Minimum 300 mm clearance around the valve outlet
| checkpoint | Minimum 1000 mm clear space in front of valve outlet is provided
| checkpoint | Valve handwheel clearance is minimum 100 mm clear of any obstruction at fully open
| section | Completion
| checkpoint | Sign Off below - pass once complete
| signoff | Sign-Off - click to Add signature(s)
| checklist | SYS - PT - Pre-Start |  | Pre-Start | 0041fc80-ef95-4188-83ca-724a32bfe739
| checkpoint | Add photos/comments
| checklist | SYS - PT - Sprinkler & Hydrant Hydrostatic Test |  | Sprinkler & Hydrant Hydrostatic Test | dd0c9be5-20c4-4a07-abaa-42a84925ed94
| section | Guidelines
| checkpoint | Guidelines understood - Pass once read
a80e0e8d-279f-49fa-b45c-6a867eb6bec9 | note | Guidelines: Fire Sprinkler Systems – 1600 kPa or 400 kPa above the maximum static pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
b205769c-45fc-4231-8677-8497a48c986a | note | Fire Hydrant Systems (Low Rise) – 1700 kPa or 1.5 times the design pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
ae0bb09a-bcd0-4330-ba3d-cb9fd3fe2a08 | note | Playhouse Theatre – 1200 kPa or 1.5 times the design pressure for a duration of 2 hours. (Check notes on Construction Drawing for nominated test pressure)
| section | Rough In Only OR Rough In & Fit Off Together
| checkpoint | First Sighting - Pass once entered - attach photo of pressure gauge and builder sign off if required
| checkpoint | Second Sighting - Pass once entered - attach photo of pressure gauge and builder sign off if required
| section | Fit Off (if required ie if not covered by the above section)
| checkpoint | Subsequent Sighting - Pass once entered - attach photo of pressure gauge and builder sign off if required
| checklist | SYS - PT - Sprinkler Control Valve |  | Sprinkler Control Valve | 53c0ebdc-e5d3-425d-8d55-59cf5c8bbf36
| section | Installation
| checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
| checkpoint | All supports are completely installed, spaced and bolted down box / assembly secured
| checkpoint | All roll grooved couplings / flanges are properly tightened
| checkpoint | Valve station drain is properly connected to risers drain and building hydraulic drainage
| checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
| checkpoint | All specific signage is installed lock shut / lock open including FSV number of M/V’s
| checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
| checkpoint | Correct type solenoid, flow switch, couplings etc installed
| checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
| checkpoint | Confirm GFA on solenoid activation/ flow switch/ MV activation
| checkpoint | Control Valve is positioned between 1150mm to 1800mm
| section | Completion
| checkpoint | Sign Off below - pass once complete
| signoff | Sign-Off - click to Add signature(s)
| checklist | SYS - PT - Sprinkler Control Valve Detail |  | Sprinkler Control Valve Detail | a3d4fd97-54be-4fb0-8cf1-c391b47bf4f8
| checkpoint | Documents/Drawings attached for reference - Pass once attached
| checkpoint | Latest consented drawings checked & referenced
d1cbf5cb-01a7-45de-b6b3-176798e6407c | textbox | Drawing & Revision #
| checkpoint | Area clear, tidy and accessible
85bdd3f2-0510-4c9c-b47c-99a195f3a1a2 | note | Attach Photos/Comments below if any issues & send report to Builder
| checklist | SYS - PT - Sprinkler Installation/Fitoff |  | Sprinkler Installation/Fitoff | 0febf7fd-d093-46c7-830e-253ffda17dc6
| section | Sprinkler Rough-In
| checkpoint | Supports spacing & fixing as per AS2118
| checkpoint | Pipework installed as per drawings
| checkpoint | Concealed space sprinklers installed
| checkpoint | All ends blanked off/plugged for testing
| checkpoint | Pipes left out
677ca8e3-24ec-4bb8-abe0-3ce498fb0d08 | note | Fail=Missing, Pass=Complete
7b77eb06-eb3f-4f5d-9dc2-2d73eeb713b2 | button | Pipes left out - installed | Yes,No
| section | Sprinkler Fit-Off
| checkpoint | Ceiling grid levelled
| checkpoint | Sprinklers installed as per drawings
| checkpoint | Sprinkler Type & temperature as per drawings
| checkpoint | All escutcheon plates installed
| checkpoint | Areas not fitted-off
65918d10-35b4-463a-a3a8-e9e82b7788ed | note | Fail=Missing, Pass=Complete
4cfa682d-f353-466d-95d1-4264778d516b | button | Areas not fitted-off - completed | Yes,No
| checkpoint | Client Sign Off Sheets Complete
| checkpoint | Painting carried out
| checkpoint | Pressure Tested (refer ITR 401) - Completed
| section | Completion
| checkpoint | Sign Off below - pass once complete
| signoff | Sign-Off - click to Add signature(s)
| checklist | Variation |  | Variation | a659d88b-5c37-4e63-9e98-cff636986adb
| checkpoint | Variation Details Complete (Pass once inputted)
0cf51977-6d75-5af4-a97d-fbb55832298b | textbox | Variation Name
456c7393-3d47-5f94-96fe-dde149bcdf48 | textbox | Variation Description
83b89ec8-1776-5044-a934-f4d09f4b1d81 | textbox | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
ec2054e7-1c8c-5337-b42c-32593298a0a6 | textbox | Acknowledgement
f1d0cdfe-486c-57f8-ab76-60e4a40d8048 | textbox | Signature/Reference Mail
| checkpoint | Photo(s)
| checkpoint | Supporting Documentation (Attached or Referenced)
| checkpoint | Variation Sign-Off - Click to Add signatures below
64723357-e840-5990-b650-f9868a197067 | button | Leemark Representative Signature Added below | Yes, No
678e2a6c-2c78-56d9-a89f-7bfd9a7761c0 | button | Builder Representative Signature Added below | Yes, No
| signoff | Click to Add Signatures
| checklist | wet fire ITP |  | wet fire ITP | 2412e832-de20-48ca-81fe-69a052460085
| checkpoint | Are all sprinklers installed clear of obstructions as per AS2118.4(2012) Clause 4.4.3.2?
| checkpoint | Have sprinkler spares been left in cabinet including a sprinkler key, if new install? INSERT PHOTO
| checkpoint | Have the valves been labelled inside the SCV? INSERT PHOTO
| checkpoint | Has the Sprinkler Block Plan been laminated and stuck on to the inside of the SCV cabinet? INSERT PHOTO
| checkpoint | Has the Water Tapping been connected to the SCV? INSERT PHOTO OF PRESSURE GAUGE
| checkpoint | Has the Water Tapping Cage been installed? INSERT PHOTO
| checkpoint | Has a Flow Test been conducted and recorded?
| checkpoint | Has the remote test valve been installed as per our shop drawing and labelled? INSERT PHOTO
| checkpoint | Have sprinklers been installed with guards if exposed? INSERT PHOTO
| checkpoint | Has a Hydrostatic test record been completed and recorded? 1200kPA min 2 Hours INSERT PHOTO OF PRESSURE GAUGE
| checkpoint | Do the As-Installed conditions on site reflect the Shop Drawings