## Project Structure
Folder Structure |  |  |  | Checklists
Site QA
Outstations Phase 2
OS-A5-01
|  |  | OS FAT | L1 Factory Acceptance Test Results (CR): OS
|  |  | OS Installation | L2 Installation QAQC Procedure - Outstation
|  |  | CABLE ID: OS-A5-01 / DB-GLP-AF-L1-11 | L2 Installation QAQC Procedure - RS485 Cabling
|  |  | CABLE ID: OS-A5-01 / DB-GLP-AF-L1-13 | L2 Installation QAQC Procedure - RS485 Cabling
|  |  | CABLE ID: OS-A5-01 / DB-GLP-AF-L1-15 | L2 Installation QAQC Procedure - RS485 Cabling
|  |  | CABLE ID: OS-A5-01 / DB-GLP-AF-L1-17 | L2 Installation QAQC Procedure - RS485 Cabling
|  |  | HLI Cabling Copper/Fiber | Fluke Linkware Report Attached
OS-A5-02
|  |  | OS FAT | L1 Factory Acceptance Test Results (CR): OS
|  |  | OS Installation | L2 Installation QAQC Procedure - Outstation
|  |  | CABLE ID: OS-A5-02 / DB-GLP-AG-L1-12 | L2 Installation QAQC Procedure - RS485 Cabling
|  |  | CABLE ID: OS-A5-02 / DB-GLP-AG-L1-14 | L2 Installation QAQC Procedure - RS485 Cabling
|  |  | CABLE ID: OS-A5-02 / DB-GLP-AG-L1-16 | L2 Installation QAQC Procedure - RS485 Cabling
|  |  | CABLE ID: OS-A5-02 / DB-GLP-AG-L1-18 | L2 Installation QAQC Procedure - RS485 Cabling
|  |  | HLI Cabling Copper/Fiber | Fluke Linkware Report Attached
SLA Sensors Phase 2
DHA2 SLA Sensors
|  |  | SLA sensors DHA2 | L2 Installation QAQC Procedure - SLA Sensor
DHA5 SLA Sensors
|  |  | SLA sensors DHA5 | L2 Installation QAQC Procedure - SLA Sensor

## Checklists
type | name | values
checklist | OS Reference docs
section | Reference Documents
checkpoint-no-status | Issued For Construction Drawing Set
checkpoint-no-status | Issued For Construction OS Locations
checkpoint-no-status | Issued For Construction Cable Schedule
checklist | L1 Factory Acceptance Test Results (CR): OS
section | Reference Documents
checkpoint-no-status | Issued For Construction Drawing Set
section | Visual & Pre Inspection
checkpoint | Inspection with final drawing design
checkpoint | Paint, hinges, door handles/locks operable and of satisfactory appearance
checkpoint | Gland plates — IP barrier and screws installed correctly
checkpoint | Circuit breakers installed as per design
checkpoint | Control PSU’s and Diode Module installed as per design
checkpoint | Main switch installed — type and size
checkpoint | Functional Earth bar installed
checkpoint | Power terminals correct and tightened
checkpoint | Control terminals installed and tight as per design
checkpoint | All components installed as per design
checkpoint | Ethernet switches/gateway patch leads installed as per schedule
checkpoint | Power panel wiring size and colour as per design
checkpoint | Control panel wiring size and colour as per design
checkpoint | Control panel wiring ferruled as per design
checkpoint | Earthing to all necessary points connected and earth continuity test performed
section | Pre-Energisation Electrical Testing
checkpoint | Insulation Resistance L1-E, (>1 Megohm = Pass)
checkpoint | Insulation Resistance L1-N, (>1 Megohm = Pass)
checkpoint | Insulation Resistance N-E, (>1 Megohm = Pass) *ENSURE ALL PROTECTIVE EARTHS ARE DISCONNECTED FROM ELECTRONICS
checkpoint | Check Earth Continuity to all metallic parts (Pass=<.5ohm )
section | Energised Function Testing
checkpoint | All powered components have correct power supply (test before energization)
checkpoint | All MCB’s and terminals have correct power supplies
checkpoint | Field MCB’s isolate associated terminals
checkpoint | All devices have correct voltage at terminals
checkpoint | Ethernet switches patch leads installed if required
checkpoint | Protocol Converter/Gateway patch leads installed if required
checkpoint | IO Module patch leads installed if required
section | Final Inspection
checkpoint | Engraved labels correct and installed
checkpoint | Clean Switchboard (free of debris and swarf)
checkpoint | Schematic drawing inside compartment
checkpoint | Equipment missing - Comment as applicable
section | Approval / Witnessing
checkpoint | Tests conducted by
checkpoint | Tests witnesses/approved by
checklist | L2 Installation QAQC Procedure - LLI Cabling
section | Visual & Pre Inspection
checkpoint | Cable type aligns with IFC-issue documentation
checkpoint | Cable is free of visible damage or defects
checkpoint | Cable entry to Outstation is through bottom and free from sharp edges or glanded
checkpoint | Cable Terminations is as per IFC-issue Cable Schedule
checkpoint | Wire point-point testing (continuity tester) is complete as per IFC-issue Cable Schedule
checkpoint | Cable is installed correctly on Cable containment/management
checkpoint | Cable Labels in place as per IFC-issue Cable Schedule
checkpoint | Wire Labels in place as per IFC-issue Cable Schedule
checkpoint | Cable screen earth/drain is connected - one end only
checkpoint | All spare cores insulated and secured within Duct
section | Pre-Energisation Electrical Testing...24VDC power cabling only
checkpoint | Insulation Resistance Pos to Neg, Megohms (Pass = >0.5Megohm @250VDC)
checkpoint | Insulation Resistance Pos-E, Megohms (Pass = >0.5Megohm @250VDC)
checkpoint | Insulation Resistance Negative-E, Megohms (Pass = >0.51Megohm @250VDC)
section | Approval / Witnessing
checkpoint | Tests conducted by
checkpoint | Tests witnesses/approved by
checklist | L2 Installation QAQC Procedure - RS485 Cabling
section | Visual & Pre Inspection
checkpoint | Cable type aligns with IFC-issue documentation
checkpoint | Cable is free of visible damage or defects
checkpoint | Cable entry to Outstation is through bottom and free from sharp edges or glanded
checkpoint | Cable Terminations is as per IFC-issue Cable Schedule
checkpoint | Cable is installed correctly on Cable containment/management
checkpoint | Cable Labels in place as per IFC-issue Cable Schedule
checkpoint | Wire Labels in place as per IFC-issue Cable Schedule
checkpoint | Cable screen earth/drain is connected - one end only
section | Approval / Witnessing
checkpoint | Tests conducted by
checkpoint | Tests witnesses/approved by
checklist | L2 Installation QAQC Procedure - SLA Sensor
section | Reference Documents
checkpoint-no-status | Issued For Construction SLA Location and Mount
section | Visual & Pre Inspection
checkpoint | Inspection with final drawing design- Is Sensor mounted using correct mount
checkpoint | Inspection with final drawing design- Is Sensor mounted in correct locations
checkpoint | Inspect Sensor mount to be free of paint chips and scratches
checkpoint | Sensor label to be installed, Equipment ID correct, spelling and grammar correct
section | Approval / Witnessing
checkpoint | Tests conducted by
checkpoint | Tests witnesses/approved by
checklist | L2 Installation QAQC Procedure - Outstation
section | Visual & Pre Inspection
checkpoint | Inspection with final drawing design- Is Panel location correct to drawings
checkpoint | Inspection with final drawing design- Is Panel layout correct to drawings
checkpoint | Paint, hinges, door handles/locks operable and of satisfactory appearance
checkpoint | Power terminals correctly installed and checked for tightness
checkpoint | Control terminals correctly installed and checked for tightness
checkpoint | Door swing not impeded by equipment (1000mm clearance required from edge of open door)
checkpoint | Earthing to all necessary points connected
checkpoint | Outstation mounted securely
checkpoint | All caution and warning labels in place
section | Final Inspection
checkpoint | Engraved labels installed, Equipment ID correct, spelling and grammar correct
checkpoint | Clean Switchboard (free of debris and swarf)
checkpoint | Schematic drawing inside compartment
checkpoint | Equipment missing - Comment as applicable
section | Approval / Witnessing
checkpoint | Tests conducted by
checkpoint | Tests witnesses/approved by
checklist | Fluke Linkware Report Attached
checkpoint | FLUKE LINKWARE Report Attached
checklist | Upload L3 Commissioning Doc
section | Approval / Witnessing
checkpoint | Tests conducted by
checkpoint | Tests witnesses/approved by
checklist | Upload L4 Commissioning Doc
section | Approval / Witnessing
checkpoint | Tests conducted by
checkpoint | Tests witnesses/approved by