## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | 22240c98-5de8-4c04-8e65-1082f4b1ea10 |  | checklist | L2 Installation QAQC Procedure - SLA Sensor |  |  |  |  | Yes | L2 Installation QAQC Procedure - SLA Sensor | 2e7244ed-cd1a-4b46-be0e-b4680e137554
checkpoint-group | 2ad1b634-0c47-4aea-9933-d5fc965b7fef |  | section | Reference Documents
checkpoint-no-status | 42ba5d85-d185-4d4c-83bf-9ac8999ddca2 |  | checkpoint | Issued For Construction SLA Location and Mount
checkpoint-group | 82c429c6-2d5c-4058-b2d1-522e1bea5fe7 |  | section | Visual & Pre Inspection
checkpoint-status | 297b4c2f-d4b6-4727-93db-c7b63edac1a9 |  | checkpoint | Inspection with final drawing design- Is Sensor mounted using correct mount
checkpoint-status | fac70996-d181-4b1a-9cc9-b23906158a16 |  | checkpoint | Inspection with final drawing design- Is Sensor mounted in correct locations
checkpoint-status | fc131a46-c925-4d33-8c67-180af3cfc271 |  | checkpoint | Inspect Sensor mount to be free of paint chips and scratches
checkpoint-status | 23ea658e-b454-4e14-b9c5-57e0f7d1edf5 |  | checkpoint | Sensor label to be installed, Equipment ID correct, spelling and grammar correct
checkpoint-group | be7222cf-1a0c-4af5-bf6d-9eb61b4bef81 |  | section | Approval / Witnessing
checkpoint-status | a9f46546-ddd1-4d1b-964d-f69c0a5da74d |  | checkpoint | Tests conducted by
checkpoint-status | 60cec58a-835b-412d-84cb-4805df506f72 |  | checkpoint | Tests witnesses/approved by
checklist-sectioned | 9833215a-a729-41e3-8a69-a52cdbcdd504 |  | checklist | L2 Installation QAQC Procedure - LLI Cabling |  |  |  |  | Yes | L2 Installation QAQC Procedure - LLI Cabling | 637c3531-9465-4686-a6d8-9c9a259683d1
checkpoint-group | 7eee0a8a-4558-41fc-ab46-1e0bd6b1cda5 |  | section | Visual & Pre Inspection
checkpoint-status | 6cdd85c7-e0ad-494d-a59c-69a2ffc8fe26 |  | checkpoint | Cable type aligns with IFC-issue documentation
checkpoint-status | f892cca2-57fa-4266-9686-1a9389ad4cbf |  | checkpoint | Cable is free of visible damage or defects
checkpoint-status | 14429429-da0d-498f-a7da-364351852940 |  | checkpoint | Cable entry to Outstation is through bottom and free from sharp edges or glanded
checkpoint-status | 1356b132-0504-4688-b8e2-c1106e897891 |  | checkpoint | Cable Terminations is as per IFC-issue Cable Schedule
checkpoint-status | 19646a91-593a-4fd0-8aa4-7c37bfc9dbfd |  | checkpoint | Wire point-point testing (continuity tester) is complete as per IFC-issue Cable Schedule
checkpoint-status | 2a3007cf-e992-4a62-84c7-b7b33fbda413 |  | checkpoint | Cable is installed correctly on Cable containment/management
checkpoint-status | 7cb3bdfb-7453-41ad-9220-278031759364 |  | checkpoint | Cable Labels in place as per IFC-issue Cable Schedule
checkpoint-status | 374be5bf-bb8e-40d1-835e-7961df716690 |  | checkpoint | Wire Labels in place as per IFC-issue Cable Schedule
checkpoint-status | 792da3dd-1816-461b-9501-73246387b073 |  | checkpoint | Cable screen earth/drain is connected - one end only
checkpoint-status | bcd3a9ea-d865-4603-a7f4-705a2b6d6c54 |  | checkpoint | All spare cores insulated and secured within Duct
checkpoint-group | a25dcf38-4195-436b-bd69-38db92176ab1 |  | section | Pre-Energisation Electrical Testing...24VDC power cabling only
checkpoint-status | 2f9cc03b-2f12-4d7d-acfd-eee028e11de5 |  | checkpoint | Insulation Resistance Pos to Neg, Megohms (Pass = >0.5Megohm @250VDC)
checkpoint-status | 6c81b1a8-526d-4b6e-9a2f-c4106d625374 |  | checkpoint | Insulation Resistance Pos-E, Megohms (Pass = >0.5Megohm @250VDC)
checkpoint-status | c8b94cb9-a12f-4350-93b2-21b28cc178de |  | checkpoint | Insulation Resistance Negative-E, Megohms (Pass = >0.51Megohm @250VDC)
checkpoint-group | 67d0e009-1d24-4420-b51c-c2bc103cb352 |  | section | Approval / Witnessing
checkpoint-status | 47da7157-815a-421d-b17c-1a4de5255c0a |  | checkpoint | Tests conducted by
checkpoint-status | c8e2d207-3c21-4809-8a4d-b9ec2e234119 |  | checkpoint | Tests witnesses/approved by
checklist-sectioned | 0844917f-7f03-4aab-ad93-bbb5270818fa |  | checklist | L2 Installation QAQC Procedure - RS485 Cabling |  |  |  |  | Yes | L2 Installation QAQC Procedure - RS485 Cabling | 7ad05f9d-7d49-4f94-8fbb-a7924c21e84e
checkpoint-group | 2f0734cb-c0bb-484a-b026-ef3fa28c8f0d |  | section | Visual & Pre Inspection
checkpoint-status | 88e35ab3-3c1b-4802-897f-02067ac28979 |  | checkpoint | Cable type aligns with IFC-issue documentation
checkpoint-status | 947ba0b1-0c1b-4c49-9d20-98e55cf04ff1 |  | checkpoint | Cable is free of visible damage or defects
checkpoint-status | df804550-0807-48b6-a19e-0e514461eeb6 |  | checkpoint | Cable entry to Outstation is through bottom and free from sharp edges or glanded
checkpoint-status | 6d00765a-82fc-4068-bc7a-34b0886c95b8 |  | checkpoint | Cable Terminations is as per IFC-issue Cable Schedule
checkpoint-status | 74ba5a5e-bd63-4cba-b040-d0ba875c1e4a |  | checkpoint | Cable is installed correctly on Cable containment/management
checkpoint-status | e731a104-af0a-4b89-bb5d-0111873347a0 |  | checkpoint | Cable Labels in place as per IFC-issue Cable Schedule
checkpoint-status | 3a7dffe0-4ca2-44d5-acb4-183f03f9212c |  | checkpoint | Wire Labels in place as per IFC-issue Cable Schedule
checkpoint-status | f3ffb695-af8d-4f8a-b0b5-93096e19250f |  | checkpoint | Cable screen earth/drain is connected - one end only
checkpoint-group | 7d65e70b-5089-4551-9fc2-e172af6b32fd |  | section | Approval / Witnessing
checkpoint-status | f9da3d99-9622-46c5-a2f3-61f91601d695 |  | checkpoint | Tests conducted by
checkpoint-status | 7cadb373-28e9-4b13-ae53-50f40bdb231c |  | checkpoint | Tests witnesses/approved by
checklist-flat | e3e79780-6196-4e62-abbe-d13ff2d84bfb |  | checklist | L3 |  |  |  |  | Yes | Upload L3 Commissioning Doc | 96093337-2986-4004-bba0-a3dbab96d0e6
checkpoint-status | 250e2523-4b68-47e3-9439-89364b20ac9a |  | checkpoint | Tests conducted by
checkpoint-status | 42020c46-e2d0-4cb9-8208-ab9e8cb2b311 |  | checkpoint | Tests witnesses/approved by
checklist-flat | ca61e376-1ddb-49c7-9079-1c26db411077 |  | checklist | L4 |  |  |  |  | Yes | Upload L4 Commissioning Doc | b51bb465-8700-4bbb-944d-d75f60d86890
checkpoint-status | ebfb5de3-5038-484a-b6d8-f725c8941f54 |  | checkpoint | Tests conducted by
checkpoint-status | 5faa447c-50c2-40f4-8bf5-1f627f25f553 |  | checkpoint | Tests witnesses/approved by
checklist-sectioned | 7426c569-21b9-4c43-9cde-0218464c4a85 |  | checklist | L1 Factory Acceptance Test Results (CR): OS |  |  |  |  | Yes | L1 Factory Acceptance Test Results (CR): OS | cc65e090-5abd-4c8d-846f-2fad6587597c
checkpoint-group | 7ad07c78-9d2d-4ff1-b12a-addfd889ed20 |  | section | Reference Documents
checkpoint-no-status | 0a0c64dd-5bd9-49c5-b186-b67d6e03ff7b |  | checkpoint | Issued For Construction Drawing Set
checkpoint-group | fefa7053-a59a-4a68-b8d5-c97f8e289e30 |  | section | Visual & Pre Inspection
checkpoint-status | b1850064-8048-4ae0-9d5b-bde531218630 |  | checkpoint | Inspection with final drawing design
checkpoint-status | 45f2482d-9b78-46cb-899c-01ea50cbb8e6 |  | checkpoint | Paint, hinges, door handles/locks operable and of satisfactory appearance
checkpoint-status | d44bb075-51d1-420c-998c-fc8fd342dbc8 |  | checkpoint | Gland plates — IP barrier and screws installed correctly
checkpoint-status | 91dfbe7e-83d1-4cd3-9f84-3d128f71b95c |  | checkpoint | Circuit breakers installed as per design
checkpoint-status | 43f39c4f-98ea-4434-9fdc-36f009c1f38d |  | checkpoint | Control PSU’s and Diode Module installed as per design
checkpoint-status | 60086145-f4b9-4993-bf45-b3e1341e4635 |  | checkpoint | Main switch installed — type and size
checkpoint-status | 486492dc-7cea-460a-9ae7-f25cbb664396 |  | checkpoint | Functional Earth bar installed
checkpoint-status | b630079f-864d-4361-82d7-39044cfa36ff |  | checkpoint | Power terminals correct and tightened
checkpoint-status | 341cb101-b52a-41c9-9fa6-531b6132e5cb |  | checkpoint | Control terminals installed and tight as per design
checkpoint-status | 85621b4e-cefb-4d88-8213-02437bf42b63 |  | checkpoint | All components installed as per design
checkpoint-status | 4e0401ad-7462-41ec-9568-a8f6e19edd32 |  | checkpoint | Ethernet switches/gateway patch leads installed as per schedule
checkpoint-status | f183747a-0883-4f8f-aebf-2c5ceaab1800 |  | checkpoint | Power panel wiring size and colour as per design
checkpoint-status | 9b3e9092-f9ba-40e2-b7c4-0943c077afe7 |  | checkpoint | Control panel wiring size and colour as per design
checkpoint-status | d611e959-3013-4a3e-ab99-d8fb5965f930 |  | checkpoint | Control panel wiring ferruled as per design
checkpoint-status | bf57ad55-b7b1-49ab-b736-380954957379 |  | checkpoint | Earthing to all necessary points connected and earth continuity test performed
checkpoint-group | 99de172e-adce-46b6-8217-6401bb49ced8 |  | section | Pre-Energisation Electrical Testing
checkpoint-status | df76d4a6-d8ea-46a1-8d05-b6f30833dea4 |  | checkpoint | Insulation Resistance L1-E, (>1 Megohm = Pass)
checkpoint-status | 8f08a709-26b0-403c-a2e4-2f05e96b611c |  | checkpoint | Insulation Resistance L1-N, (>1 Megohm = Pass)
checkpoint-status | 55b6969b-fa4f-4017-9869-293c88ee1796 |  | checkpoint | Insulation Resistance N-E, (>1 Megohm = Pass) *ENSURE ALL PROTECTIVE EARTHS ARE DISCONNECTED FROM ELECTRONICS
checkpoint-status | 3aa4380d-c3fb-4539-89cf-a6e0d695e0ff |  | checkpoint | Check Earth Continuity to all metallic parts (Pass=<.5ohm )
checkpoint-group | e83c6c89-8632-42c5-bf6e-e75c937b69ab |  | section | Energised Function Testing
checkpoint-status | 84eeba2a-2bed-4405-8a62-b22ec31c8258 |  | checkpoint | All powered components have correct power supply (test before energization)
checkpoint-status | 1ee0de2d-7915-49d8-9ad4-78adadeb6aa0 |  | checkpoint | All MCB’s and terminals have correct power supplies
checkpoint-status | 10c62547-cab1-48ec-83dd-a56e02066fb4 |  | checkpoint | Field MCB’s isolate associated terminals
checkpoint-status | 1fd9b200-8356-46a8-a913-3027dc35d2ad |  | checkpoint | All devices have correct voltage at terminals
checkpoint-status | 04f83e98-c795-4e17-b60b-ab313def5c92 |  | checkpoint | Ethernet switches patch leads installed if required
checkpoint-status | 129f31c5-d3e3-42b2-81e5-30414aa7be37 |  | checkpoint | Protocol Converter/Gateway patch leads installed if required
checkpoint-status | c289a602-9df5-4b7e-a372-2344289a5bb5 |  | checkpoint | IO Module patch leads installed if required
checkpoint-group | ac4fbf14-858a-4919-bfc0-570a83ad53dc |  | section | Final Inspection
checkpoint-status | 20121f7b-8b8e-44a9-9f34-32cb17a91ebb |  | checkpoint | Engraved labels correct and installed
checkpoint-status | 67ace65b-2408-47d4-8b15-11e235ee03d7 |  | checkpoint | Clean Switchboard (free of debris and swarf)
checkpoint-status | 5e4b3b5c-d0eb-46ce-afe2-6dd12f544cc1 |  | checkpoint | Schematic drawing inside compartment
checkpoint-status | 53a5fef0-a65f-42d3-a2ad-9f0e0eba9660 |  | checkpoint | Equipment missing - Comment as applicable
checkpoint-group | 005d11ad-33d5-420c-abde-6cf0cad1ed7a |  | section | Approval / Witnessing
checkpoint-status | 3c5afe42-7f84-42e3-b0b4-c4923f6ae0d1 |  | checkpoint | Tests conducted by
checkpoint-status | 8b29be02-4775-4327-b02a-d1b3a59c3a41 |  | checkpoint | Tests witnesses/approved by
checklist-flat | 1ebfe173-9ac1-4f65-8132-80f5bc12d6a8 |  | checklist | Fluke Linkware Report Attached |  |  |  |  | Yes | Fluke Linkware Report Attached | deb4f1b5-0a85-43e6-b8c5-d7281cbf8385
checkpoint-status | 254290b1-84be-433c-a48f-29bd3e1b7cff |  | checkpoint | FLUKE LINKWARE Report Attached
checklist-sectioned | 6574fcca-0d78-4f27-a5a6-b33fdd2b62c1 |  | checklist | OS Reference docs |  |  |  |  | Yes | OS Reference docs | ed3dc958-1015-444f-b79c-1d36f12f049b
checkpoint-group | 31dab1f9-be22-4a1e-8907-b5662b8c4175 |  | section | Reference Documents
checkpoint-no-status | d1f1f8fc-2c37-404f-a107-9d840751c6a2 |  | checkpoint | Issued For Construction Drawing Set
checkpoint-no-status | 1f4f72c3-28cb-463d-b52e-8fa0bb0af471 |  | checkpoint | Issued For Construction OS Locations
checkpoint-no-status | bfda77c9-c7dd-4f0b-a2f1-a02cab82590e |  | checkpoint | Issued For Construction Cable Schedule
checklist-sectioned | 6a510170-4c1c-4c85-8a1b-77e1671a928e |  | checklist | L2 Installation QAQC Procedure - Outstation |  |  |  |  | Yes | L2 Installation QAQC Procedure - Outstation | f8ef503d-1ca4-4b50-b3e0-cddc5546a43b
checkpoint-group | c7cd9093-8674-4cc1-995f-e83585981b23 |  | section | Visual & Pre Inspection
checkpoint-status | 84331bc7-f719-48d5-86b6-fd5592c60f64 |  | checkpoint | Inspection with final drawing design- Is Panel location correct to drawings
checkpoint-status | 98c32727-3c52-406d-ba40-12403a402434 |  | checkpoint | Inspection with final drawing design- Is Panel layout correct to drawings
checkpoint-status | b884cabb-d74f-495d-909c-933ac7d30b71 |  | checkpoint | Paint, hinges, door handles/locks operable and of satisfactory appearance
checkpoint-status | 39a72f29-7673-4888-8c70-51fcb573fa71 |  | checkpoint | Power terminals correctly installed and checked for tightness
checkpoint-status | f4e01557-93e7-470d-912a-d973f9d6529d |  | checkpoint | Control terminals correctly installed and checked for tightness
checkpoint-status | 70f3fbc2-3e4a-42f1-878f-79ae2bbdf884 |  | checkpoint | Door swing not impeded by equipment (1000mm clearance required from edge of open door)
checkpoint-status | 27351e95-9486-4ebf-b9a8-4413c506d8a6 |  | checkpoint | Earthing to all necessary points connected
checkpoint-status | 9ff3e4b2-0417-490e-ab49-765bea086977 |  | checkpoint | Outstation mounted securely
checkpoint-status | dc73a4af-cf25-4223-96b2-09cc1f4ae2c3 |  | checkpoint | All caution and warning labels in place
checkpoint-group | 751a1eab-b3a4-4382-b049-c8d2a84f05e8 |  | section | Final Inspection
checkpoint-status | dcf57b7d-172a-47e0-8dd4-7772d4d75160 |  | checkpoint | Engraved labels installed, Equipment ID correct, spelling and grammar correct
checkpoint-status | f14e4444-2d8a-4541-93a7-d4eb72ea89e9 |  | checkpoint | Clean Switchboard (free of debris and swarf)
checkpoint-status | dbdd187e-4db7-4d44-b63f-58657485b01f |  | checkpoint | Schematic drawing inside compartment
checkpoint-status | 6d042525-53a6-4bbd-a727-ea47fccd3b5f |  | checkpoint | Equipment missing - Comment as applicable
checkpoint-group | e547a59f-cb7d-4dce-b540-70207c83f2df |  | section | Approval / Witnessing
checkpoint-status | 9ad4a9b9-7f75-4d01-98a5-7be724560883 |  | checkpoint | Tests conducted by
checkpoint-status | 63795df8-d238-4387-b350-154fddb7aaed |  | checkpoint | Tests witnesses/approved by