## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-240-CIV-Ferris-Under track crossing - Ausnet Gas and Telstra | itp |  |  |  |  | ITP-240-CIV-Ferris-Under track crossing - Ausnet Gas and Telstra Rev 0
section | 1. Referenced Documentation
checkpoint-no-value | Referenced Documentation
label | Document Title: ITP-240-CIV-Ferris-Under track crossing - Ausnet Gas and Telstra
label | ITP Description: Under track crossing - Ausnet Gas and Telstra
label | Discipline (e.g. CIV/STR/RAIL): 240-CIV
label | Revision Number: 0
label | Revision Date: 4/02/2025
label | ITP created by: Joanthan Kogan
label | ITP approved for use by: Pradeep Talasila
label | 1.01 - Non Dependent
label | Reference - AS 4799-2000 Installation of underground utility services ad pipelines within railway boundaries
label | 1.02 - Non Dependent
label | Reference - D/17/62901 Design Requirements & Guidelines - Civil Works on, under or over VicTrack Land
label | 1.03 - Non Dependent
label | Reference - NIST 012.2 - Specification for Signalling Supply, Construction and Installation (V/Line)
label | 1.04 - Non Dependent
label | Reference - AS 4142 Fibre Ropes, installed and anchored in the pit
label | 1.05 - Non Dependent
label | Reference - NIST 012.2.1 - Standard for Construction of Cable Route and Signalling Civil Works (V/Line)
label | 1.06 - Non Dependent
label | Reference - NIST-2706 - Inspection and Assessment Track Geometry (V/Line)
label | 1.07 - Non Dependent
label | Reference - VRIOGS 012.2.1. Settlement Monitoring during construction
label | 1.08 - Non Dependent
label | Reference - VICTRACK STANDARD TS-SP-013 installation of the encasing pipe
section | 2. Preliminaries
checkpoint | 2.01 - Materials - Gas Jacking Pipe
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202
label | Acceptance Criteria - Confirm that the GRP pipes delivered to site meet the Pipe Specifications:
label | — Internal Dia: 389mm
label | — Outside Dia: 427mm
label | — Material: GRP Pipe
label | ○ Specification & Grade: DM427 SN100,000 N/m²­­
label | — Wall Thickness: 19mm
label | — Maximum Working Pressure: N/A
label | — Joint Type: Stainless Steel Collar with EPDM Seal
label | — Pipe Coating: N/A
label | — Cathodic Protection: N/A
label | Method - Document Review
label | Frequency - Prior to Commencement
label | Category - HP
label | Responsibility - SE
label | Verifying Documents - Material Compliance Certificate
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.02 - Materials - Comms Jacking Pipe
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0203
label | Acceptance Criteria - Confirm that the GRP pipes delivered to site meet the Pipe Specifications:
label | — Internal Dia: 389mm
label | — Outside Dia: 427mm
label | — Material: GRP Pipe
label | ○ Specification & Grade: DM427 SN100,000 N/m²­­
label | — Wall Thickness: 19mm
label | — Joint Type: Stainless Steel Collar with EPDM Seal
label | — Pipe Coating: No Coating
label | — Electrically Continuous: N/A
label | — Cathodic Protection: N/A
label | Method - Document Review
label | Frequency - Prior to Commencement
label | Category - HP
label | Responsibility - SE
label | Verifying Documents - Material Compliance Certificate
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.03 - Materials - Draw ropes
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0002
label | Acceptance Criteria - All conduits must have minimum of one 6mm polypropylene draw rope to AS4142.
label | Method - Document review/ Visual
label | Frequency - Prior to commencement
label | Category - HP
label | Responsibility - PE/SE
label | Verifying Documents - Material compliance certificate
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.04 - Materials - Comms Carrier conduits
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0203
label | Acceptance Criteria - Conduit fittings shall be the same type and material as the conduit.
label | ○ Comms conduits to be:
label | — Internal Dia: 93.3mm
label | — Outside Dia: 110.5mm
label | — Material: White PE100 Branded "TELSTRA"
label | ○ Specification & Grade: OD110 PE100 SDR13
label | — Wall Thickness: 8.6mm
label | — Joint Type: Butt weld
label | — Pipe Coating: N/A
label | — Cathodic Protection: N/A
label | Method - Document review/ Visual
label | Frequency - Prior to commencement
label | Category - HP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP/ Material compliance certificate.
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.05 - Materials - Gas Encasing pipe
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202
label | Acceptance Criteria - Confirm that the Gas Encasing pipes delivered to site meet the Pipe Specifications:
label | — Internal Dia: 256mm
label | — Outside Dia: 315mm
label | — Material: Polyethylene
label | ○ Specification & Grade: DN315 PE100 SDR11
label | — Wall Thickness: 28.6mm
label | — Maximum Working Pressure: 700kPa
label | — Joint Type: Burtt Weld
label | — Pipe Coating: No Coating
label | — Electrically Continuous: N/A
label | — Cathodic Protection: N/A
label | Method - Document review/ Visual
label | Frequency - Prior to commencement
label | Category - HP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP/ Material compliance certificate.
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.06 - Materials - Gas Carrying pipe
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202
label | Acceptance Criteria - Confirm that the Gas Carrier pipes delivered to site meet the Pipe Specifications:
label | — Internal Dia: 145mm
label | — Outside Dia: 180mm
label | — Material: Polyethyene
label | ○ Specification & Grade: DN180 PE100 SDR11
label | — Wall Thickness: 16.4mm
label | — Maximimum Working Pressure: 700kPa
label | ○ Joint Type: Burtt Weld
label | — Pipe Coating: No Coating
label | — Electrically Condinuous: N/A
label | — Cathodic Protection: N/A
label | Method - Document review/ Visual
label | Frequency - Prior to commencement
label | Category - HP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP/ Material compliance certificate.
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.07 - Materials - Grout
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202
label | Acceptance Criteria - Diameter of bored hole to jacking pipe shall not exceed diameter of encasing by more than 50mm. annulus to be grouted with an approve controlled low strength material (CLSM) of minimum 2MPa strength material
label | Method - Document Review
label | Frequency - Prior to Commencement
label | Category - HP*
label | Responsibility - SE
label | Verifying Documents - Material Compliance Certificate and TDS
date | Date Completed:
checkpoint | 2.08 - Marker Post and Marker Plate
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202 & MRP-103-C-AUR-DRG-65-RBK-CUT-0203, AS4799-2000 cl 3.10
label | Acceptance Criteria - Be of non-combustible material for the marker plates and of at least fire-resistant material for the pole.
label | Method - Document Review
label | Frequency - Prior to Commencement
label | Category - WP
label | Responsibility - SE
label | Verifying Documents - Material Compliance Certificate
date | Date Completed:
checkpoint | 2.09 - Poly Welding Qualification (if applicable)
label | Reference - IFC Drawings
label | Acceptance Criteria - HDPE welder qualifications to be supplied
label | Method - Document Review
label | Frequency - Prior to Commencement
label | Category - WP
label | Responsibility - SE
label | Verifying Documents - Welding Certificate
date | Date Completed:
section | 3. Pre-construction Activities
checkpoint | 3.01 - Survey Set-out
label | Reference - IFC Drawings: MRP-DPK-103-00-CUT-0065, MRP-103-C-AUR-DRG-65-RBK-CUT-0202 & MRP-103-C-AUR-DRG-65-RBK-CUT-0203
label | Acceptance Criteria - Set out line and level of drilling works.
label | ○ Survey to mark out existing services.
label | ○ Must maintain a min. of 600mm clearance to any existing service and a min. 3m clearance to any Railway Structure UON.
label | ○ GFRP must achieve a min. 1200mm vertical clearance to tracks and minimum 800mm to surface level. Check FSL of track and ground.
label | Method - Measure, Visual
label | Frequency - Each element
label | Category - IP
label | Responsibility - Surveyor, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
section | 4. Construction Activities
checkpoint | 4.01 - Drill rig set out
label | Reference - NA
label | Acceptance Criteria - Location as per current Drill shot plans
label | Method - Visual
label | Frequency - Prior to commencement
label | Category - VP
label | Responsibility - SE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.02 - Ground Conditions
label | Reference - IFC Design Report
label | Acceptance Criteria - Assumed ground conditions are as per site geotechnical report.
label | ○ Geotech Engineer to be immediately notified if the excavations encounter different materials than expected
label | Method - Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - Photos, Sign ITP
date | Date Completed:
checkpoint | 4.03 - Pilot Hole Drilling
label | Reference - IFC Drawings & SAP
label | Acceptance Criteria - Pilot hole to be drilled and fully supported at all times.
label | Method - Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - Sign ITP
date | Date Completed:
checkpoint | 4.04 - Pipe Jacking Monitoring
label | Reference - IFC Drawings & SAP
label | Acceptance Criteria - Inclination and path to be monitored as per design alignment.
label | ○ Ensure bore hole blockage and fluid losses are detected and addressed by:
label | ○ Monitoring drilling fluid volumes, monitoring annular pressureand monitoring cutting returns.
label | Method - Measure
label | Frequency - Continuously through installation
label | Category - WP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - Sign ITP
date | Date Completed:
checkpoint | 4.05 - Jacking Pipe installation
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202 & MRP-103-C-AUR-DRG-65-RBK-CUT-0203, D/17/62901
label | Acceptance Criteria - DN427 GRP Jacking Pipe to be reamed, then immediately followed by pipe being pulled through. Bore should remain supported at all times.
label | ○ Diameter of bore is not to exceed diameter of pipe by more than 50mm.
label | ○ Pipes to be installed in straight sections with no excessive bending in the pipes
label | Method - Visual and Measure
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - Sign ITP
date | Date Completed:
checkpoint | 4.06 - ULX1 - Gas Encasing Pipe Installation
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202
label | Acceptance Criteria - Install thininsulators @ 1000mm centres between Encasing pipe and Jacking pipe to ensure centralisation
label | Method - Visual
label | Frequency - All Pipe
label | Category - VP
label | Responsibility - SE
label | Verifying Documents - Sign ITP.
date | Date Completed:
checkpoint | 4.07 - ULX1 - Gas Carrier Pipe Installation
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202 & MRP-103-C-AUR-DRG-65-RBK-CUT-0203
label | Acceptance Criteria - Min depth as per IFC drawings.
label | ○ Install thininsulators @ 1000mm centres between Encasing pipe and carrier pipe to ensure centralisation
label | Method - Visual
label | Frequency - All Pipe
label | Category - VP
label | Responsibility - SE
label | Verifying Documents - Sign ITP.
date | Date Completed:
checkpoint | 4.08 - ULX2 - Conduit Installation and Trace Wire
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0203
label | Acceptance Criteria - Min depth as per IFC drawings.
label | ○ All bored communications conduits shall include the installation of stainless steel 3mm trace wire.
label | Method - Visual
label | Frequency - All Pipe
label | Category - VP
label | Responsibility - SE
label | Verifying Documents - Sign ITP.
date | Date Completed:
checkpoint | 4.09 - Track Monitoring and Ground Settlement
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0002, MRP-103-C-AUR-DRG-65-RBK-CUT-0202 & MRP-103-C-AUR-DRG-65-RBK-CUT-0203
label | ○ NIST-2706
label | ○ MRP-000-MRPA-PLN-XPM-0055
label | Acceptance Criteria - Both tracks are to be monitored at 2m intervals either side of the centreline of the under bore for 10m either side of the bore centreline, with additional tilt sensors at 5m intervals up to 20m either side of the bore centreline.
label | ○ Settlement to be monitored with the escalation matrix on the monitoring plan to be followed. <5mm = no action. 5 to 9mm = notify v/line for inspection. 10 to 14mm = stop works and rectify. >14mm = halt train operations.
label | Method - Measure and Visual
label | Frequency - Continuously through installation
label | Category - IP
label | Responsibility - SE/Site Supervisor/Survey
label | Verifying Documents - Sign ITP
date | Date Completed:
checkpoint | 4.10 - Conduit Welding
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202 & MRP-103-C-AUR-DRG-65-RBK-CUT-0203
label | Acceptance Criteria - Joints are to be butt welded.
label | ○ Weld map to be supplied and identify unique joint numbers.
label | ○ Butt Welding records to be supplied.
label | Method - Record and Review
label | Frequency - All Joints
label | Category - IP
label | Responsibility - SE/Site Supervisor/Survey
label | Verifying Documents - Sign ITP, Butt Welding Records
date | Date Completed:
checkpoint | 4.11 - Vent Pipe Installation for ULX1 Gas
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202
label | Acceptance Criteria - DN50 PE Gas Ven to be installed by Asset owner (Downer) a minimum of 3m away from rail assets
label | Method - Record and Review
label | Frequency - All Pipe
label | Category - HP*
label | Responsibility - SE/SPE
label | Verifying Documents - Sign ITP
date | Date Completed:
checkpoint | 4.12 - Grouting
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202 & MRP-103-C-AUR-DRG-65-RBK-CUT-0203
label | Acceptance Criteria - Diameter of bored hole to jacking pipe shall not exceed diameter of encasing by more than 50mm. annulus to be grouted with an approve controlled low strength material (CLSM) of minimum 2MPa strength material
label | Method - Review
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - Sign ITP
date | Date Completed:
checkpoint | 4.13 - Draw rope
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0002
label | Acceptance Criteria - The draw rope shall be continuous for the complete length of the conduit run.
label | ○ All draw ropes must be continuous between pits and have 2m slack in the pit.
label | ○ Draw ropes to be restrained in each pit to prevent them from being inadvertently pulled into the conduits
label | Method - Visual
label | Frequency - All Pipe
label | Category - VP
label | Responsibility - SE
label | Verifying Documents - Sign ITP.
date | Date Completed:
checkpoint | 4.14 - Mandrelling
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0002
label | Acceptance Criteria - Plug with 90% of the pipe diameter to be pulled through each conduit to ensure the conduit hasn't been compressed.
label | Method - Record and Review
label | Frequency - All Pipe
label | Category - HP*
label | Responsibility - SE/SPE
label | Verifying Documents - Sign ITP
date | Date Completed:
checkpoint | 4.15 - Tracer Wire
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0002
label | Acceptance Criteria - All bored communication conduits shall include the installation of a stainless steel trace wire of 3mm diameter.
label | Method - Record and Review
label | Frequency - All Pipe
label | Category - HP*
label | Responsibility - SE/SPE
label | Verifying Documents - Sign ITP
date | Date Completed:
checkpoint | 4.16 - Pipe Completion
label | Reference - IFC Drawings
label | Acceptance Criteria - End of encasing pipe to be sealed at each end as per IFC drawings
label | Method - Review
label | Frequency - Each end of pipe
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - Delivery dockets, Sign ITP
date | Date Completed:
checkpoint | 4.17 - Reinstatement
label | Reference - IFC Drawings
label | Acceptance Criteria - Entry pits, exit pits and trenches to be backfilled using approved fine crushed rock material. Backfill material shall be compacted to the same density as adjacent material or as specified.
label | Method - Review
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor, VicTrack
label | Verifying Documents - Sign ITP
date | Date Completed:
checkpoint | 4.18 - Marker Post Installation
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202 & MRP-103-C-AUR-DRG-65-RBK-CUT-0203, AS4799-2000
label | Acceptance Criteria - Marker posts to be installed at every 200m intervals, any change in direction and at the entry and exit points of VicTrack property.
label | ○ Marker Posts to be placed facing the rail tracks within VicTrack property
label | ○ 50mm x 8mm Galvanised Steel Plate Welded to 50mm Ø Galvanised Post with as Capped top protruding to the air and flatted end in concrete
label | ○ Marker plate riveted to post with 8mm insulated aluminium rivets.
label | ○ Post to be extend 500mm in ground and be concreted in a 300mm Ø footing, concrete to extend out of ground
label | Method - Review
label | Frequency - Entry and Exit Points
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - Sign ITP, Delivery Dockets
date | Date Completed:
section | 5. Post-construction Activities
checkpoint | 5.01 - As-built Survey
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0202 & MRP-103-C-AUR-DRG-65-RBK-CUT-0203
label | Acceptance Criteria - Survey as built report to be compiled.
label | ○ Must maintain a min. of 600mm clearance to any existing service and a min. 3m clearance to any Railway Structure UON.
label | ○ Sleeve must achieve a min. 2000mm vertical clearance to tracks.
label | Method - Document Review
label | Frequency - Each element
label | Category - IP
label | Responsibility - Surveyor, SE/PE/SPE
label | Verifying Documents - Survey As Report
date | Date Completed:
checkpoint | 5.02 - Track Inspection and Maintenance
label | Reference - IFC Drawings: MRP-103-C-AUR-DRG-65-RBK-CUT-0002, MRP-103-C-AUR-DRG-65-RBK-CUT-0202 & MRP-103-C-AUR-DRG-65-RBK-CUT-0203
label | ○ NIST-2706
label | ○ MRP-000-MRPA-PLN-XPM-0055
label | Acceptance Criteria - Once works are completed, survey to confirm settlement of the track and ground are within the predicted design settlement values.
label | ○ Not > 15mm
label | ○ To be provided to V/Line prior track hand back.
label | ○ Where track has been disturbed beyond the tolerances, realignment and/or maintenance is required by a qualified sub-contractor.
label | ○ Attach: Track Inspection & Maintenance plan
label | ○ Attach: Track Measuring Sheet
label | Method - Document Review
label | Frequency - Each element, Where applicable,
label | Category - IP
label | Responsibility - Surveyor, SE/PE/SPE
label | Verifying Documents - Survey As Built Report
date | Date Completed:
checkpoint | 5.03 - Red-line / As-constructed IFC Drawings
label | Reference - MRPA Quality Management Plan
label | Acceptance Criteria - All RFIs, NCRs and changes to the IFC drawings are captured on a controlled drawing set marked "Red-line", "As-built" or similar.
label | Method - Document Review
label | Frequency - Once, after construction of the design package
label | Category - WP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - Red Line Drawing Pack
date | Date Completed:
checkpoint | Final Inspection
label | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
textbox | Name:
textbox | Position:
textbox | Date Completed:
signoff | Sign ITP