## Folder Structure
Tier 1 | Tier 2 | Tier 3 | Tier 32 | Tier 4 | Tier 5 | Instruction to CONQA | Checklist Name
Chint J#43687 & J#45005
Solar Farm J#43687 - Large Room
Toolbox Meetings
|  |  |  | Daily Toolbox meetings - Site Installation | checklist | please add: | Toolbox Meeting
Room Construction
|  |  |  | Room Construction Checklist | Sign Off | please add: | Sign Off
|  |  |  | QA Documentation | Sign Off | please add: | Sign Off
Frame Construction
|  |  |  | Frame Construction Checklist | Sign Off | please add: | Sign Off
|  |  |  | Coastal Services QA Documentation | Sign Off | please add: | Sign Off
Floor, Duct Penetrations
Flooring, Penetrations Checklist
[5 empty] | Floor Cable Penetrations | please add: | Create Folder ITR Under construction
[5 empty] | Floor Covering | please add: | Create Folder ITR Under construction
Cable Supports
Cable Support Checklists
[5 empty] | Cable Ladder | please add: | ITR-E-02B Cable Supports Above Ground
[5 empty] | Uni Tray | please add: | ITR-E-02B Cable Supports Above Ground
LV Lighting, Power, DATA & Accessories
MV Room
[5 empty] | Internal 5ft Emergency Light 01 | please add: | ITR-E-64 General Lighting
[5 empty] | Internal 5ft LED Light 02 | please add: | ITR-E-64 General Lighting
[5 empty] | 2 Way Light Switch 01 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | 2 Way Light Switch 02 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Exterior Flood Light 03 | please add: | ITR-E-64 General Lighting
[5 empty] | Emergency Exit Light 04 | please add: | ITR-E-64 General Lighting
Control Room
[5 empty] | Internal 5ft LED Light 05 | please add: | ITR-E-64 General Lighting
[5 empty] | Internal 5ft LED Light 06 | please add: | ITR-E-64 General Lighting
[5 empty] | Internal 5ft LED Light 07 | please add: | ITR-E-64 General Lighting
[5 empty] | Internal 5ft Emergency Light 08 | please add: | ITR-E-64 General Lighting
[5 empty] | 2 Way Light Switch 03 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | 2 Way Light Switch 04 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Emergency Exit Light 09 | please add: | ITR-E-64 General Lighting
[5 empty] | Double Socket Outlet GPO01 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Daylight Sensor 01 | please add: | ITR-E-01 General Electrical Equipment
Office
[5 empty] | Internal 5ft LED Light 10 | please add: | ITR-E-64 General Lighting
[5 empty] | Internal 5ft Emergency Light 11 | please add: | ITR-E-64 General Lighting
[5 empty] | 2 Way Light Switch 05 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | 2 Way Light Switch 06 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Double Socket Outlet GPO02 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Double Socket Outlet GPO03 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Double Socket Outlet GPO04 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Emergency Exit Light 12 | please add: | ITR-E-64 General Lighting
Smoko Room
[5 empty] | Internal 5ft LED Light 13 | please add: | ITR-E-64 General Lighting
[5 empty] | Internal 5ft Emergency Light 14 | please add: | ITR-E-64 General Lighting
[5 empty] | 2 Way Light Switch 07 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | 2 Way Light Switch 08 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Emergency Exit Light 15 | please add: | ITR-E-64 General Lighting
[5 empty] | Exterior Flood Light 16 | please add: | ITR-E-64 General Lighting
[5 empty] | Double Socket Outlet GPO05 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Double Socket Outlet GPO06 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Double Socket Outlet GPO07 | please add: | ITR-E-01 General Electrical Equipment
Toilet
[5 empty] | Internal LED round light 17 | please add: | ITR-E-64 General Lighting
[5 empty] | 1 Way Light Switch 09 | please add: | ITR-E-01 General Electrical Equipment
HVAC
AC01
[5 empty] | Indoor Unit | please add: | ITR-E-55 HVAC System
[5 empty] | Outdoor Unit | please add: | ITR-E-55 HVAC System
[5 empty] | AC Controller | please add: | ITR-E-01 General Electrical Equipment
AC02
[5 empty] | Indoor Unit | please add: | ITR-E-55 HVAC System
[5 empty] | Outdoor Unit | please add: | ITR-E-55 HVAC System
[5 empty] | AC Controller | please add: | ITR-E-01 General Electrical Equipment
Equipment and Installation
Panels
[5 empty] | TCE LV AC Distribution Board | please add: | ITR-E-34A Low Voltage Switch Board
[5 empty] | 33KV RMU Siemens 8DJH | please add: | ITR-E-10 Electrical Equipment Package
[5 empty] | SCADA / Comms panel | please add: | ITR-E-06 Control Panel
[5 empty] | No1 UPS Cabinet | please add: | ITR-E-15 UPS Installation
[5 empty] | No2 UPS Cabinet | please add: | ITR-E-15 UPS Installation
[5 empty] | Fire Panel | please add: | ITR-E-06 Control Panel
[5 empty] | Revenue Metering Panel | please add: | ITR-E-06 Control Panel
[5 empty] | Meteo Control Panel | please add: | ITR-E-06 Control Panel
Pressurization Unit
[5 empty] | Pressurization Unit | please add: | ITR-E-10 Electrical Equipment Package
Earth Bar
[5 empty] | Switchroom Earth bar | please add: | ITR-E-40A Bus Bar
Cable Installation
|  |  |  | A01 | 6.0mm 4C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | A02 | 1.5mm 3C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | A03 | 1.5mm 3C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | A04 | 1.5mm 3C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | U01 | 1.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | U02 | 1.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | U03 | 1.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | D01 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | D02 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | D03 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | D04 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | D05 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | D06 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | D07 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | F01 | SM 0S2 | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | C01 | CAT6 | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  |  | C02 | CAT6 | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  |  | C03 | CAT6 | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  |  | C04 | CAT6 | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  |  | T01 | 2.5mm 12C Firstflex CTP12/2.5 | please add: | ITR-I-21A - Instrument and Control Cables
|  |  |  | T02 | 2.5mm 12C Firstflex CTP12/2.6 | please add: | ITR-I-21A - Instrument and Control Cables
|  |  |  | T03 | 2.5mm 12C Firstflex CTP12/2.7 | please add: | ITR-I-21A - Instrument and Control Cables
|  |  |  | T04 | 2.5mm 12C Firstflex CTP12/2.8 | please add: | ITR-I-21A - Instrument and Control Cables
Building Access
Stairs
[5 empty] | Sign Off | please add: | Sign Off
Platform
[5 empty] | Sign Off | please add: | Sign Off
COC, ESC
|  |  |  | COC | COC | please add: | Certificate of compliance (COC)
|  |  |  | ESC | ESC | please add: | Electrical Safety Certificate (ESC)
|  |  |  | Test Equipment | Test Equipment Details: | please add: | Test Equipment Details:
Punchlist Walkdown
[5 empty] | Sign Off | please add: | Sign Off
Punchlist work Complete Acceptance
[5 empty] | Sign Off | please add: | Sign Off
Switchroom Complete
|  |  |  | Entec Project Engineer | Sign Off | please add: | ITR-E-09 Electrical Switch Rooms
As Built Drawings Complete
|  |  |  | Entec Supervisor | Sign Off | please add: | Sign Off
Workpack Completion Sign Off
|  |  |  | Entec Project Engineer | Sign Off | please add: | Sign Off
|  |  |  | Chint Client representative | Sign Off | please add: | Sign Off
North Power J#45005 - Small Room
Toolbox Meetings
|  |  |  | Daily Toolbox meetings - Site Installation | checklist | please add: | Toolbox Meeting
Room Construction
|  |  |  | Room Construction Checklist | Sign Off | please add: | Sign Off
|  |  |  | QA Documentation | Sign Off | please add: | Sign Off
Frame Construction
|  |  |  | Frame Construction Checklist | Sign Off | please add: | Sign Off
|  |  |  | Coastal Services QA Documentation | Sign Off | please add: | Sign Off
Floor, Duct Penetrations
Flooring, Penetrations Checklist
[5 empty] | Floor Cable Penetrations | please add: | Create Folder ITR Under construction
[5 empty] | Floor Covering | please add: | Create Folder ITR Under construction
Cable Supports
Cable Support Checklists
[5 empty] | Cable Ladder | please add: | ITR-E-02B Cable Supports Above Ground
[5 empty] | Uni Tray | please add: | ITR-E-02B Cable Supports Above Ground
LV Lighting, Power, DATA & Accessories
Lighting Checklist
[5 empty] | Internal 5ft Emergency Light 01 | please add: | ITR-E-64 General Lighting
[5 empty] | Internal 5ft LED Light 02 | please add: | ITR-E-64 General Lighting
[5 empty] | 2 Way Light Switch 01 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | 2 Way Light Switch 02 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Emergency Exit Light 03 | please add: | ITR-E-64 General Lighting
[5 empty] | Emergency Exit Light 04 | please add: | ITR-E-64 General Lighting
[5 empty] | Exterior Flood Light 05 | please add: | ITR-E-64 General Lighting
[5 empty] | Exterior Flood Light 06 | please add: | ITR-E-64 General Lighting
[5 empty] | Daylight Sensor 01 | please add: | ITR-E-01 General Electrical Equipment
Power Checklist
[5 empty] | Double Socket Outlet GPO01 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Double Socket Outlet GPO02 | please add: | ITR-E-01 General Electrical Equipment
Fire and Security
Fire System
[5 empty] | Manual Call Point 01 | please add: | ITR-I-01 Fire and Gas Detection Alarms
[5 empty] | Manual Call Point 02 | please add: | ITR-I-01 Fire and Gas Detection Alarms
[5 empty] | Exterior Becon Sounder 01 | please add: | ITR-I-01 Fire and Gas Detection Alarms
[5 empty] | Exterior Becon Sounder 02 | please add: | ITR-I-01 Fire and Gas Detection Alarms
[5 empty] | Smoke Heat detector 01 | please add: | ITR-I-01 Fire and Gas Detection Alarms
[5 empty] | Smoke Heat detector 02 | please add: | ITR-I-01 Fire and Gas Detection Alarms
Security System
[5 empty] | PIR Sensor 01 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | PIR Sensor 02 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Electronic door lock 01 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Electronic door lock 02 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Swipe Card Reader 01 | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Swipe Card Reader 02 | please add: | ITR-E-01 General Electrical Equipment
Equipment and Installation
Panels
[5 empty] | SCADA / Comms panel | please add: | ITR-E-06 Control Panel
[5 empty] | Cardex Panel | please add: | ITR-E-06 Control Panel
[5 empty] | AC LV DB | please add: | ITR-E-34A Low Voltage Switch Board
[5 empty] | DC Panel | please add: | ITR-E-06 Control Panel
[5 empty] | 110V DC Battery Rack | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | 24V DC Battery Rack | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | 33KV Protection Panel | please add: | ITR-E-01 General Electrical Equipment
[5 empty] | Generator Connection Box | please add: | ITR-E-01 General Electrical Equipment
HVAC
AC01
[5 empty] | Indoor Unit | please add: | ITR-E-55 HVAC System
[5 empty] | Outdoor Unit | please add: | ITR-E-55 HVAC System
[5 empty] | AC Controller | please add: | ITR-E-01 General Electrical Equipment
Cable Installation
|  |  |  | L-001 | 1.5mm 3C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | L-002 | 1.5mm 3C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | L-003 | 1.5mm 3C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | L-004 | 1.5mm 3C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | L-005 | 1.5mm 3C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | L-006 | 1.5mm 3C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | L-007 | 1.5mm 3C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | L-008 | 1.5mm 3C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | L-009 | 1.5mm 3C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | P-001 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | P-002 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | P-003 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | P-004 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | P-005 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | P-006 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | P-007 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | P-008 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | P-009 | 2.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | P-010 | 1.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | P-011 | 1.5mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | P-012 | 25mm 4C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | C-005 | 1.5mm 1 PR | please add: | ITR-I-21A - Instrument and Control Cables
|  |  |  | W575 | 1.5mm 1 PR | please add: | ITR-I-21A - Instrument and Control Cables
|  |  |  | W576 | 1.5mm 1 PR | please add: | ITR-I-21A - Instrument and Control Cables
|  |  |  | W405 | 6mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | W311 | 6mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | W380 | 16mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | W381 | 25mm 2C&E PVC/PVC TPS 90C 0.6/1KV | please add: | ITR-E-05 - Low Voltage Cable
|  |  |  | W391 | 0.5mm 1 PR | please add: | ITR-I-21A - Instrument and Control Cables
|  |  |  | W392 | 0.5mm 1 PR | please add: | ITR-I-21A - Instrument and Control Cables
Earth / Bonding Cables
[5 empty] | 25mm 1c GRN/Y Cardex Panel | please add: | ITR-E-05 - Low Voltage Cable
[5 empty] | 25mm 1c GRN/Y 110VDC Battery Rack | please add: | ITR-E-05 - Low Voltage Cable
[5 empty] | 25mm 1c GRN/Y 110VDC Battery Rack | please add: | ITR-E-05 - Low Voltage Cable
[5 empty] | 25mm 1c GRN/Y Rear Entrance Stairs | please add: | ITR-E-05 - Low Voltage Cable
[5 empty] | 25mm 1c GRN/Y 33KV Protection Panel | please add: | ITR-E-05 - Low Voltage Cable
[5 empty] | 25mm 1c GRN/Y DC Panel | please add: | ITR-E-05 - Low Voltage Cable
[5 empty] | 25mm 1c GRN/Y SCADA/COMMS Panel | please add: | ITR-E-05 - Low Voltage Cable
[5 empty] | 25mm 1c GRN/Y ACDB | please add: | ITR-E-05 - Low Voltage Cable
[5 empty] | 25mm 1c GRN/Y Cable Ladders | please add: | ITR-E-05 - Low Voltage Cable
[5 empty] | 25mm 1c GRN/Y Main Entrance Stairs | please add: | ITR-E-05 - Low Voltage Cable
[5 empty] | 25mm 1c GRN/Y Structural Steel | please add: | ITR-E-05 - Low Voltage Cable
Building Access
Stairs
[5 empty] | Sign Off | please add: | Sign Off
Platform
[5 empty] | Sign Off | please add: | Sign Off
COC, ESC
|  |  |  | COC | COC | please add: | Certificate of compliance (COC)
|  |  |  | ESC | ESC | please add: | Electrical Safety Certificate (ESC)
|  |  |  | Test Equipment | Test Equipment Details: | please add: | Test Equipment Details:
Punchlist Walkdown
[5 empty] | Sign Off | please add: | Sign Off
Punchlist work Complete Acceptance
[5 empty] | Sign Off | please add: | Sign Off
Switchroom Complete
|  |  |  | Entec Project Engineer | Sign Off | please add: | ITR-E-09 Electrical Switch Rooms
As Built Drawings Complete
|  |  |  | Entec Supervisor | Sign Off | please add: | Sign Off
Workpack Completion Sign Off
|  |  |  | Entec Project Engineer | Sign Off | please add: | Sign Off
|  |  |  | TOP Energy Client representative | Sign Off | please add: | Sign Off

## Checklists
Type | Name | Values | Prefix | Postfix | Usage Count | User Addable | Template Name
checklist | JHA - Job Hazard Analysis
section | Job details
checkpoint-no-status | Job details
date | Date:
textbox | Permit No.
textbox | Job No.
textbox | Site
textbox | Activity Location
textbox | Asset:
textbox | Work Details:
section | Prompts for Hazards - Mark all that apply.
checkpoint-no-status | Prompts for Hazards - Mark all that apply.
tickbox | Sparks/Open flame
tickbox | Disabled safety device(s)
tickbox | Uneven surfaces
tickbox | Fatigue, over-exertion
tickbox | Crane movements
tickbox | Moving/Rotating parts
tickbox | Remote area, working alone
tickbox | Conflicting work/SIMOPS
tickbox | Electrical arc flash
tickbox | Sharp objects/materials
tickbox | Restricted/Difficult Entry/Exit
tickbox | Overhead obstacles
tickbox | Ignition sources (other)
tickbox | Access/Egress
tickbox | Water body
tickbox | Live equipment
tickbox | Slippery surfaces
tickbox | Suspended loads
tickbox | Hazardous substances (chemicals)
tickbox | Use of non-intrinsically safe equipment
tickbox | Weather extremes
tickbox | Moving vehicles
tickbox | Task related noise
tickbox | Engulfment
tickbox | General waste
tickbox | Hazardous waste
tickbox | Hazardous/toxic substance, fumes, gas
tickbox | Flammable materials - Gas, liquids, solids
tickbox | Reduced visibility, lighting
tickbox | Electricity
tickbox | Static electricity
tickbox | Work at height
tickbox | Underground services
tickbox | O2 Deficiency/Excess
tickbox | Temperature extremes
tickbox | Heavy objects
tickbox | Radiation
tickbox | Potential energy - Tension/Compression
tickbox | Flying particles/Dust/Objects
tickbox | Vehicle entry
tickbox | Exposure to process temperatures.
section | Prompts for Initial Consequences - Mark all that apply
checkpoint-no-status | Prompts for Initial Consequences - Mark all that apply
tickbox | Falling/Dropped objects
tickbox | Fall from height
tickbox | Trip/Slip/Fall
tickbox | Gas release
tickbox | Pressure release
tickbox | Struck by object
tickbox | Exceeding tool limits
tickbox | Overloading people
tickbox | Unplanned shutdown
tickbox | Exposure to O2 deficiency/excess
tickbox | Exposure to hazardous substance
tickbox | Entanglement
tickbox | Flying objects
tickbox | Loss of control
tickbox | Loss of containment
tickbox | Excess exposure to Emissions, dust, fumes, noise, fibres, heat
tickbox | Loss of structural integrity
tickbox | Equipment failure
tickbox | Uncontrolled ignition source
tickbox | Collision
tickbox | Ignition/Fire
tickbox | Back strain/Injury
tickbox | Burns
tickbox | Heat exhaustion
section | Initial controls - Mark all that apply.
checkpoint-no-status | Initial controls - Mark all that apply.
note | People controls
tickbox | Safety/Fire watch person
tickbox | Barriers/Flagging
tickbox | Warning signs
note | Equipment controls
tickbox | Master tags and locks
tickbox | Scaffolding for access
tickbox | Radio communication
note | Environmental controls
tickbox | Ventilation
tickbox | Lighting
tickbox | Gas Testing
note | High risk controls
tickbox | WSCS Work permit
tickbox | WSCS Certificates
tickbox | Critical lift/Fall protection plan
tickbox | Specialised PPE
tickbox | Spill kit
tickbox | Fire extinguisher
section | Signatures
checkpoint-no-status | Signatures
signoff | Applicant signature
checklist | JHA - Job Step
section | Task Step - add task step for each individual task
checkpoint-no-status | Task Step - add task step for each individual task
date | Date:
textbox | Task step number (eg. Step 1, Step 2 etc):
textbox | Task details:
textbox | Hazards:
dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
textbox | Potential consequence:
textbox | Controls:
textbox | Recovery steps:
dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
checklist | Toolbox Meeting
section | Toolbox meeting
checkpoint-no-status | Toolbox meeting
date | Date:
textbox | Meeting location:
textbox | Meeting conducted by:
textbox | Meeting attendees:
textbox | Today's work scope/Hazards
textbox | Hazard controls:
signoff | PICWS Signoff
checklist | As-Built Drawings
section | As-Built Drawings - attach scanned documents
checkpoint-no-status | As-Built Drawings - attach scanned documents
textbox | Drawing no.
checklist-flat | Cable Test Record
checkpoint | Upload completed ITR scans
checklist-flat | Certificate of compliance (COC)
checkpoint | Please upload Certificate of Compliance here when complete (COC)
checklist-flat | Record of Inspection (ROI)
checkpoint | Please upload Record of Inspection here when complete (ROI)
checklist | ITR-E-01 General Electrical Equipment
checkpoint | General Electrical Equipment
button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | Installation is clean and tidy | Yes,N/A
button | Mounting arrangement correct | Yes,N/A
button | All internal cabling and wiring correctly installed and labelled. | Yes,N/A
button | External cabling is correctly installed and labelled. | Yes,N/A
button | Check that Equipment is correctly earthed. | Yes,N/A
button | Check gland, plate, frame & door earth continuity | Yes,N/A
button | All spare entries blanked off with correct plugs. | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | Conforms to Specifications and Drawings. | Yes,N/A
button | As-builts complete. | Yes,N/A
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other. |  |  | MegaOhms
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-02A Conduit/Ducting Below Ground
checkpoint | Conduit/Ducting Installation Below Ground
button | Check equipment details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | Check conduit cable enclosure installation is as-per design, layout drawings and specifications. | Yes,N/A
button | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed. | Yes,N/A
button | Confirm that there are no obstructions, and that the installation will be accessible for maintenance. | Yes,N/A
textbox | Record GPS coordinates End 1
textbox | Record GPS coordinates End 2
button | Check all fixings are tight and secure. | Yes,N/A
button | Check bends do not exceed the maximum cable bend radius. | Yes,N/A
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-02B Cable Supports Above Ground
checkpoint | Cable Supports Above Ground
button | Verify cable support has been installed as per relevant drawings, and is correct size and type. | Yes,N/A
button | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection. | Yes,N/A
button | All covers fitted if applicable. | Yes,N/A
button | Check cable support structures are adequately fixed and present no hazard to personnel. | Yes,N/A
button | Welded support brackets have been wire-brushed and painted to completion. | Yes,N/A
button | Splice plates, barriers, earthing system secure. | Yes,N/A
button | Trays / ladders, supports, brackets not interfering with other disciplines. | Yes,N/A
button | Check bends do not exceed the maximum cable bending radius. | Yes,N/A
button | Cables have adequate mechanical protection as and where required. | Yes,N/A
button | Inspect for system rigidity, and check levels to correct plane. | Yes,N/A
button | Earth bonding straps have been fitted to any sections that are split, hinged or flexible. | Yes,N/A
textbox | Record GPS coordinates End 1
textbox | Record GPS coordinates End 2
button | Tray bonded to structure at correct locations. | Yes,N/A
button | Earth bonding continuity tested – record result: | Yes,N/A
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-02C Cable Transits
checkbox | Cable Transits
button | Transit frame installed as per drawings. | Yes,N/A
button | Transit frame identification marked correctly and visible. | Yes,N/A
button | Frame correctly packed with correct sized blocks and infills. | Yes,N/A
button | Correct stay plates fitted (non-ferrous for single core power cables.) | Yes,N/A
button | Rated insulation installed to transit (where required.) | Yes,N/A
button | Cables entering and leaving transits adequately supported and protected. | Yes,N/A
button | Cables pass through frames without strain on blocks. | Yes,N/A
button | All cables identified on both sides of transit and visible. | Yes,N/A
textbox | Record GPS coordinates End 1
textbox | Record GPS coordinates End 2
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-03 Entec - Distribution Board Installation
checkpoint - Mandatory photo | Distribution Board Installation
button | Inspect for mechanical damage from freight and handling | Yes,N/A
button | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct. | Yes,N/A
button | Check type, size and number of breakers is correct as per drawings | Yes,N/A
button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
button | Confirm main isolator operates with associated switches and auxiliaries | Yes,N/A
button | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
button | Check DB, sub circuits, DB Legend and internal cables correctly labelled. As Built drawings complete | Yes,N/A
button | Check sealing of all cable penetration (where applicable). | Yes,N/A
button | Active, Neutral and Earth bar properly identified and labelled | Yes,N/A
button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
checkpoint | Test Results
textbox | Insulation Resistance (Eg. P-P, P-N, P-E, N-E) |  |  | MegaOhms
textbox | Earth Continuity |  |  | Ohms
textbox | Earth Bond |  |  | Ohms
textbox | Fault Loop Impedance, PSSC.
textbox | RCD Test results (1/2x I, 1x I, 5x I)
textbox | Voltage and Phase Rotation
signoff | Installed by:
signoff | Client Representative:
checklist-flat | ITR-E-04 Schedule of Test Results DB
checkpoint | Upload completed ITR scans
signoff | Installed by:
signoff | Client Representative:
checklist-flat | ITR-I-21A - Instrument and COntrol Cables
checkpoint | Instrument and Control Cable
button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
button | Check dressing / cleating, cable undamaged | Yes,N/A
button | Cable mechanically protected | Yes,N/A
button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
button | Screen correctly made off | Yes,N/A
button | Glanding / Locknuts correctly installed. | Yes,N/A
textbox | Gland type - from: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
textbox | Gland type - to: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
textbox | Confirm spare cores and shields are terminated and conform to drawings and client spec.
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
signoff | Installed by:
signoff | Client Representative:
checklist-flat | ITR-E-05 - Low Voltage Cable
checkpoint | Low Voltage Cable
button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
button | Check dressing / cleating, cable undamaged | Yes,N/A
button | Check cable cores correctly identified and labelled. | Yes,N/A
button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
button | Check Armour / Screen correctly made off. | Yes,N/A
button | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Yes,N/A
button | Glanding / Locknuts correctly installed. | Yes,N/A
textbox | Gland type - from: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
textbox | Gland type - to: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-06 Control Panel
checkpoint | Control Panel
button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | Check holding down/mounting arrangement is correct. | Yes,N/A
button | Check for mechanical damage. | Yes,N/A
button | Check tightness of circuit connections. | Yes,N/A
button | All internal cabling and wiring is correctly numbered, colour coded and terminated | Yes,N/A
button | Ammeter scale and current transformer correct. | Yes,N/A
button | Check internals for cleanliness. | Yes,N/A
button | Check manual operation of selector switches, MCB, push buttons, etc. | Yes,N/A
button | Incoming cables correctly glanded, terminated and labelled. Unused entries sealed with correct plug | Yes,N/A
button | Heaters correctly installed. | Yes,N/A
button | Fuse rating correct. | Yes,N/A
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
signoff | Installed by:
signoff | Client Representative:
checklist-flat | ITR-E-07 - Junction Box
checkpoint | Junction Box
button | Check Equipment and Nameplate details are correct in accordance with the data sheet and equipment schedule | Yes,N/A
button | Check mechanical damage | Yes,N/A
textbox | Zone and IP rating
button | Earthing installed correctly and as per drawing | Yes,N/A
button | All internal cabling and wiring correct, (including segregation between ELV and LV, IS and Non IS circuits if applicable) | Yes,N/A
button | Incoming cables glanded correctly, empty holes plugged using correct plug for area classification to maintain IP rating | Yes,N/A
button | Check all Cables & Cores are correctly identified | Yes,N/A
button | Check internals for cleanliness | Yes,N/A
button | Check manual operation of selector switch, MCB, push button, etc | Yes,N/A
button | Check MCB/Fuse ratings (If applicable) | Yes,N/A
textbox | Record earth bar resistance to earth bond
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-08 Heat Tracing Circuit
checkpoint | Heat Tracing Circuit
button | Circuit installed, connected & identified according to design drawings. | Yes,N/A
button | End caps and connection kits correctly installed. | Yes,N/A
button | All junction boxes properly supported, and all cables protected against sharp edges. | Yes,N/A
button | Cable termination and glanding at all junction boxes correct. | Yes,N/A
button | All spare entries blanked off correctly. | Yes,N/A
textbox | IR test: Phase - Earth, Phase - Neutral | Yes,N/A
button | Equipment certification meets the area classification requirements. | Yes,N/A
button | Confirm warning labels are fixed on outside of pipe lagging | Yes,N/A
checkpoint | Electrical tests
textbox | Insulation Resistance: Phase - Earth
textbox | Insulation Resistance: Phase - Neutral
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-09 Electrical Switch Rooms
checkpoint - Mandatory photo | Electrical Switchroom
button | Ensure all equipment is installed in accordance with layout drawings and equipment schedule. | Yes,N/A
button | Ensure all equipment is installed as per manufacturers instructions. | Yes,N/A
button | Ensure there is no visible damage to installed equipment. | Yes,N/A
button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
button | Confirm any slide-in cards / modules are firmly fitted to the equipment panel and properly identified. | Yes,N/A
button | Check equipment panel external earthing connections are securely fitted to and properly terminated on the cabinet protective earth bar. | Yes,N/A
button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
button | Ensure any AC power connection(s) is securely fitted / identified different power sources and potentials and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
button | Check sealing of all cable penetration (where applicable). | Yes,N/A
button | Ensure all signal cables, including any RF coaxial cables, are correctly identified, and securely fitted to the equipment panel. | Yes,N/A
button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
button | Equipment IP, Ex ratings correct. Check tightness for all circuit connections | Yes,N/A
button | All internal cables and wiring is correctly numbered, colour coded and terminated | Yes,N/A
button | Check internals for cleanliness | Yes,N/A
button | Relays Metering and Protection ratings are correct as per design | Yes,N/A
button | As-builts complete | Yes,N/A
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-10 Electrical Equipment Package
checkpoint | Electrical Equipment Package
button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | Check equipment is correctly rated for the area. | Yes,N/A
button | Check if package is complete with all accessories. | Yes,N/A
button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | All transportation supports, stops and fastenings removed. | Yes,N/A
button | Package fixing down bolts/shims/washers installed and tensioned. | Yes,N/A
button | Check package is installed on a level plane. | Yes,N/A
button | External cabling (if required) correctly installed. | Yes,N/A
button | Internal equipment installed and all tests complete and accepted. | Yes,N/A
button | Verify package using vendor and/or project P&IDs. | Yes,N/A
button | Check that equipment is correctly earthed. | Yes,N/A
textbox | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm |  |  | Ohm
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-11 Generator Package (LV)
checkpoint | Generator Package (LV)
button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | Check terminal boxes and glanding correct. | Yes,N/A
button | Instruments correctly installed. | Yes,N/A
button | Heaters correctly installed. | Yes,N/A
button | Check unit for cleanliness. | Yes,N/A
button | Check manual operation of selector switches, MCB, push buttons etc. | Yes,N/A
button | External cabling correctly installed. | Yes,N/A
button | Protection of live parts adequate. | Yes,N/A
button | Main terminal box complete and terminations correct torque. | Yes,N/A
button | Ensure direction of rotation is clearly marked. | Yes,N/A
button | Check gasket and seals are not damaged. | Yes,N/A
button | Unused cable entries are correctly sealed. | Yes,N/A
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
textbox | Heater circuit insulation resistance:
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-12 Electrical earthing
Checkpoint | Electrical earthing system installation
button | Confirm earth grid layout, earth conductors/connections and number of earth electrodes is in accordance with drawings, drawings as-built | Yes,N/A
button | Ensure that all metal work is earthed as required. | Yes,N/A
button | Check welding of earth bosses and associated surface finish. | Yes,N/A
button | Ensure that earth cables/conductors/electrodes have adequate mechanical protection i.e. conduits, tobys, kick-plates etc at points of high exposure. | Yes,N/A
button | Ensure that brazing or welding of all joints has been completed correctly. | Yes,N/A
button | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, cad (thermal) welds and earth bosses | Yes,N/A
button | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating. | Yes,N/A
button | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly. | Yes,N/A
button | Check that all bi-metal connections have been performed correctly to manufacturer’s requirements. | Yes,N/A
button | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar. | Yes,N/A
button | Ensure that earth cable identification markings are in place. | Yes,N/A
button | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible. | Yes,N/A
button | Check earth bar fixings, mounting points and terminations are tight and secure and conform to project specification (if applicable) | Yes,N/A
checkpoint | Test Results
textbox | Earth continuity test results (Earth bar to Electrode, Grid, etc - please specify)
textbox | 3-Wire earth test results (If applicable).
textbox | Earth grid test results (if applicable). (HV earth grid, LV earth grid, combined earth grids)
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-13 Motors
checkpoint | Motors installation
tickbox | Tag number, area classification, IP rating correct as per drawings and equipment schedule
button | Space heater | Yes,N/A
textbox | Space heater specification (Power (Watts) and Voltage:)
checkpoint - Mandatory photo | Nameplate details correct and in accordance with the data sheet
note | Upload clear photo of nameplate
checkpoint | Checklist items
button | Equipment has been received in good condition and is the correct type as per the site drawings, specifications & data sheets | Yes,N/A
button | Identification Tag and Rotation Plate correctly fitted | Yes,N/A
button | Motor electrical coupling (Delta/Star) is correct. | Yes,N/A
button | Check for mechanical condition, air ducts and fan free of debris | Yes,N/A
button | Correct glanding for area classification. | Yes,N/A
button | Holding down bolts fitted correctly. | Yes,N/A
button | Check bearing lubrication, free rotation with shaft uncoupled | Yes,N/A
button | Cable(s) correctly terminated, labelled and colour identification | Yes,N/A
button | Terminations/connections torqued correctly to data sheets. | Yes,N/A
checkpoint | Motor Installation Testing
textbox | LV Motor winding insulation resistance with supply cables disconnected; 1 minute test
note | Insulation resistance U, V, W
textbox | LV Motor winding insulation resistance with supply cables disconnected; 10 minute test
note | Insulation resistance U, V, W
textbox | Motor continuity between windings
note | Continuity U1-U2, V1-V2, W1-W2.
textbox | Space heater continuity & resistance check
note | Continuity & Insulation resistance results:
textbox | Thermostat or RTD wiring resistance check
note | Resistance:
textbox | Check motor is earthed correctly and record motor earth bond:
checkpoint | Additional checks
tickbox | Winding temperature detector
tickbox | Air temp detectors
tickbox | Bearing temp indicators
tickbox | Vibration Monitors
tickbox | Condensation detector
button | All spare entries in terminal boxes have been blanked off correctly (with certified plugs if applicable) | Yes,N/A
button | Inspect all Ex "d" terminal box flange surfaces and apply approved grease (if applicable) | Yes,N/A
button | Installation conforms to specification and drawings | Yes,N/A
button | As-Builts complete | Yes,N/A
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-14 Motor Control
checkpoint | General Motor Control
button | Check all labelling and warning signs are correctly installed and visible | Yes,N/A
button | Check control equipment is clean and free from dust, debris and tools, no mechanical damage | Yes,N/A
button | Check preservation and transit items are removed | Yes,N/A
button | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor | Yes,N/A
button | Check all cabling to control gear and motor is undamaged, supported and tidy | Yes,N/A
button | Check earthing bar and connections are correct and tight | Yes,N/A
button | Check incoming and outgoing power cables are terminated and glanded correctly | Yes,N/A
button | Check phase identification on power cables is correct and visible | Yes,N/A
button | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque | Yes,N/A
button | Check all other nuts and bolts are tight | Yes,N/A
button | Check spare gland entries are plugged with correct rated plugs | Yes,N/A
button | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected | Yes,N/A
checkpoint | Variable Speed Drives (VSD)
note | Record VSD Details
textbox | Volts (Input) |  |  | V
textbox | Amps (Input) |  |  | A
textbox | Amps (Output) |  |  | A
button | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input) | Yes,N/A
button | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used. | Yes,N/A
button | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged | Yes,N/A
button | Check control signal cables use twisted pairs | Yes,N/A
button | Check control signal and profibus cables shield is earthed at one end | Yes,N/A
button | Check analogue and digital signals are run in separate cables | Yes,N/A
checkpoint | Voltage segregation
button | Distance between input power and motor cable >300mm | Yes,N/A
button | Distance between input power and control signal cable >200mm | Yes,N/A
button | Distance between motor cable and control signal cable >500mm | Yes,N/A
button | Check there are no power factor compensation capacitors installed on the outgoing power cables | Yes,N/A
button | Check gland plates with single core power cables are non-magnetic at VSD and LIS | Yes,N/A
button | Check mains voltage cannot be applied to the VSD output by means of a bypass connection | Yes,N/A
button | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC | Yes,N/A
button | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position) | Yes,N/A
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-15 UPS Installation
checklist | ITR-E-15 - UPS Installation
checkpoint -MANDATORY PHOTO | UPS Installation
button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
button | Check for mechanical damage. | Yes,N/A
button | Panel IP rating is correct. | Yes,N/A
button | Holding down arrangement and seat alignment correct. | Yes,N/A
button | Panels aligned correctly. | Yes,N/A
button | External bonding correct | Yes,N/A
button | Phase identification correct. | Yes,N/A
button | Instrument, indication lamps & interlocks correct. | Yes,N/A
button | Main switches, contactors, fuses etc. sized & identified correctly as per Single Line Drawings. | Yes,N/A
button | Check Main Isolator and Bypass switch operation | Yes,N/A
button | COM Interface & Mod Link. | Yes,N/A
button | Padlocking facilities correct. | Yes,N/A
button | Check internals for cleanliness. | Yes,N/A
button | Check manual operation of selector switch, MCB, push button, etc. | Yes,N/A
button | Incoming cable correctly installed, terminated & supported. | Yes,N/A
button | All internal cabling & wiring neat, correct & tight. Unused cable entries sealed. | Yes,N/A
button | Drawings marked up with relevant changes and As-builts complete. | Yes,N/A
checkpoint | Test results
textbox | Earth Continuity, Insulation Resistance, Temperature, Phase Rotation, Polarity.
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-E-16 Lightning Protection
checkpoint - Mandatory photo | Lightning Protection Earthing system
button | All checks done in accordance with Client specification, drawings and AS/NZS 1768:2007 | Yes,N/A
button | Lightning conductor is 2 metres or more above the entire protected area | Yes,N/A
button | Check the materials and equipment used for the down conductors are suitable | Yes,N/A
button | Check the down conductors are routed, located and electrically bonded as required | Yes,N/A
button | Check all installed components are firmly secured | Yes,N/A
button | Check the method of protection against electric shock, including the measurement of distances | Yes,N/A
button | Check earth termination systems are interconnected | Yes,N/A
button | Check isolating and switching devices correctly located | Yes,N/A
button | Check warning signs and diagrams are installed | Yes,N/A
button | Check accessibility for operation and maintenance | Yes,N/A
checkpoint | Test Results
textbox | Resistance of all connections at the location of the connection. (The resistance of each connection shall not exceed 0.05 Ohm) |  |  | Ohm
textbox | Earth termination system resistance is correct and record value |  |  | Ohm
textbox | Record the insulation resistance of the electrical installation |  |  | MegaOhm
textbox | Continuity of the main and supplementary equipotential bonding: |  |  | Ohm
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-I-01 Fire and Gas Detection Alarms
checkpoint | Fire and Gas detection alarms
textbox | Make and Model
textbox | Type
button | Location correct as per drawings | Yes,N/A
button | Component & Type / Model correct per equipment schedule | Yes,N/A
button | Cable connection & termination correct | Yes,N/A
button | Installation free of mechanical damage and clean | Yes,N/A
button | Glanding correct and spare entries plugged with correctly rated plug | Yes,N/A
button | E.O.L Installation | Yes,N/A
button | Test tubing installation | Yes,N/A
button | Detection Path Clear | Yes,N/A
checkpoint | Inspection
textbox | Tag No.
textbox | RX Tag No:
button | Area Classification correct | Yes,N/A
textbox | Hazardous Area Certificate:
textbox | Detector Type:
textbox | Gas Type:
textbox | Supply Voltage:
textbox | Output Signal:
checkpoint | Functional Check
button | Self Test | Yes,N/A
button | Alarm Operation | Yes,N/A
button | Fault Relay Operation | Yes,N/A
textbox | Measured output (clear path)
textbox | Measured output (blocked path)
textbox | Measured output (filter in place)
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-02 Instrument Tubing Installation
checkpoint | Checks Pre-Installation
button | Tubing connection to and from equipment as per drawings. | Yes,N/A
button | Tube material type, size, gauge and standard confirmed and available | Yes,N/A
button | Tube fitting size and type confirmed and available | Yes,N/A
section | Checks During and Post-Installation
button | Correct thread compatibility and engagement | Yes,N/A
button | Correct thread tape and sealant used on fittings | Yes,N/A
button | Check fitting ferrule orientation and confirm prior to connection | Yes,N/A
button | Tube installation is in compliance with the client specification. (Supports, bracketry, slope, expansion, vibration, access, cables) | Yes,N/A
button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
button | Depth insertion tool used; witness mark visible at all stages of process | Yes,N/A
button | Tube fitting hexes marked to ensure correct swage tightness | Yes,N/A
button | Random check with No-Go gap gauge | Yes,N/A
button | In service leak test performed and passed (ITR-CL-1-118) | Yes,N/A
button | Fitting completion tag completed and applied to each fitting | Yes,N/A
note | Refer to Swagelok book for tube/thread size pressure ratings
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-03 Instrument Pressure/Leak Test
checkpoint | Checklist items
button | Tube identification correct | Yes,N/A
button | Mechanical damage visual check | Yes,N/A
button | Flow direction and instrument orientation correct | Yes,N/A
button | Tubing size and installation correct | Yes,N/A
checkpoint | Testing
note | Verify test pressure and medium is correct per project and manufacture specification prior to test
textbox | Test fluid:
textbox | Test pressure:
textbox | Max design pressure:
dropdown | Test pressure unit: | kgf/cm2, PSI, kPa, bar, Other
textbox | Duration: |  |  | Minutes
button | Confirm all impulse lines have been drained and cleaned | Yes,N/A
button | Confirm any temporary test connections, valve etc. are rated for the intended test. | Yes,N/A
button | Confirm pneumatic, test gas and aspirator lines have been blown clear. | Yes,N/A
button | Check hydraulic lines flushed to project specification. | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-04 Valve & Ancillaries (Pre-Installation)
checkpoint | Equipment
button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
button | Equipment checked for additional items as applicable | Yes,N/A
checkpoint | Valve
textbox | Valve Size:
textbox | Flange type:
button | Material certification correct | Yes,N/A
button | Trim material correct | Yes,N/A
textbox | Rating:
textbox | Service:
button | Body material correct | Yes,N/A
textbox | Leakage class:
checkpoint | Actuator
textbox | Input range: |  |  | kPa
button | Failure action | Yes,N/A
button | Hand wheel operation correct | Yes,N/A
checkpoint | Positioner
textbox | Signal range
textbox | Output range
checkpoint | I/P Converter
textbox | Signal range
textbox | Output range
checkpoint | Filter/Regulator/On-Off Valve
textbox | Range |  |  | kPa
textbox | Pressure setting |  |  | kPa
button | Stroke Time correct | Yes,N/A
textbox | Open |  |  | sec
textbox | Close |  |  | sec
button | Open/Close times conform to commissioning specifications | Yes,N/A
checkpoint | Fail Action
dropdown | Electrical Fail Action | FO, FC, FL
dropdown | Motive Force | FO, FC, FL
checkpoint | Valve Field Calibration and Hysteresis Check
tickbox | Confirm test equipment is within calibration period prior to testing
note | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
button | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100% | Yes,N/A
checkpoint | Proximity Detectors
button | Open switch set, correct mode setting | Yes,N/A
button | Closed switch set, correct mode setting | Yes,N/A
button | Electrical connections and certification correct | Yes,N/A
checkpoint | Solenoid Valve
button | Operation correct | Yes,N/A
button | Electrical connections correct | Yes,N/A
button | Electrical certification correct | Yes,N/A
textbox | Voltage: |  |  | V
button | Pneumatic connections correct | Yes,N/A
textbox | Pneumatic pressure |  |  | kPa
checkpoint | Pilot Valve
button | Pneumatic connections correct | Yes,N/A
button | Operation correct | Yes,N/A
button | Action/Lockup | Yes,N/A
checkpoint | Hydraulic Actuator
textbox | Working pressure
textbox | Manifold pressure
textbox | Fluid type
button | Hydraulic connections correct | Yes,N/A
textbox | Regulator pressure setting
button | Pilot operation correct | Yes,N/A
checkpoint | Accumulator
button | N2 Charge required | Yes,N/A
textbox | N2 Pre-charge pressure
textbox | Pressure switch setting
textbox | Working pressure
textbox | Output range
button | Volume tank & check valve installed correctly | Yes,N/A
checkpoint | Electric Actuator
textbox | Voltage:
button | Electrical certification correct | Yes,N/A
button | Electrical connections correct | Yes,N/A
button | Remote operation correct | Yes,N/A
button | Local hand operation correct | Yes,N/A
button | Torque switches and travel stops set | Yes,N/A
checkpoint | Miscellaneous Equipment
textbox | Description
textbox | Manufacturer
textbox | Model No:
textbox | Serial No:
textbox | Range:
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-05 Analogue Valve & Ancillaries (Pre-Installation)
checkpoint | Equipment
button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
button | Equipment checked for additional items as applicable | Yes,N/A
checkpoint | Valve
textbox | Valve Size:
textbox | Flange type:
button | Material certification correct | Yes,N/A
button | Trim material correct | Yes,N/A
textbox | Rating:
textbox | Service:
button | Body material correct | Yes,N/A
textbox | Leakage class:
checkpoint | Actuator
textbox | Input range: |  |  | kPa
button | Failure action | Yes,N/A
button | Hand wheel operation correct | Yes,N/A
checkpoint | Positioner
textbox | Signal range
textbox | Output range
checkpoint | I/P Converter
textbox | Signal range
textbox | Output range
checkpoint | Filter/Regulator
textbox | Range |  |  | kPa
textbox | Pressure setting |  |  | kPa
section | Fail Action
dropdown | Electrical Fail Action | FO, FC, FL
dropdown | Motive Force | FO, FC, FL
checkpoint | Proximity Detectors
button | Open switch set, correct mode setting | Yes,N/A
button | Closed switch set, correct mode setting | Yes,N/A
button | Electrical connections and certification correct | Yes,N/A
checkpoint | Solenoid Valve
button | Operation correct | Yes,N/A
button | Electrical connections correct | Yes,N/A
button | Electrical certification correct | Yes,N/A
textbox | Voltage: |  |  | V
button | Pneumatic connections correct | Yes,N/A
textbox | Pneumatic pressure |  |  | kPa
checkpoint | Pilot Valve
button | Pneumatic connections correct | Yes,N/A
button | Operation correct | Yes,N/A
button | Action/Lockup | Yes,N/A
checkpoint | Hydraulic Actuator
textbox | Working pressure
textbox | Manifold pressure
textbox | Fluid type
button | Hydraulic connections correct | Yes,N/A
textbox | Regulator pressure setting
button | Pilot operation correct | Yes,N/A
checkpoint | Accumulator
button | N2 Charge required | Yes,N/A
textbox | N2 Pre-charge pressure
textbox | Pressure switch setting
textbox | Working pressure
textbox | Output range
button | Volume tank & check valve installed correctly | Yes,N/A
checkpoint | Electric Actuator
textbox | Voltage:
button | Electrical certification correct | Yes,N/A
button | Electrical connections correct | Yes,N/A
button | Remote operation correct | Yes,N/A
button | Local hand operation correct | Yes,N/A
button | Torque switches and travel stops set | Yes,N/A
checkpoint | Miscellaneous Equipment
textbox | Description
textbox | Manufacturer
textbox | Model No:
textbox | Serial No:
textbox | Range:
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-06 Instrument Installation
checkpoint - Mandatory photo | Instrument Installation
button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
button | Vent lines are directed into a safe area. | Yes,N/A
button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
button | Spare entries plugged correctly, using certified plug. | Yes,N/A
button | Instrument earthed in accordance with project specification. | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-07 Instrument Calibration
checkpoint-no-status | Required Data
textbox | Type and Size:
textbox | Make and Model:
textbox | Serial No:
textbox | Instrument Type:
textbox | Instrument designation/equipment no
textbox | Calibration interval
textbox | Calibration method
textbox | Calibrated at
checkpoint | Instrument Power Supply
dropdown | Supply type | VAC, 2 Wire DC, Other, None
textbox | Supply value:
button | Calibration sheet completed and attached below | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-08 Instrument Pre-Commissioning
checkpoint | Checklist items
button | Verify transmitter loop connection - Remove wre on transmitter and confirm at Control System interface | Yes,N/A
button | Relevant individual control system/ESD loops have been checked and test sheets completed | Yes,N/A
checkpoint | Analogue Input:
checkpoint-no-status | Analogue Input:
textbox | Input range & units:
textbox | Indication range & units:
checkpoint-no-status | 0% Rising
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 25% Rising
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 50% Rising
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 75% Rising
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 100% Peak
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 75% Falling
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 50% Falling
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 25% Falling
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 0% Falling
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint | Digital Input/Analogue Alarm Trip Points
checkpoint-no-status | Alarm Lo:
textbox | Alarm setting
textbox | Measured Alarm Point
textbox | Filter/Time Delay
textbox | Result
checkpoint-no-status | Alarm Lo-Lo:
textbox | Alarm setting
textbox | Measured Alarm Point
textbox | Filter/Time Delay
textbox | Result
checkpoint-no-status | Alarm Hi:
textbox | Alarm setting
textbox | Measured Alarm Point
textbox | Filter/Time Delay
textbox | Result
checkpoint-no-status | Alarm Hi-Hi:
textbox | Alarm setting
textbox | Measured Alarm Point
textbox | Filter/Time Delay
textbox | Result
checkpoint-no-status | Control loop set points correct:
textbox | Set Point 1:
textbox | Set Point 2:
textbox | Set Point 3:
textbox | Set Point 4:
checkpoint | Startup, Shutdown and Override functions
button | Control system graphic display | Yes,N/A
button | Control system point display | Yes,N/A
button | ESD graphic display | Yes,N/A
button | Alarm Recording and Text | Yes,N/A
checkpoint | Additional checks
button | Control system display and alarms are correct as per control functions | Yes,N/A
button | Transmitter fail direction and burnout are to spec (Upscale/Downscale) | Yes,N/A
button | Switch action verified, including power loss | Yes,N/A
button | Drawings, documents and As-Builts scanned and attached | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-09 Commissioning Instruments
checkpoint | Required Data
textbox | Instrument range:
button | Installation complete | Yes,N/A
button | Point-to-point | Yes,N/A
button | Haz. Inspected | Yes,N/A
button | Tag correct | Yes,N/A
button | Hook-up correct | Yes,N/A
checkpoint | Alarms & Set points
checkpoint-no-status | Alarm Lo
textbox | Activated:
checkpoint-no-status | Alarm Lo-Lo
textbox | Activated:
checkpoint-no-status | Alarm Hi
textbox | Activated:
checkpoint-no-status | Alarm Hi-Hi
textbox | Activated:
checkpoint-no-status | Set Point 1
textbox | Activated:
checkpoint-no-status | Set Point 2
textbox | Activated:
checkpoint-no-status | Set Point 3
textbox | Activated:
checkpoint-no-status | Set Point 4
textbox | Activated:
checkpoint | Calibration settings
textbox | Zero
textbox | Range
textbox | Other (Specify)
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-10 Cone and Thread Tubing Installation
checkpoint-no-status | General Data
textbox | Location:
textbox | Duty:
textbox | Reference Drawings/Hook-up drawing:
textbox | Related instrument tag no:
textbox | Tube diameter and wall thickness:
checkpoint | Cone and Thread installation - Stainless fittings
button | Correct thread compatibility and engagement | Yes,N/A
button | Check fitting collar prior to connection - 1 to 2 threads visible at cone | Yes,N/A
button | Tube installation follows the client specification. (Supports, Bracketry, Slope, Expansion, Vibration, Access, Cables) | Yes,N/A
button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
checkpoint-MANDATORY PHOTO | Cone machined face. No defects, lines, bumps etc.
label | Attach photo of cone and thread.
checkpoint-MANDATORY PHOTO | Thread cleanly cut, de-burred and cleaned.
label | Attach photo of collar.
button | Lubricate collar, cone and gland thread at assembly to prevent galling as required | Yes,N/A
button | Correct Tube nut used for the right sized tube | Yes,N/A
label | Ensure No thread tape or sealant are used on tube nuts | Yes,N/A
button | Tube fitting hex torqued to ensure correct tightness, marked with pen | Yes,N/A
button | Ensure Weep hole is unobstructed and clean | Yes,N/A
button | In service leak test performed and passed | Yes,N/A
button | Fitting completion tag completed and applied to each fitting | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-1-11 Cone and Thread Pressure Testing
checkpoint-no-status | General Data
textbox | Location:
textbox | Duty:
textbox | Reference Drawings:
textbox | Hook-up drawing:
textbox | Related instrument tag no:
textbox | Tube diameter and wall thickness:
checkpoint | Checklist items
button | Tubing orientation as per hook up drawing. | Yes,N/A
button | Checked with a Torque Wrench and marked and tagged | Yes,N/A
button | Ensure Area is barricaded off to restrict unauthorized entry to personnel | Yes,N/A
button | Tube as per specification and hook up drawings. | Yes,N/A
textbox | Max design pressure:
textbox | Test medium used:
textbox | Record Testing pressure:
textbox | Test pressure duration: |  |  | Minutes
textbox | Test leak rate: |  |  | Litres/minute
button | Chart recorder used and attached (where applicable). | Yes,N/A
button | Confirm all Tubing lines have been pigged / cleaned. | Yes,N/A
button | Check all plugs are replaced (if removed), vents are closed, and isolation valves are in correct positions. | Yes,N/A
button | Ensure equipment is left clean and in a safe state for handover to operations to the standard of ITP-I-08 Cone and Thread cleaning procedure | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-12 Telecommunications Equipment Panel
checkpoint | Telecommunications Equipment Panel
button | Ensure equipment panel is securely mounted within the Telecommunications Cabinet in the correct location as shown on general layout drawings: | Yes,N/A
button | Check tag number is in accordance with Telecommunications Equipment List. | Yes,N/A
button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
button | Confirm any slide-in cards are firmly fitted to the equipment panel and properly identified. | Yes,N/A
button | Check panel air vents are clean and free of dust and dirt. | Yes,N/A
button | Check equipment panel external earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
button | Ensure any AC power connection(s) is securely fitted and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
button | Check sealing of all cable penetration (where applicable). | Yes,N/A
button | Ensure all signal cables, including any RF co-axial cables, are correctly identified and securely fitted to the equipment panel. | Yes,N/A
button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
checklist | ITR-I-13 Temperature Instrument Installation
checkpoint | Temperature Instrument Installation
button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
button | Temperature instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
dropdown | Type of thermowell installed | Flanged, Welded, Screwed, Other
button | Thermowell details including flange size are correct in accordance with the specifications | Yes,N/A
button | Internal depth of thermowell checked and recorded | Yes,N/A
textbox | Depth:
button | Bar material and tag number stamped on thermowell flange/exposed surface | Yes,N/A
button | Thermowell CE marked | YES,NO
button | EOL resistor fitted and correctly rated where applicable | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-14 Flow Meter Installation
checkpoint | Flow Meter Installation
button | Check instrument nameplate details are correct in accordance with the instrument index | Yes,N/A
button | Flow meter calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
button | Ensure location and tapping point is verified as per P&ID & location drawings | Yes,N/A
button | Ensure direction of flow is correct with respect to flow meter | Yes,N/A
button | Check mechanical clearance is adequate for installation of flow meter | Yes,N/A
button | Verify type and size of gasket is correct between process line and measuring unit flange | Yes,N/A
button | Ensure correct nut and bolt grade and material for connecting unit to process line | Yes,N/A
button | Verify display/cover is oriented for ease of use for operators and access for technicians | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-15 Pressure Instrument Installation
checkpoint | Pressure Instrument Installation
button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
button | Pressure Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
button | Instrument mounted as per hook-up drawings | Yes,N/A
button | Air line/Impulse line are correct material to site specifications | Yes,N/A
button | Air line/Impulse line are routed tidily and as per hook-up drawings | Yes,N/A
button | Correct bolt size and material/grade used | Yes,N/A
button | Local indicator is mounted and easy to read, easy access for technicians | Yes,N/A
button | Instrument and tubing are adequately supported as per drawings | Yes,N/A
button | Isolation valve installed | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-16 Level Instrument Installation
checkpoint | Level Instrument Installation
button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
button | Level Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
button | Level instrument mounting equipment is adequately sturdy and correct materials used | Yes,N/A
button | Bolts and studs are to site specification | Yes,N/A
button | Ensure location and tapping point is verified per relevant drawings | Yes,N/A
button | Ensure gasket and studs are used as per specifications | Yes,N/A
button | Verify contact type sensor probes are installed without any resistance | Yes,N/A
button | Verify antenna/source are installed correctly | Yes,N/A
button | Ensure display is easily readable by operations and access is easy for technicians | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat | Test Equipment Details:
checkpoint-no-status | Details
textbox | Make
textbox | Model
textbox | Serial No
textbox | Calibration Expiry Date
checklist-flat | Earth Bonding
checkpoint | Continuity test from Point A to Point B
textbox | Results: |  |  | Pass if <0.5Ω
textbox | Size of bond cable
note | Upload photo of bond connection
checklist | ITR-E-40A Bus Bar |  | ITR-E-40A Bus Bar
checkpoint | Bus Bar
button | Check entire Bus Bar and confirm there is no damage | Yes,N/A
textbox | Verify zone bus-bar is rated for
note | Please attatch photo of Bus Bar
button | Bus Bar alignment is correct | Yes,N/A
button | Confirm all jointing bolts are present and have been torque tested in accordance with the manufacturer and design requirements. Acceptable Bus Bar Torque Settings: Bolt: M6 M8 M10 M12 M16 Torque: 10Nm 20Nm 30Nm 40Nm 60Nm | Yes,N/A
button | Confirm all transit packing and preservation materials have been removed. | Yes,N/A
button | Confirm Bus Bar clearances conform to manufactures and design requirements. | Yes,N/A
button | Confirm all Bus Bars are secure within the supports. | Yes,N/A
textbox | Record the total number of bus bar joints.
signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist-flat | Electrical Safety Ceritificate (ESC)
checkpoint | Please upload Electrical Safety Certificate here when complete (ESC)
checklist | Sign Off
Signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist | ITR-E-64 General Lighting |  | ITR-E-64 General Lighting
Checkpoint | General Lighting
button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | Operation of emergency lighting fixtures checked | Yes,N/A
button | Mounting arrangement and degree unit is installed is correct | Yes,N/A
button | External cabling is correctly installed and labelled. | Yes,N/A
button | Battery run-down test per manufacturers specification | Yes,N/A
button | Power / load balance on distribution board checked | Yes,N/A
button | Operation of remote lighting control checked | Yes,N/A
button | All spare entries blanked off with correct plugs. | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | Conforms to Specifications and Drawings. | Yes,N/A
button | Insulation resistance of final sub-circuits checked | Yes,N/A
button | Operation of photo-electric cell control checked | Yes,N/A
button | Lighting pole is adequately earthed | Yes,N/A
button | Circuit ID fitted to all light switches | Yes,N/A
button | All fittings correctly labelled | Yes,N/A
button | All switching tested and confirmed as correct (two way, intermediate, on/off/auto etc | Yes,N/A
button | As-Built drawings completed | Yes,N/A
checkpoint | Lux Levels
button | Lux levels meet minimum client specifications. (Closed door and measure lux level at darkest point of personnel accessible area) | Yes,N/A
textbox | Lux Results:
signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist-flat | ITR-E-29 Cat 6 Communication Cable
checkpoint | Common to all circuits
button | check cable for damage | Yes, N/A
button | Check cable is correctly identified and labelled | Yes, N/A
button | Check glanding/locknuts correctly installed | Yes, N/A
button | Confirm cable routing and segregation is correct | Yes, N/A
button | Confirm to and from destination as per design. | Yes, N/A
checkpoint | Data Circuits
button | Check cable terminated with correct crimps | Yes, N/A
button | Check sheild/screen correctly made off | Yes, N/A
button | Check Cat6 end-to-end certification (outlet and cable) | Yes, N/A
signoff | Installed by: | Yes, N/A
signoff | Client Representative: | Yes, N/A
checklist-flat | FAT Testing
checkpoint | Upload completed test sheet scans
checklist | ITR-E-34A Low Voltage Switch Board |  | ITR-E-34A Low Voltage Switch Board
Checkpoint | Low Voltage Switch Board
button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | Check holding down/mounting arrangement is correct. | Yes,N/A
button | Check for mechanical damage. | Yes,N/A
button | Confirm that all temporary supports, jumpers and ties have been removed. | Yes,N/A
button | Incoming cables correctly installed, terminated and supported. | Yes,N/A
button | Phase identification correct. | Yes,N/A
button | Confirm that padlocking facilities are provided and operate correctly allowing all circuit breakers to be locked in the open position and safety shutters locked in the closed position. | Yes,N/A
button | Confirm all cubicle doors can be opened without obstruction and minimum required clearances are retained | Yes,N/A
button | Bus bar terminations tightened to specified torque | Yes,N/A
button | Confirm components, fuses etc. correctly sized and identified as per design drawings and Single Line Diagrams. | Yes,N/A
button | Instruments, indication lamps and interlocks correct. | Yes,N/A
button | Ammeter and current transformer correctly installed. | Yes,N/A
button | Check internals for cleanliness. | Yes,N/A
button | Check that Switchboard is correctly earthed. Check door, escutcheon, gland plate, gland and frame. | Yes,N/A
textbox | Test and confirm the earth resistance between switchboard and local earth system is less than 0.5ohms
button | All internal cabling and wiring neat, correct, and undamaged. | Yes,N/A
button | Unused cable entry sealed. | Yes,N/A
button | Heaters correctly installed. | Yes,N/A
button | Confirm that all insulating bushings and barriers are satisfactory. | Yes,N/A
Checkpoint | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages. System KV Test V (dc) Min IR Reading <1.0 500 10 MΩ <2.5 1000 50 MΩ < 4.6 2500 100 MΩ >4.6 5000 250 MΩ
textbox | L1 - Earth |  |  | mega ohms
textbox | L2 - Earth |  |  | mega ohms
textbox | L3 - Earth |  |  | mega ohms
textbox | L1 - L2 |  |  | mega ohms
textbox | L1 - L3 |  |  | mega ohms
textbox | L2 - L3 |  |  | mega ohms
textbox | N - Earth |  |  | mega ohms
signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist | ITR-I-07A Transmitters/Gauges/Hand Valves
textbox | Tag No.
button | Indicator Range Correct | Yes,N/A
textbox | Hazardous Area Certificate
button | Shipping stops removed | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | Body material is correct | Yes,N/A
button | Unit condition is acceptable | Yes,N/A
button | Process connections correct | Yes,N/A
button | Pneumatic/Elec. Connections correct | Yes,N/A
button | Supply settings correct | Yes,N/A
textbox | Operating Range:
textbox | Output Signal:
textbox | Calibrated Range:
Textbox | Insert any relevant test results:
signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist | ITR-E-30 Earthing Electrodes
textbox | Location of electrodes:
textbox | Electrode length/size:
textbox | Electrode type:
textbox | Method of installing electrode:
textbox | Method of attatching to electrode (E.g. Clamp, cadweld, lug/bolt):
textbox | No. of electrodes:
button | Earth pits correct as per specifications, covers, no damage | Yes,N/A
button | Connections to electrodes are secure | Yes,N/A
button | Structural and equipment earth connections secure | Yes,N/A
button | Earth cable lugs secure, cable passes through concrete in PVC. | Yes,N/A
button | Equipment bonding, connection to main earth bar secure | Yes,N/A
button | Earth electrode identified, MEN linked, installed and labeled | Yes,N/A
Textbox | Insert any relevant test results:
signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist | ITR-I-34A Instrument Installation PRV/PSV
textbox | Make and Model:
textbox | Manufacturer:
textbox | Type:
textbox | Check equipment and nameplate details are correct in accordance with the instrument index
button | Valve is installed correctly | Yes,N/A
button | Valve is installed level and per P&ID | Yes,N/A
button | All gaskets are correct specification and fitted | Yes,N/A
button | All bolting is tight and to specification | Yes,N/A
textbox | Tagged by SGS/IVE, upload certification | Yes,N/A
button | Correctly labelled as per drawings | Yes,N/A

## Examples
Command | Description
checklist | complex checklist with progress bar
checklist-flat | simple checklist
section | breaks checklist into sections
checkpoint | Pass/Fail/NA checkpoint
checkpoint-no-status
textbox | Textbox for inputting data for above checkpoint/section
dropdown | Select from a dropdown range of options. Enter options in "Values" tab separated by commas eg. Item 1, Item 2, Item 3
date | users can select date from a calendar
label | Creates a label for relevant checkpoint/section, good for additional notes or instruction e.g "Test 230v circuits at 500VDC for IR test"
button | Buttons with defined labels, enter options in "Values" tab separated by commas eg. Yes, No or option A, option B, option C, etc
signoff | creates touchscreen signature input section, for signing off documents
tickbox | simple tickbox, in final export it appears as "Yes" when ticked and "No" when unticked.