## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITR-E-64 General Lighting
section | Details
checkpoint | General Lighting
button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | Operation of emergency lighting fixtures checked | Yes,N/A
button | Mounting arrangement and degree unit is installed is correct | Yes,N/A
button | External cabling is correctly installed and labelled. | Yes,N/A
button | Battery run-down test per manufacturers specification | Yes,N/A
button | Power / load balance on distribution board checked | Yes,N/A
button | Operation of remote lighting control checked | Yes,N/A
button | All spare entries blanked off with correct plugs. | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | Conforms to Specifications and Drawings. | Yes,N/A
button | Insulation resistance of final sub-circuits checked | Yes,N/A
button | Operation of photo-electric cell control checked | Yes,N/A
button | Lighting pole is adequately earthed | Yes,N/A
button | Circuit ID fitted to all light switches | Yes,N/A
button | All fittings correctly labelled | Yes,N/A
button | All switching tested and confirmed as correct (two way, intermediate, on/off/auto etc | Yes,N/A
button | As-Built drawings completed | Yes,N/A
checkpoint | Lux Levels
button | Lux levels meet minimum client specifications (Closed door and measure lux level at darkest point of personnel accessible area) | Yes,N/A
textbox | Lux Results:
signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist | ITR-E-34A Low Voltage Switch Board
section | Details
checkpoint | Low Voltage Switch Board
button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | Check holding down/mounting arrangement is correct. | Yes,N/A
button | Check for mechanical damage. | Yes,N/A
button | Confirm that all temporary supports, jumpers and ties have been removed. | Yes,N/A
button | Incoming cables correctly installed, terminated and supported. | Yes,N/A
button | Phase identification correct. | Yes,N/A
button | Confirm that padlocking facilities are provided and operate correctly allowing all circuit breakers to be locked in the open position and safety shutters locked in the closed position. | Yes,N/A
button | Confirm all cubicle doors can be opened without obstruction and minimum required clearances are retained | Yes,N/A
button | Bus bar terminations tightened to specified torque | Yes,N/A
button | Confirm components, fuses etc. correctly sized and identified as per design drawings and Single Line Diagrams. | Yes,N/A
button | Instruments, indication lamps and interlocks correct. | Yes,N/A
button | Ammeter and current transformer correctly installed. | Yes,N/A
button | Check internals for cleanliness. | Yes,N/A
button | Check that Switchboard is correctly earthed. Check door, escutcheon, gland plate, gland and frame. | Yes,N/A
textbox | Test and confirm the earth resistance between switchboard and local earth system is less than 0.5ohms
button | All internal cabling and wiring neat, correct, and undamaged. | Yes,N/A
button | Unused cable entry sealed. | Yes,N/A
button | Heaters correctly installed. | Yes,N/A
button | Confirm that all insulating bushings and barriers are satisfactory. | Yes,N/A
checkpoint | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages.
label | System KV ¦¦ Test V (dc) ¦¦ Min IR Reading
label | <1.0 ¦¦ 500 ¦¦ 10 MΩ
label | <2.5 ¦¦ 1000 ¦¦ 50 MΩ
label | < 4.6 ¦¦ 2500 ¦¦ 100 MΩ
label | >4.6 ¦¦ 5000 ¦¦ 250 MΩ
textbox | L1 - Earth |  |  | mega ohms
textbox | L2 - Earth |  |  | mega ohms
textbox | L3 - Earth |  |  | mega ohms
textbox | L1 - L2 |  |  | mega ohms
textbox | L1 - L3 |  |  | mega ohms
textbox | L2 - L3 |  |  | mega ohms
textbox | N - Earth |  |  | mega ohms
signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist | ITR-E-40A Bus Bar
section | Details
checkpoint | Bus Bar
button | Check entire Bus Bar and confirm there is no damage | Yes,N/A
textbox | Verify zone bus-bar is rated for
note | Please attatch photo of Bus Bar
button | Bus Bar alignment is correct | Yes,N/A
button | Confirm all jointing bolts are present and have been torque tested in accordance with the manufacturer and design requirements. | Yes,N/A
label | Acceptable Bus Bar Torque Settings:
label | Bolt: M6 ¦¦ M8 ¦¦ M10 ¦¦ M12 ¦¦ M16
label | Torque: 10Nm ¦¦ 20Nm ¦¦ 30Nm ¦¦ 40Nm ¦¦ 60Nm
button | Confirm all transit packing and preservation materials have been removed. | Yes,N/A
button | Confirm Bus Bar clearances conform to manufactures and design requirements. | Yes,N/A
button | Confirm all Bus Bars are secure within the supports. | Yes,N/A
textbox | Record the total number of bus bar joints.
signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist | ITR-I-21A - Instrument and COntrol Cables
section | Details
checkpoint | Instrument and Control Cable
button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
button | Check dressing / cleating, cable undamaged | Yes,N/A
button | Cable mechanically protected | Yes,N/A
button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
button | Screen correctly made off | Yes,N/A
button | Glanding / Locknuts correctly installed. | Yes,N/A
textbox | Gland type - from: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
textbox | Gland type - to: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
textbox | Confirm spare cores and shields are terminated and conform to drawings and client spec.
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
signoff | Installed by:
checkpoint | Client Representative
signoff | Client Representative:
checklist | Electrical Safety Ceritificate (ESC)
section | Details
checkpoint | Please upload Electrical Safety Certificate here when complete (ESC)
checklist | ITR-I-01 Fire and Gas Detection Alarms
section | Details
checkpoint | Fire and Gas detection alarms
textbox | Make and Model
textbox | Type
button | Location correct as per drawings | Yes,N/A
button | Component & Type / Model correct per equipment schedule | Yes,N/A
button | Cable connection & termination correct | Yes,N/A
button | Installation free of mechanical damage and clean | Yes,N/A
button | Glanding correct and spare entries plugged with correctly rated plug | Yes,N/A
button | E.O.L Installation | Yes,N/A
button | Test tubing installation | Yes,N/A
button | Detection Path Clear | Yes,N/A
checkpoint | Inspection
textbox | Tag No.
textbox | RX Tag No:
button | Area Classification correct | Yes,N/A
textbox | Hazardous Area Certificate:
textbox | Detector Type:
textbox | Gas Type:
textbox | Supply Voltage:
textbox | Output Signal:
checkpoint | Functional Check
button | Self Test | Yes,N/A
button | Alarm Operation | Yes,N/A
button | Fault Relay Operation | Yes,N/A
textbox | Measured output (clear path)
textbox | Measured output (blocked path)
textbox | Measured output (filter in place)
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-E-15 UPS Installation
section | Details
checkpoint | UPS Installation
button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
button | Check for mechanical damage. | Yes,N/A
button | Panel IP rating is correct. | Yes,N/A
button | Holding down arrangement and seat alignment correct. | Yes,N/A
button | Panels aligned correctly. | Yes,N/A
button | External bonding correct | Yes,N/A
button | Phase identification correct. | Yes,N/A
button | Instrument, indication lamps & interlocks correct. | Yes,N/A
button | Main switches, contactors, fuses etc. sized & identified correctly as per Single Line Drawings. | Yes,N/A
button | Check Main Isolator and Bypass switch operation | Yes,N/A
button | COM Interface & Mod Link. | Yes,N/A
button | Padlocking facilities correct. | Yes,N/A
button | Check internals for cleanliness. | Yes,N/A
button | Check manual operation of selector switch, MCB, push button, etc. | Yes,N/A
button | Incoming cable correctly installed, terminated & supported. | Yes,N/A
button | All internal cabling & wiring neat, correct & tight. Unused cable entries sealed. | Yes,N/A
button | Drawings marked up with relevant changes and As-builts complete. | Yes,N/A
checkpoint | Test results
textbox | Earth Continuity, Insulation Resistance, Temperature, Phase Rotation, Polarity.
signoff | Installed by:
checkpoint | Client Representative
signoff | Client Representative: