## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | HPP-UGL-CIV-GN-GEN-ITP-015 FRP (structures) - Rev.2 | itp | HPP-UGL-CIV-GN-GEN-ITP-015 FRP (structures) - Rev.2 |  | 1c6dc460-8091-476b-a2ce-699177311463
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
c60c84df-1b49-58cf-b11b-a418b623f5f5 | note | Ref docs - Issued drawings / Site copy drawings
27b52c1a-f966-5003-a5ee-d541c8c0c9c5 | note | Acceptance criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
c757d7ae-6f26-5a2a-b27a-b5bd5f4d1d37 | button | Acceptance | Yes,No,N/A
af9030db-2a2a-54ed-af9c-867c84bcf9c9 | note | HPP CON Key - S
106f7316-8d0d-5d74-9265-63467605ee7b | note | HPP QA Key - S
| checkpoint | 1.2 - Lot Traceability
293b4f1f-30e7-5be1-b927-5144c449312c | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
7a1a3754-e0f2-5e4c-8de1-93612a8956a4 | note | Acceptance criteria - Prepare a lot map for traceability of the work area.
23661ccc-69d5-5485-834d-ed82e53f416c | button | Acceptance | Yes,No,N/A
66eca277-178d-5a8d-a085-59e626240b3b | note | HPP CON Key - S
faab98b1-75a4-5e18-a9a9-836a0f920e4f | note | HPP QA Key - S
| checkpoint | 1.3 - Set out
a39907b4-c760-5ce3-9fb3-bb5647fd20be | note | Ref docs - Drawings
19e04819-6d01-5023-ae3b-0f73c38fcffd | note | Acceptance criteria - Setout structure to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
69934601-e4f5-594e-a07b-dfb805c8b05f | button | Acceptance | Yes,No,N/A
637640fd-6e6b-5f5f-a206-e30f9565b2df | note | HPP CON Key - S
6c0e1d82-c98b-5674-88a7-cbcfa08a3dc8 | note | HPP QA Key - S
| checkpoint | 1.4 - Underlying Lot Conformance
a4049f0f-e0f0-5826-bafd-d8a2c3345b6e | note | Ref docs - Underlying Lot ITP
b8236a7c-c6d9-55f3-b01b-68aa4e6603b3 | note | Acceptance criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
0ac16a93-bc94-5e4c-9337-ebbf4b018b64 | note | ○ Refer underlying lot ITP(s)
f09bcdbd-3336-5288-ac44-cbfbb8d176ac | button | Acceptance | Yes,No,N/A
00ace88b-6f05-57df-a43b-99283da2a24e | note | HPP CON Key - S
bfa433fb-2b5b-5d9b-9e7b-72a56c65d3ab | note | HPP QA Key - S
| checkpoint | 1.5 - Site Checklist(s)
32bc56b0-8cb2-5d3c-90e5-ab7c2a25873f | note | Acceptance criteria - Have Site checklist(s) been signed and uploaded?
d9b7a3d3-3883-5c95-a1b3-6eb9ed6dabf8 | button | Acceptance | Yes,No,N/A
4e146152-5e77-551b-abd2-0221f0f0eab6 | note | HPP CON Key - S
1756e808-b4ff-5143-9f9a-39a90a90d446 | note | HPP QA Key - S
15d89f3d-c29d-538a-ad81-8d542818de25 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
090e428b-da7c-5cf6-9141-217383e53ec3 | tickbox | Site Checklist(S)
| section | 2.0 Excavation and Pipe Laying
| checkpoint | 2.1 - Excavation
3b8b2767-6792-530e-88b1-77b8e8069680 | note | Acceptance criteria - Excavate to the depth nominated on the drawings and remove any loose material at the base.
85229522-06ac-5b5e-8723-22be12663ae2 | note | ○ Ensure excavation is carried out to a width which will not impede external formwork.
0f5dbbe2-3f30-5114-a650-6eb95db57fc5 | button | Acceptance | Yes,No,N/A
f2b0d068-4e87-5114-8178-60fb3de8b363 | note | HPP CON Key - S
9c84627f-73c1-544c-8930-fe34efe0952c | note | HPP QA Key - S
3c97fbcf-5a42-588e-9c82-3f1af4d039cc | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
| checkpoint | 2.2 - Unsuitable Material
5426b24d-2901-51c9-ace8-7a872f38d00f | note | Ref docs - Spec. 1112 Earthwork s [Cl 4.6]
8ef2a836-5a4a-593f-b4df-78253403674b | note | Acceptance criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
a8d36eb4-a4a8-5875-8973-037801ad8285 | note | ○ HOLD POINT
7e365618-a204-507b-b90e-06699581e4f7 | button | Acceptance | Yes,No,N/A
f729a7fe-f743-52fe-8ebf-9645d513d5fc | note | HPP CON Key - H
bf494884-aca1-5043-8010-d2a02ef0ce6f | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Compaction - Foundation
69db9fd3-d99a-5260-a7f3-8498b1760824 | note | Ref docs - Spec. 1112 Earthworks [Cl 4.7, 4.13], Spec 0161 [CL 7.2]
ab05bf26-ae78-5a3e-ae6b-d85f92e7c13d | note | Acceptance criteria - Foundation (including any unsuitable replacement) to be compacted to a relative compaction of 97% modified to a depth of 200mm below foundation level
d3c4e944-e310-5db9-a286-ed7197b7db32 | note | ○ Test Frequency = 1 per 500m2
4f2d7ee8-65ff-57c2-841d-6757de46941e | button | Acceptance | Yes,No,N/A
2b34550b-0bf9-5016-a1c2-3728e039a13b | note | HPP CON Key - S
77e38b80-4cdc-594a-b44d-39da84e7b0cc | note | HPP QA Key - S
6cb42743-474b-5fbd-86f7-a515260f4ff6 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
6f32605f-8c52-53cb-b118-e49920920531 | tickbox | Test reports
| checkpoint | 2.4 - Foundation Inspection
95ad6f1a-a51f-5fb1-83ee-24f551c37215 | note | Ref docs - Spec. 1112 Earthwork s [4.7]
f12fa3f1-d446-50ce-9595-7173058ac9fd | note | Acceptance criteria - Foundation to be inspected by the Superintendent prior to placing blinding
c004eb4b-dbb0-5568-bdf6-2e5434bf56e6 | note | ○ HOLD POINT
15f654bc-7f62-5b41-9423-cdaf5e2a8ef1 | button | Acceptance | Yes,No,N/A
cd5f360d-b988-5503-bab1-373eeaef6938 | note | HPP CON Key - H
fa9f8289-a7fa-5f69-80e9-50a399eb41c2 | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.5 - Blinding
63edb35d-4763-597f-b887-45bb30fff3a0 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.6]
2894bab0-030e-52e9-9bbe-1eb3d6015d31 | note | Acceptance criteria - Blinding (N15) for Reinforced Concrete Bases to be a 100mm thick mass concrete layer or as otherwise shown on the drawings.
d2d300f1-f7a2-5159-ba6e-f6691208fbbf | note | ○ Unreinforced bases can be poured directly on the earth
2870a525-a839-5f23-9cca-63ffaaa05d50 | button | Acceptance | Yes,No,N/A
8e4af1ad-574b-5e81-9974-e6b3dee5d43a | note | HPP CON Key - S
208f0f0d-9f31-5a1a-acc2-3504fb55e05d | note | HPP QA Key - S
| checkpoint | 2.6 - Mating Concrete Surface Preparation
ba9be1c7-c353-5e97-bb57-9953af79b95d | note | Ref docs - Spec. 0002 [CL 3.9]
1bae79c4-c065-57c7-afbd-a8dd9c39f3bb | note | Acceptance criteria - Construction joints prepared and free of loose material
f31cdbcd-6915-53f6-90e2-d5876191a727 | note | ○ Dowelled joints prepared and bond breaker applied for expansion joints if applicable
4a57aab1-bc4f-544f-8893-6620f4d2f63c | button | Acceptance | Yes,No,N/A
cf524272-f047-5fab-8ce6-af1a8e18c176 | note | HPP CON Key - S
93d33769-7a96-5487-ab3d-eede1cce7204 | note | HPP QA Key - S
| section | 3.0 Installation of Cast In-situ Structures
| checkpoint | 3.1 - Formwork
3cc9ba6d-efaa-506f-b3ad-4f5ecd323e06 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 4.0] Drawings
2df1831c-3ac1-50ea-8955-cbe03abf27b6 | note | Acceptance criteria - Formwork installed as per drawings and adequately supported.
4928edac-8e32-5eaf-93f9-5ec6e4f490cf | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
8803f5f3-fca3-5bdb-a6c8-4c1b5e98d1f0 | note | ○ Formwork engineers inspection certificate complete and received Survey report to be received prior to ordering concrete.
1f6d7ae4-fb05-5332-98be-c192fd495e7d | note | ○ HOLD POINT
9d30863e-b837-5a69-89e4-8713c272cabe | note | ○ Before Placing Concrete
ed72ee01-bed2-5b3c-8432-ea2d7482a209 | button | Acceptance | Yes,No,N/A
231d7d5b-4d3f-51f0-8102-72b691c30712 | note | HPP CON Key - H
f5a1ef13-b621-5a68-bee7-b7476de6f500 | note | HPP QA Key - H
4843d47a-c944-5a0c-a6b4-9d6e785e0a0d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a15889a8-fbd3-531d-b838-784bf08e0e7c | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.2 - Steel reinforcement
ac9f018e-a3bb-5926-9205-975c1cb10540 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 5.0] Drawings
0e6e0cca-f6c5-56a4-86b7-37fddee9cb65 | note | Acceptance criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars. Inspection per layer installed.
019bb8f0-b18c-55ec-bc14-632f412cfb3a | note | ○ Concrete pre-pour inspection complete.
f2a968ed-9bc5-5436-a3c2-f049400816ba | note | ○ HOLD POINT
ae514156-ffc0-54d5-a6aa-21288d906438 | note | ○ Before Placing Concrete
b282c6f8-e3b7-5398-9546-0dbcbdcf92c7 | button | Acceptance | Yes,No,N/A
09b98ce8-13b0-5230-9b0f-62421f6684e9 | note | HPP CON Key - H
5fffa92e-dff3-52c7-a543-a06d9a7e8c55 | note | HPP QA Key - H
6b1dd62b-6552-5a76-84a6-1774ac924842 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
fd7d16b4-80b8-5790-b038-672fe6f76c59 | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Reinforcement Splice Lengths
60eba216-d399-51ca-acae-04291c2d06b8 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 5.7]
c0129881-53cb-5c56-8b2d-35c0ed86b139 | note | Acceptance criteria - Where splicing of reinforcement is not shown on drawings min. lap lengths shown below shall be adopted. (SPT-0002 Table 6)
41e5e9ab-be38-5e8a-a2b5-22dd34854ddf | button | Acceptance | Yes,No,N/A
2b10f850-c0ef-50e5-8519-ecc72ac271d9 | note | HPP CON Key - S
5cb118a2-2b4e-5eb6-9cd7-15840242f988 | note | HPP QA Key - S
| checkpoint | 3.4 - Pit & Pipe Connections
57fb4b92-3185-5ac0-a425-d0ad549be4a5 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3], Spec. 0002 Concrete supply, construction, and grouting [Cl 2.6] Drawings
cc27d066-f4e7-53de-9b1e-77e5227b7483 | note | Acceptance criteria - Inlet and outlet pipes to be integrally cast into foundation/pit walls and the joint waterproofed as per design requirements.
18329f62-221c-5baf-abdc-96643f16fae6 | note | ○ Embedded pipes to be adequately restrained against flotation
bd6d1fc2-60a5-526c-9bbb-e461a4eead02 | note | ○ HOLD POINT
dc92fa36-cafc-5090-955a-5162616e48d7 | button | Acceptance | Yes,No,N/A
126b4ce9-68a4-5898-8521-fa2e0226e258 | note | HPP CON Key - H
5762e6cb-16fb-587c-b2ef-8f71c6857229 | note | HPP QA Key - W
9a7fc328-f94e-5737-99e2-b517edb03d27 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - ITP for associated pit/pipe reviewed for conformance
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.5 - Installation of Core Holes, Voids, HD Bolts and Embedments
337fc49d-9a2b-5196-9304-516a4f949f83 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [CL 2.6, 7.1, 7.2, 7.3]
d07b2da7-103a-5819-a15d-9b984ead675f | note | Acceptance criteria - Firmly Fixed in position in all directions
ebcca41d-a7e0-565f-8750-abeb64a223c1 | note | ○ Reinforcement displaced where necessary, bars requiring cutting approved by superintendent
9f97cb56-64c9-5fbb-a317-675be1c88349 | note | ○ Integrity of surface treatments maintained (galvanising, painting etc) Threads covered
ee74b250-085c-5148-a717-346c9336be99 | button | Acceptance | Yes,No,N/A
69f81e9e-e633-5f7a-84ac-ab7b8c1ebe5d | note | HPP CON Key - S
41ec78ca-c645-5971-b2a8-cd32b78bf95a | note | HPP QA Key - S
| checkpoint | 3.6 - Tolerances of Core Holes, HD Bolts and Embedments
07971b7b-4f67-533f-81a4-ba622283a52f | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [CL 2.6, 7.1, 7.2, 7.3]
cedcac6d-5497-57c1-8fbd-fe001ab678af | note | Acceptance criteria - HD bolts positioned using a template. Tolerance for HD bolts as per CL 7.2 (see below table)
05e5488d-d141-5680-97ff-cdc75d983dea | note | – – – – – – – – – – – – – – – –
9384639f-ea1e-5d83-9c84-02412f27a83a | note | Condition ¦¦ Tolerance
d0b60f01-14fa-53fe-8788-5ad04322cf84 | note | – – – – – – – – – – – – – – – –
149654ca-d8f6-5452-8233-ae473813a991 | note | Any 2 bolts within a group ¦¦ ± 3mm Centre to Centre
503f2756-f6a8-50af-bb4d-19cc4f7d80af | note | Adjacent HD bolt groups ¦¦ ± 6mm Centre to Centre
d0301179-9829-51b9-9c08-119fb064df7c | note | Bolt Projections – From concrete level ¦¦ + 5mm, -0mm
42c6b0f5-3dba-564e-98ef-004a18ba3a7d | note | Embedded steel finishing flush with surface ¦¦ ± 3mm from surface
499c2e64-738e-5439-9b76-1a801fd124e5 | note | Bolt reduced level ¦¦ + 5mm, -0mm
4e4aca4e-56d3-581e-a14e-6d7efc0a0405 | note | Verticality of any bolt ¦¦ 1:300
37bfcef0-a7f1-5bdf-86a8-b41398e3a572 | note | – – – – – – – – – – – – – – – –
9635091f-0fe6-5b29-a400-3d90ca9ce57b | note | Maximum accumulation of 6 mm per 30,000mm along an established column line of multiple HD bolt groups, but not to exceed a total of 25 mm.
45109b99-aced-580f-b389-baa113829e6e | note | 6 mm from the centre of any HD bolt group to the established column line through that group.
7c7ca62f-81d5-530b-9bbd-2c5ea5552285 | note | – – – – – – – – – – – – – – – –
7bc10d94-7f84-5b6b-9737-4a27236651cd | note | * Before pouring concrete of the GT & GEN foundation, MPW TA will check the setting condition of GT & GEN anchor bolt. Witness Point as per MHI ITP.
ffc4ec84-8b44-55b2-b649-088e88da1e33 | note | ○ Tolerances for other embedded fabricated items in line with AS 3990 or AS4100 as applicable.
7b2840c5-f60a-5855-af09-f0fbfc6df691 | note | ○ Pre-pour survey performed and recorded to verify location
4ae78dd6-5d98-5753-bc15-9442fb7e6ca3 | note | ○ HOLD POINT
4bac51fc-e0f1-5f35-b588-35dd08bd0a7e | button | Acceptance | Yes,No,N/A
a4871036-f8a3-5542-ae37-957eb8ea5582 | note | HPP CON Key - H
2ec3b2a1-eb03-5e96-907e-ff70e370bd8a | note | HPP QA Key - W
6cd1443e-fb30-57b4-bd3a-35cb69617cc9 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
85808471-4318-5ba8-a295-cc022dd7fde7 | tickbox | Pre-pour inspection and Survey Records Inc MHI Check Sheet for GT & GTG Anchor Bolt Setting CG-64294
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.7 - Earthing for Concrete Structures
fe3dcd26-f1c8-5c1d-a3e9-48f669582bc5 | note | Ref docs - Drawings Spec. 0002 Concrete supply, construction, and grouting [CL 2.6]
cde7527b-421b-5fb9-aad1-567c4625caf9 | note | Acceptance criteria - Earthing installed for concrete structures as per provided Drawings
cfd470dd-d375-5775-b083-998dcf03573c | note | ○ HOLD POINT
7fa907db-2a74-5b85-b51d-23b266ec7115 | button | Acceptance | Yes,No,N/A
404c8417-6796-5f05-92f4-1f2a3179c811 | note | HPP CON Key - H
e3b0a604-902e-5bb2-ae11-c147271d5fc7 | note | HPP QA Key - W
c81b894a-b9ff-5bd1-8ab1-f0c52f56d4b9 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a5af57e4-d3f2-575a-818a-a9f952cd87c0 | tickbox | UGL Earthing FIC
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.8 - Concrete Mix and properties
88d8c435-87de-5761-b33d-4e43800de7c0 | note | Acceptance criteria -
9d02740d-6f7d-52b1-88f8-09b143b64a50 | textbox | Concrete compressive strength required (28 days) |  |  | MPA
1625ffeb-3852-52d9-b8b8-88e449b6c0e2 | textbox | Approved Concrete mix ID
4b8ef3b3-6ba5-577a-a1ba-5e65d868c696 | textbox | Slump |  |  | mm
4448dc0d-0f9a-50c1-8fc1-7295f84dda01 | button | Acceptance | Yes,No,N/A
959955a4-0db7-5ab3-b9fe-88ae3af0d9c4 | note | HPP CON Key - S
a6d477ab-833f-5a85-97e0-cd2a7b1df453 | note | HPP QA Key - S
b07f0337-09c2-5e9b-955a-15ae0455a298 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e021cc4a-296c-5d7f-850b-7f5ceabaf273 | tickbox | Material dockets
d0592693-43c4-5d96-88c7-5677d8dc1f84 | tickbox | Concrete pour records
| checkpoint | 3.9a - Concrete Supply Temperature - GT Foundation Only
35f7d8c3-bf2c-5ff9-8e9b-f4897935b04f | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.2] Thermal Analysis Report
ebd4f1bc-bdb0-50fd-b372-c1784cac609b | note | Acceptance criteria - Temperature of concrete at the time of placement must be minimum 10°C and maximum 25°C.
2c22cdac-e3b6-50bf-81f3-7fb7d6b4a79c | note | ○ Ambient air temperature at the time of placement must be between 5oC and 30oC.
98cfe851-1a78-5949-a584-8dfbb897441f | note | HPP CON Key - S
1183f600-cbfd-52fe-b248-9b48de445901 | note | HPP QA Key - S
559d0214-42dc-55b3-b6fb-ff5b606397ab | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
3ec71db2-af72-5797-a8fd-5f6c951a5472 | tickbox | Material dockets
087a61dd-b65a-531c-bccb-0617c9deaaea | tickbox | Concrete pour records
| checkpoint | 3.9b - Concrete Supply Temperature - Other foundations
c35afc66-2df0-51ee-ae45-e70da0e665af | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.2]
0940340c-05b8-5e07-a093-5bde3ca7b19a | note | Acceptance criteria - Temperature of concrete at the time of placement must be minimum 10°C and maximum 30°C.
76d97212-9e71-5ebc-9259-f84a141212a4 | note | ○ Ambient air temperature at the time of placement must be between 5oC and 32oC.
2e9d639d-6e05-5855-808b-a76aafbda699 | note | ○ If ambient temperature is between 32oC and 38oC, seek approval from superintendent to proceed by taking special precautions noted in the specification.
6106368a-22bd-561b-8e36-8d67eb735bae | note | HPP CON Key - S
58d57739-e55f-5c7a-964f-54359370e5c3 | note | HPP QA Key - S
e5b4d62f-cd31-5b66-b04a-deb472efa957 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e71bfb8d-5540-5a8d-91d2-14edd0b07be2 | tickbox | Material dockets
98d74c5d-0304-55ea-960a-a796cdcbd6d7 | tickbox | Concrete pour records
| checkpoint | 3.10 - Concrete Placement
9f2de50d-41e7-5597-bbd9-e609adc2b7ec | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.4]
764ec084-1d72-5ad7-ba25-baef327c3a4e | note | Acceptance criteria - Ensure elapsed time between batching and discharge of the mix does not exceed 1.5 hours.
84b9244b-cf0d-5ee2-aa20-d5a7d6f92d1e | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
ea8205de-6b81-540b-8228-f57bcfe180ed | note | ○ Concrete thoroughly compacted – one internal vibrator per 10m3 concrete placed per hour
de8a9c71-290f-54cc-b315-adf85418c73f | note | HPP CON Key - S
2ad81e71-414e-5a37-9446-2c7e11fb2624 | note | HPP QA Key - S
b72f714b-8fec-5644-b2a8-b79b713d9b89 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
2ba49439-f07c-511c-b936-f18ffe564ef8 | tickbox | Material dockets
25c4852b-659d-5f45-9b55-99e60acaa2d9 | tickbox | Concrete pour records
| checkpoint | 3.11 - Concrete Slump Testing
5b9f099c-20f0-5739-93aa-b745b6edbb43 | note | Acceptance criteria - Slump Test - One per batch of concrete
1b7fbf04-779b-594f-9a6a-80acc77f8d8b | note | ○ Slump within tolerances specified in AS 1379
96624dfe-946f-5afb-8816-e0f66519c218 | note | – – – – – – – – – – – – – – – –
81fb2849-189d-5116-bc2e-c2ce6f100c5f | note | TABLE 5.1 PERMISSIBLE TOLERANCE ON SLUMP
4658b425-cca7-5c1a-b6fc-bbbe498a5fe6 | note | – – – – – – – – – – – – – – – –
e1c70c06-c24b-51b4-a154-1b903baf9a20 | note | Specified slump, mm ¦¦ Tolerance, mm
16ec52d6-613b-56de-9c2e-881e7ad15a36 | note | <60 ¦¦ ±10
05116e1b-ad67-586c-ac4a-1f898a9962dc | note | ≥60 ≤80 ¦¦ ±15
1e2af528-b471-5afa-aeb4-1687404d3609 | note | >80 ≤110 ¦¦ ±20
ce890bb2-ae9f-5720-b611-3eb5a2efbb8e | note | >110 ≤150 ¦¦ ±30
ba297919-053a-58c4-bac9-e8df4d463ae5 | note | >150 ¦¦ ±40
1a676764-2fc1-55a4-acc1-98f2f376b972 | note | – – – – – – – – – – – – – – – –
d11c3fce-4d03-5c18-bb45-f063b0256ab3 | note | ○ Testing to be executed by a NATA accredited test facility
98b3aec1-f598-5dca-93d9-f0467ed0182f | button | Acceptance | Yes,No,N/A
27270519-e8cc-5459-9fb0-71d1cabd91dd | note | HPP CON Key - S
8539b4ed-6665-538d-895c-75c884d37e2e | note | HPP QA Key - S
a6d1870f-ddbf-5597-a69f-79ab50488a9b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a77dac0d-02f3-5657-9438-5f8ff8972111 | tickbox | Concrete pour record
| checkpoint | 3.12 - Concrete Compressive Strength Testing
b9ebd3f1-c936-5e3d-96c8-f4f94913f0b8 | note | Ref docs - Drawings
3123de94-a33c-5888-8743-c2d7fc42f9f2 | note | Acceptance criteria - Compressive Strength Testing - 2 x 7day and 2 x 28day per 50m3
026bc221-7673-539f-b1db-6b1c41fab104 | note | ○ Testing to be executed by a NATA accredited test facility
a6a3ea46-21ea-50f6-af9d-b6d15b2cd755 | button | Acceptance | Yes,No,N/A
fa54ee5f-7895-5887-aa14-9b1a04424625 | note | HPP CON Key - S
006dd9d9-2d97-5a79-8e42-2d3173ba540b | note | HPP QA Key - S
8899d1d4-5e51-50a3-85a4-8be961059375 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
8e0972fd-b94c-5426-868a-c363ddc91103 | tickbox | Concrete pour record
| checkpoint | 3.13 - Surface finish
e4312dd8-a9c7-5709-93ae-4529afdb2a56 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2] Drawings
dbfc1aee-224b-503e-be4b-366f86ad10d8 | note | Acceptance criteria - Concrete surfaces shall be true and even, free from honeycombed surface depressions or rejections.
b8ae8951-6e62-5e0e-a234-85598ef899f7 | note | ○ Formed surfaces conform with surface finish requirements of AS3610 for the surface class nominated.
79fa46d6-50de-581d-8b12-ce952e0de138 | note | ○ WITNESS POINT
8943fd5f-546a-5289-972a-f632a08bd33b | note | ○ 1 day prior
4f272d95-264f-58de-a0d6-b1b6ccc69228 | button | Acceptance | Yes,No,N/A
120c236b-ef33-53fb-8622-0ae1ec5476c2 | note | HPP CON Key - W
d3f7b209-8841-57e7-be9d-97e25298a35b | note | HPP QA Key - W
| checkpoint | 3.14 - Surface Treatments
8c1fdc14-2157-5627-ab09-cd8b8c2c8700 | note | Acceptance criteria - Any surface treatments to be applied are approved for use and appropriate dose rates have been determined
1035ad11-11d2-53f3-b074-a73a9700e768 | button | Acceptance | Yes,No,N/A
8b620b08-a8de-5796-99ba-6b85e132375f | note | HPP CON Key - S
f46d2b7d-3150-5e40-8f16-130dfb8a5e73 | note | HPP QA Key - S
| checkpoint | 3.15 - Joints
e65a9e6a-0dcb-51a5-83ed-2ddcc653bf1a | note | Ref docs - As per drawings
665c6405-f1aa-57e8-8305-febada7c26aa | note | Acceptance criteria - As per design drawings. Sawn joints to commence as soon as the concrete has hardened sufficiently.
27df5007-1afd-5fe0-babf-dc6ad34a1a4b | button | Acceptance | Yes,No,N/A
7fa0db36-44a0-52bd-947b-005213c7be25 | note | HPP CON Key - S
c001d7c1-3284-573d-9a3a-b177b1f8544f | note | HPP QA Key - S
| checkpoint | 3.16 - Curing
94bb7700-ab5b-508f-8626-8e2544947b28 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
dc69f3c4-f35b-5743-84bd-921ca3b5cb53 | note | Acceptance criteria - From completion of finishing cure continuously with an approved method for a min period of 7 days or as directed by the Superintendent.
3b5d7966-3f4c-5ce4-8e9c-c657ec12d03c | note | a. Ordinary Portland cement concrete – 7 days
7bbf6599-0027-599b-b0b2-1ae95334afc0 | note | b. High early strength concrete – 3 days
c6d2b559-813f-5013-9a6b-98d060af180c | note | c. Concrete with cement or pozzolan materials – 10 days
873066b8-3106-5adf-9832-e6b1da18e0c6 | button | Acceptance | Yes,No,N/A
d9f1d4b3-54ab-56f1-a0e1-248f44e17237 | note | HPP CON Key - S
458a34d5-011f-563d-91d8-5446ac32447d | note | HPP QA Key - S
| checkpoint | 3.17 - Stripping of formwork
35b777e6-badd-5fe2-8442-776cdf8b3457 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 4.4.5]
9e03ef7a-fb00-5921-ac86-3c518b752a3e | note | Acceptance criteria -
1e69a203-a31d-5e78-8faa-199ffdae563b | note | – – – – – – – – – – – – – – – –
01470246-51dc-5365-9433-688f2a805d4c | note | Member Type ¦¦ Member ¦¦ *Effective Span mm ¦¦ Minimum Stripping Time (days) for Average Air Temperature during period prior to Stripping
7aad0af7-bc0c-580a-ba07-41d92fd2e632 | note | – – – – – – – – – – – – – – – –
764c8c3a-e837-5084-8516-0d622e51f631 | note | - ¦¦ - ¦¦ - ¦¦ 20°C and over ¦¦ 10°C to 20°C ¦¦ 4°C to 10°C ¦¦ Under 4°C
ef5d86d7-c2e0-577d-9610-ac8c8e5cdf9f | note | Vertical Unloaded ¦¦ Wall, column, beam side, slab side ¦¦ 0 ¦¦ 2 ¦¦ 3¦¦ 5 ¦¦7
c8eac0eb-4593-5918-bd8f-fad3512f9ae7 | note | Vertical Loadbearing ¦¦ Wall, column Or loadbearing structure ¦¦ 0 ¦¦ 5 ¦¦ 6 ¦¦ 7 ¦¦ 9
2b37da7c-c690-5be3-8e14-8990cab57864 | note | Horizonal ¦¦ Slab ¦¦ Under 3000, 3000-6000, Over 6000 ¦¦ 7, 10, 14 ¦¦ 10, 14, 21 ¦¦ 14, 21, 28 ¦¦ 21, 28, 28
ec14358e-9018-509e-a5b7-39ca78ede5eb | note | Horizontal ¦¦ Beam ¦¦ Under 3000, 3000-6000, Over 6000 ¦¦ 10, 14, 21 ¦¦ 14, 21, 28 ¦¦ 21, 28, 28 ¦¦ 28, 28, 28
e6c937d4-6f9a-525a-adc9-caa35af7e11c | note | – – – – – – – – – – – – – – – –
2a1cb5f5-565e-5482-95c0-91be2c29985f | note | * Effective span is the maximum distance between supports (either temporary or permanent)
8ed4499d-1b5a-5fa2-991e-80b79412bb38 | button | Acceptance | Yes,No,N/A
093530d8-5b61-5f96-877e-8de2c2978a10 | note | HPP CON Key - S
e8e9386f-a035-505f-a6cd-493acf0d3911 | note | HPP QA Key - S
| checkpoint | 3.18 - Concrete Repair (If required)
5e9a21a8-f820-5c8e-9c2b-10cd6b69ec3e | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.7]
e06a559e-22f3-54ec-9abb-fabbb9e96515 | note | Acceptance criteria - Defective concrete shall be repaired or replaced. The materials and techniques of repair shall be examined and approved by the Superintendent prior to the commencement of repairs.
60e0d1cc-1850-5e38-b15d-fb0f3c86eb80 | button | Acceptance | Yes,No,N/A
25f88d95-00cb-58e2-a684-1a6367f86180 | note | HPP CON Key - H
70f2304a-f11e-5558-a690-c5ded96e869c | note | HPP QA Key - H
191049c2-b196-55e2-9876-7d817a847a30 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a7f5c8a8-314a-56c1-8bb2-9d2da2ad29e2 | tickbox | Grout Placement Checklist
4f4640ea-7a9b-56c2-8b80-d92ef1c69ec0 | tickbox | Approved Aconex Corro for Repair Methodology
| signoff | AUTHORITY HOLDPOINT
| section | 4.0 Backfill and Compaction
| checkpoint | 4.1 - Structure Backfill
59c6f5de-f4a6-53e4-870d-d5eaf942cc4a | note | Ref docs - Spec. 1112 Earthworks [Cl 4.10]
349dd079-d528-56c5-8a27-dc8601602217 | note | Acceptance criteria - Backfill to be Select fill for material within 1.5m of pavement and General Fill below 1.5m deep.
9caee80f-f5fc-52fc-813e-c44fc842d893 | note | ○ Placed in layers of maximum compacted thickness of 150mm
92a5817c-5ee2-51e0-9320-dab8ce122e39 | note | ○ Select backfill material to be a granular material with a maximum particle size of 50mm and a PI between 2 & 12
e860e39e-7d4f-5d07-a7ad-027b129c661e | button | Acceptance | Yes,No,N/A
77d67d54-d548-55bb-80bd-d008339f3bfa | note | Key - S
57645045-5a0f-51af-8eb3-3231bd1a1316 | note | HPP CON Key - S
73a549e2-4f8e-572d-81d6-6ed671d0675a | note | HPP QA Key - S
52b9d4f8-d140-543a-9706-185b1e2fc4cb | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
104a1dbd-a834-5ea8-920c-91d265cdf1da | tickbox | Material Test Report
| checkpoint | 4.2 - Compaction - Backfill
b89ae186-c174-591f-9ecf-f51694aeac5e | note | Ref docs - Spec. 1112 Earthworks [Cl 4.13]
5486e8f2-b6c8-576d-b245-27d6dba40a51 | note | Acceptance criteria - Minimum relative compaction requirements for backfill against structures to be:
1cb72897-a5b6-5219-8173-6d289a0f0e43 | note | – 92% for general fill
47224381-ee3c-5630-964a-f44678c1dc44 | note | – 97% for select fill
bac16d63-e9b2-5936-a73c-b3b20c1b63d4 | note | ○ Test Frequency = 1 per layer
f5223613-e16c-55f2-99e8-5535c68cc454 | button | Acceptance | Yes,No,N/A
5d1bdefc-bb83-5f75-bd07-6351eb18cbee | note | Key - S
0cb57372-04a5-51bd-9c87-90e230f48a67 | note | HPP CON Key - S
da778957-246d-578d-abc0-1c35719642c7 | note | HPP QA Key - S
c2d4c4ee-a13d-591f-a955-c98e6be4a4f7 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a899bc54-24c3-5b1d-b5d8-be38f1b4fc35 | tickbox | Test reports
| checkpoint | 4.3 - Moisture Content
c4da9a38-cfd3-5f3d-a296-a79307434fef | note | Ref docs - Spec. 1112 Earthworks [Cl 4.13 & 7.1]
3a947d67-ec5f-5219-a148-771ce7bdfb6e | note | Acceptance criteria - Moisture Content for Backfill material to be within 60% to 90% OMC unless otherwise approved by Superintendent
388a1cd8-f979-5bfd-9ace-f10312af56b9 | button | Acceptance | Yes,No,N/A
13575a25-f01d-5fcb-b96e-ae2c7bebcc1f | note | Key - S
481ba2c2-b3f9-532b-96c6-7b42c7bffb74 | note | HPP CON Key - S
b5e00f0f-4056-573b-8819-bc6485ccc290 | note | HPP QA Key - S
fa7f6cab-f070-59b7-909f-918c250c5dee | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bfdda01c-9157-5215-8bac-72dea317b87d | tickbox | Test reports
| section | 5.0 Conformance check
| checkpoint | 5.1 - Survey Report
29f9ec94-6368-50b2-8d73-c06750bd74fc | note | Ref docs - Spec. 0161 Quality [Cl 3.13] AS3610
fa1741f5-91d6-5395-a170-3d0f940ade47 | note | Acceptance criteria - An as-built survey of the structure has been completed to ensure all structures are within the following construction tolerances:
efc150b7-decf-50e2-a54d-1112885f0942 | note | ○ Absolute position in plan shall be within 10 mm.
1641c1da-816c-51f9-81a9-fcccb33ffe3c | note | ○ Floor to floor plumb shall not exceed 0.002 times the dimension between the floors or 10 mm whichever is the greater.
a6053e4e-594f-5912-b738-1fca6ca40196 | note | ○ Deviation from the specified dimension shall not exceed 0.001 times the specified dimension or 5mm, whichever is the greater.
551b5a3e-cb86-577f-ba5b-461c88d5d88f | button | Acceptance | Yes,No,N/A
06962e6e-8236-5627-bf5d-f5393da75cb2 | note | Key - H
54b626e2-40fd-52e7-8b5a-492c6610ff0c | note | HPP CON Key - H
ffef801f-4f9a-5a08-84ee-cc1b958403f1 | note | HPP QA Key - W
85b88ed7-06b6-58b2-bbf1-5543ce2dfc3c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
25a5449c-936e-5169-ae46-7c7bf59f74be | tickbox | Survey report
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 5.2 - Concrete Test Results
64f3e2b6-82a8-5a01-9dbf-d5740038d4cc | note | Ref docs - Spec. 0002 [Cl 8.2]
f8e74bdd-7a8c-5879-a074-5a29d6194aa5 | note | Acceptance criteria - Certificates received, reviewed and conforming to requirements for each pour.
5d1f06b2-f61f-5ee5-9a48-ff9afebe4d1f | button | Acceptance | Yes,No,N/A
bccafc4d-e697-5769-89e7-7b2db3ff85bb | note | Key - S
385efe8c-ed08-501a-bf91-78225cdfa508 | note | HPP CON Key - S
0b4672ba-84e5-5265-85ce-25d0bbabe724 | note | HPP QA Key - S
a99de69a-a0f2-58e0-8989-70f8d6ca4c0a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bb72dc0e-43bc-594d-aacd-4988b628abb8 | tickbox | Test reports
| checkpoint | 5.3 - Acceptance and closure of non-conforming items
15faa6b8-fca2-57ea-8ac9-a3d8bd896424 | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
6ed162a6-ba8d-5296-b135-e95de0633a22 | note | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
623c84c6-34fd-55fe-9055-27d9cbf27935 | note | ○ HOLD POINT
507bbb34-4bb5-5c11-9375-91a90202dbda | button | Acceptance | Yes,No,N/A
e7611d8c-dc40-53ef-a940-f6a294e0b195 | note | Key - H
980564ee-0691-5f61-9388-fb07d2648b89 | note | HPP CON Key - H
532712e8-fd7a-528f-8bf0-ebbd210ca22b | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT