## res_ITP_1_Inspection_and_Test_P
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP - Foundations & Concrete Work | itp |  |  |  |  | ITP - Foundations & Concrete Work
section | Preliminary
checkpoint | Concrete Mix Design Approved
label | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | Test Required: Jacbos
label | Inspection By: Engineer
label | Task Timing or Task Frequency: Formal request/RFI
label | Acceptance Criteria: Approved by Engineer
label | UCCL - H
label | Client - R/A
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Concrete Mix Design Trails
label | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | Test Required: Temperture, slump and strength
label | Inspection By: Engineer
label | Task Timing or Task Frequency: Per Mix Design
label | Acceptance Criteria: Approved by Engineer
label | UCCL - H
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Concrete - 1
label | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | Test Required: Compressive Strength
label | Inspection By: Supplier
label | Task Timing or Task Frequency:
label | • 1 Set of 3 tests for every 50m³ testing at the plant and 100m³ on site.
label | • Slump test on first 2 trucks from each plant.
label | • Then visual slump test for the pours over 20m³ and intermitted/random testing every 100m³.
label | Acceptance Criteria:
label | • Slump Test, Air Content Test, Compressive strength test results, shrinkage strain
label | • Accreditation/ Registration certificate from Laboratory
label | UCCL - H
label | Client - R
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Concrete - 2
label | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | Test Required: Slump Test
label | Inspection By: Supplier
label | Task Timing or Task Frequency: As Per above
label | Acceptance Criteria: As per Above
label | UCCL - H
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Concrete - 3
label | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | Test Required: Air Content Test
label | Inspection By: Supplier
label | Task Timing or Task Frequency: As Per above
label | Acceptance Criteria: As per Above
label | UCCL - H
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Concrete - 4
label | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | Test Required: Shrinkage strain at 56 days
label | Inspection By: Supplier
label | Task Timing or Task Frequency: As Per above
label | Acceptance Criteria: As per Above
label | UCCL - H
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Shop Drawings
label | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification - 12.1.4
label | Test Required: Approved shop drawings prior to fabrication
label | Inspection By: Engineer
label | Task Timing or Task Frequency: 10 Days before commencing fabrication
label | Acceptance Criteria: Approved by Engineer
label | UCCL - H
label | Comments: Applicable to embedded items. Structural Steel ITP will cover material conformance
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Supply of Reinforcement - Steel reinforcement compliance records
label | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification - STEEL REINFORCEMENT COMPLIANCE 6.1.7
label | Test Required: Schedules shall be prepared by the supplier and reviewed/accepted by CEL prior to fabrication.
label | Inspection By: Engineer
label | Task Timing or Task Frequency: Prior to manufacturing any reinforcement
label | Acceptance Criteria: Manufacturer´s Mill Certificate/Rebar schedule/Rebar summary sheet
label | UCCL - H
label | Client - R
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
section | Pre-construction site works
checkpoint | Ground Condition/Subgrade
label | Specification Reference: TABG-JEC-0-ULG-STR-DET-3104(1) Note 4
label | Test Required: Geotechnical testing
label | Inspection By: Contact
label | Task Timing or Task Frequency: Before placement of any site concrete, Scala penetrometer testing, proof roll.
label | Acceptance Criteria: SITE TO BE INSPECTED BY AN EXPERIENCED GEOTECHNICAL ENGINEER AND CONFIRM SUITABILITY FOR MINIMUM 100 kPa ULTIMATE BEARING CAPACITY.
label | UCCL - H
label | Client - R
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Trim Sub grade
label | Specification Reference: As per IFC Drawings and approved CAD files
label | Test Required: Survery plan
label | Inspection By: UCCL/Engineer
label | Task Timing or Task Frequency: Before placement of any site concrete check sub grade profile
label | Acceptance Criteria:
label | • Finished height for sub grade + 10/-50mm. Minimum thickness to be 50mm as per IFC Drawing.
label | • Target RL as per IFC Drawings.
label | UCCL - H
label | Client - S
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Site Concrete/binding
label | Specification Reference: As per IFC Drawings and approved CAD files
label | Test Required: Visual Inspection
label | Inspection By: UCCL/Engineer
label | Task Timing or Task Frequency: Thickness, minimum 50mm, consider 75mm depending on subgrade.
label | Acceptance Criteria: Finished height for site concrete to be within +/- 10mm. Thickness, minimum 50mm, consider 75mm depending on subgrade.
label | UCCL - H
label | Client - S
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
section | Foundation
checkpoint | Setout
label | Specification Reference: As per IFC Drawings and approved CAD files
label | Test Required: Surveying as built/Visual Check
label | Inspection By: UCCL/Engineer
label | Task Timing or Task Frequency: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | Acceptance Criteria: Finished height of embebded items +/- 10mm vertically and +/-20mm laterally
label | UCCL - H
label | Client - S
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Pre-pour Insepction
label | Specification Reference: Design / IFC Drawings
label | Test Required: Visual Inspection
label | Inspection By: Engineer
label | Task Timing or Task Frequency: Pre pour inspection for each Pour or Foundation
label | Acceptance Criteria: Pre pour inspection check sheet
label | UCCL - H
label | Client - W
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Embeded Items
label | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | Test Required: QA Documents and PS4, Visual inspection
label | Inspection By: Engineer
label | Task Timing or Task Frequency: For each Foundation Embeded items
label | Acceptance Criteria:
label | • As per specifications. Confirmation from Engineer.
label | • Deviation of Centerlins of the plate relative to the specified positions of the cenre-lines to be +/- 10mm vertically and Laterally
label | UCCL - H
label | Client - R
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Backfill
label | Specification Reference: Design / IFC Drawings
label | Test Required: Visual Inspection
label | Inspection By: Enginner
label | Acceptance Criteria: Backfilling with site won material with small plate compactor in confined space and static roll with 4T Roller where applicable with max. of 300mm lift
label | UCCL - W
label | Client - R
textbox | Date Completed:
section | Post Construction
checkpoint | As Built & Final Design Documentation
label | Test Required: Surveying
label | Inspection By: UCCL
label | Task Timing or Task Frequency: For each Pour
label | Acceptance Criteria: Confirmation From Engineer on as built records & redline mark ups
label | UCCL - H
label | Client - R
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY
checkpoint | Completion Inspection inc. Construction Defects Report
label | Test Required: Completion inspection on the structure by CEL
label | Inspection By: CEL/ UCCL
label | Task Timing or Task Frequency: For each structure
label | Acceptance Criteria: Provided a completed construction defect report that that details any remedial measure taken, snag lists closed out
label | UCCL - H
textbox | Date Completed:
holdpoint | HOLD POINT AUTHORITY