## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | FHC-ITP-023 - Conduit, Pit & OCS Installation Rev1 | itp |  |  |  |  | FHC-ITP-023 - Conduit, Pit & OCS Installation Rev1
section | 1 - Preliminary Works
checkpoint | 1.1 Check for correct documentation
note | FREQUENCY: Prior to commencing any activity
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA: Ensure that all employees and subcontractors are:
note | – using the correct and complete set of drawings
note | – all drawings are the latest revision
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: Drawings and drawing registers
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Visual inspection
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed off
note | – – – – – – – – –
note | HP*
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer
note | – – – – – – – – –
textbox | DATE:
checkpoint | 1.2 Implementation of all measures and controls
note | FREQUENCY: Prior to commencing any activity
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: OHSCP, PHSCP, PCMP, EMP, ECP, CEMP, ERA, QMP, CHMP, SWMS
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: OHSCP, PHSCP, PCMP, EMP, ECP, CEMP, ERA, QMP, CHMP, SWMS
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Visual Inspection
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed off
note | – – – – – – – – –
note | HP*
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer
note | – – – – – – – – –
textbox | DATE:
checkpoint | 1.3 Materials
note | FREQUENCY: Per Batch
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA:
note | • Carpark Lighting A pit is to be installed adjacent to each lighting pole with 1 x 100mm HD conduit and 1 x 63mm conduit installed between pit and the point of supply. 2 x 32mm HD conduits are to be installed between the pit and the pole mounting base.
note | • Electrical supply conduit all conduits for underground mains shall be heavy duty 'Orange' underground category PVC pipe complying with the most recent issue of AS/NZS 3000 Australia/New Zealand Wiring Rules.
note | • Communications conduit to be white 1C50 HD PVC conduits and 1C100 HD PVC conduits
note | • Camera mounting poles and structures shall meet AS47806.2 (2006) Section 5.4.1 (k)
note | • Cable pit lids shall be VicRoads type approved, impressed with 'VicRoads' and 'Electrical', 'Communication', 'Traffic signals" as appropriate as per VicRoads Standard Drawing TC-1220
note | • All equipment labelling to comply with requirements of NIST-013.4
note | • Cable pits shall be 435mm dia x 550mm deep, Type 43 plastic HDPE – Aco Cablemate cable pit with concrete lid or equivalent
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: NIST-5031 3.2.2.5 (f), Drawings
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Verify
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed
note | – – – – – – – – –
note | HP*
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer, Electrical Subcontractor, Vline representative
note | – – – – – – – – –
textbox | DATE:
section | 2 - Construction Works
checkpoint | 2.1 Survey set-out
note | FREQUENCY: As required
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA: Work is set out in accordance with drawings.
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: Work procedure, Drawings
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Verify
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed
note | – – – – – – – – –
note | HP*
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer
note | – – – – – – – – –
textbox | DATE:
checkpoint | 2.2 Excavation/Boring & Trenching
note | FREQUENCY: Prior to Backfill
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA: Trenches shall be excavated to a depth required to achieve the specified depth of cover and drainage slope, plus an over-excavation of approximately 50 mm to allow for bedding sand. The width of trenches shall be as required to fit all the conduits and pipes for services sharing the trench with specified separations, plus a further 50 mm minimum clearance from the outermost pipes or conduits.
note | • Where trenches are excavated across roadways, car parks or paved areas, the Electrical Contractor shall backfill the trench with 20mm of Class 3 crushed rock. The crushed rock shall be placed in layers not exceeding 150mm finished depth and compacted to a minimum of 95% of standard density. The backfilling shall extend for a minimum of 1.0m outside all paved areas and shall be subject to the supervision of the V/Line delegated representative.
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: L1-CHE-STD-077 Sect 6.10.6
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Verify
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed
note | – – – – – – – – –
note | HP
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer
note | – – – – – – – – –
textbox | DATE:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 Installation of Pit and Conduits
note | FREQUENCY: Each Lot
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA: Underground conduits shall have a minimum 450mm cover if around the site but away from the track corridor, should only be in the non-trafficable areas. If exposed to traffic, the depth should be 650mm.
note | • Upon installation conduits shall be cleaned and tested using a mandrel of at least 90% of the conduit inner diameter and length three times the inner diameter.
note | • Multiple conduit entry penetration holes on a pit wall shall be spaced at least 50 mm apart in horizontal and vertical planes
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: NIST-013.3 Sect 4.2, L1-CHE-STD-077 Sect 6.9
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Verify
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed WP
note | – – – – – – – – –
note | IP
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer
note | – – – – – – – – –
textbox | DATE:
checkpoint | 2.4 Back Fill of Trenches (Trafficable)
note | FREQUENCY: Each Lot
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA:
note | • Bedding: Graded recyclable glass in accordance with MTM standard L1-CHE-SPE-313
note | • Backfill: VicRoads 20mm class two crushed concrete base compacted to 95% of standard density in 150mm thick layers
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: NIST-5031, L1-CHE-SPE-313, MRP-708-C-AUR-DRG-20-TNT-CLT-0810
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Verify
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed
note | – – – – – – – – –
note | WP/IP
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer
note | – – – – – – – – –
textbox | DATE:
checkpoint | 2.5 Installation of Draw Cords
note | FREQUENCY: Each Lot
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA: A draw wire of 6mm polypropylene blue/yellow rope shall be placed in each pipe and suitably anchored at each end. Pipe ends shall be sealed using pipe end caps or an approved equivalent to prevent the ingress of dirt or sludge into the pipes.
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: NIST-012 Sect 7.12(d)
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Verify
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed
note | – – – – – – – – –
note | IP
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer
note | – – – – – – – – –
textbox | DATE:
checkpoint | 2.6 Installation of Marker Tape
note | FREQUENCY: Each Lot
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA: A 150 mm wide orange coloured PVC marker tape with the words “DANGER BURIED CABLES” shall be installed in all trenches at 300 mm below ground level except where cables are permitted in shallow trenches due to rock. In this case the depth of the marker tape shall be at the discretion of the Infrastructure Manager.
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: NIST-012 Sect 7.11.1
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Verify
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed
note | – – – – – – – – –
note | IP
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer
note | – – – – – – – – –
textbox | DATE:
checkpoint | 2.7 Cable Pits & Pit Lids
note | FREQUENCY: Each Lot
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA:
note | • Cable pits constructed and installed as per drawings
note | • Pits shall be placed at each horizontal change in direction or at spacing no greater than 100m
note | • Seperate pits shall be used for power conduits (orange) and communications (white).
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: OCS Drawing Package
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Verify
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed
note | – – – – – – – – –
note | IP
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer
note | – – – – – – – – –
textbox | DATE:
section | 3 - Completion
checkpoint | 3.1 Cleaning of Site
note | FREQUENCY: Each Lot
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA: All obselete cabling to be removed during installation and disposed of appropriately. Upon removal of all redundant signalling equipment; the site shall be cleared of all project scrap and associated rubbish.
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: NIST-012.2 Sect 23
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Visual inspection
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed
note | – – – – – – – – –
note | IP
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer
note | – – – – – – – – –
textbox | DATE:
checkpoint | 3.2 Recording/As Built
note | FREQUENCY: Each Lot
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA: As-built drawings will be completed by the Contractor based upon the installed system by a process of editing the approved ‘for construction’ drawings.
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: NIST-013.3 Sect 5.1.3
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Verify
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed, As Built Drawing
note | – – – – – – – – –
note | IP
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer
note | – – – – – – – – –
textbox | DATE:
checkpoint | 3.3 Commisioning
note | FREQUENCY: Each Lot
note | – – – – – – – – –
note | ACCEPTANCE CRITERIA: Commisioning to be checked against V/Line checklist. For OCS Only
note | – – – – – – – – –
note | REFERENCE DOCUMENTS: V/Line Commisioning Checklist
note | – – – – – – – – –
note | INSPECTION/TEST METHOD: Verify
note | – – – – – – – – –
note | RECORD OF CONFORMITY: This ITP signed, V/Line Checklist signed
note | – – – – – – – – –
note | WP/TP
note | – – – – – – – – –
note | RESPONSIBILITY: Fulton Hogan Engineer
note | – – – – – – – – –
textbox | DATE:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | Print Name:
text | Position:
text | Date: