## Sheet 1
|  |  |  | Project: | Salford Street Watermain Renewal |  |  | Lot Number
|  |  |  | Project Location | Salford, Moana, Wilton, Waihopai Streets |  |  | Scope Of ITP
|  |  |  | Job # 549262 | Contract CC1842 |  |  | Sub Contractor |  | SM Civil
Inspection & Test Plan / Checklist
|  |  |  | Signatory |  | Role |  | Person(s) Responsible
|  |  |  | Requiring FH Signature |  | Site Engineer |  | Brendon Ferguson
| Action | H | Hold Point for Engineers Representative | Requiring FH Manager Representative |  | FH Job Manager |  | Joe Findley
|  | W | Witness for Engineers Representative | Requiring Engineers Representative |  | Engineers Representative |  | Nick Watt
|  | H | Hold Point internal |  |  | Contractors Foreman |  | Johnny McCarthy (SM Civil)
|  | M | Monitor |  |  | Environmental Advisor |  | Ciccone Tweedie
[6 empty] | STMS |  | FH STMS
No: | Inspection / Test Point | ACTION (W, M, H) | Conformance Criteria (What's Required) | Detail | Frequency | Inspection / Test Method | Verification Records | Standard | Signatory | Date(s) | Signature
8.0 Moana Street - Wilton Street to Waihopai Street (DN180mm)
D5.4.2 | Isolation Valve MOANA-WILTON-2 CH769 (1) | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 23 fig.W4 & W9 | Per each valve | Inspection | Photos | — | Site Engineer
D5.4.2 | Isolation Valve MOANA-WILTON-2 CH769 (2) | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 23 of the drawings | Per each valve | Inspection | Photos | — | Site Engineer
D5.4.2 | Isolation Valve MOANA-WILTON-2 CH769 (3) | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos | — | Site Engineer
D5.5 | Fire Hydrant MOANA FH 03-2 at CH773 (1) | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 23 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D5.5 | Fire Hydrant MOANA FH 03-2 at CH773 (2) | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D5.5 | Fire Hydrant MOANA FH 03-2 at CH773 (3) | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#123 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#121 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#120 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#117 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#116 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#113 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#109 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#108 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#105 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant MOANA FH 04 at CH890 (1) | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 23 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D5.5 | Fire Hydrant MOANA FH 04 at CH890 (2) | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D5.5 | Fire Hydrant MOANA FH 04 at CH890 (3) | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#104 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#100 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#101 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#99 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#96 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#92 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#79 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.4.2 | Isolation Valve MOANA-WAIHOPAI-2 CH962 (1) | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 23 fig.W4 & W9 | Per each valve | Inspection | Photos | — | Site Engineer
D5.4.2 | Isolation Valve MOANA-WAIHOPAI-2 CH962 (2) | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 23 of the drawings | Per each valve | Inspection | Photos | — | Site Engineer
D5.4.2 | Isolation Valve MOANA-WAIHOPAI-2 CH962 (3) | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos | — | Site Engineer
| Link in at intersection of Waihopai Street and Moana Street (1) | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail K in sheet 16 of the drawing | Before backfilling | Inspection | Photos | — | Site Engineer
| Link in at intersection of Waihopai Street and Moana Street (2) | W | Thrust protection to be constructed (x2) | As per detail K in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos | — | Site Engineer
| Removal of existing tee and bends and reinstated with straight through pipe and associated bends/thrust protection at intersection of Waihopai Street and Moana Street | W | Pipe reinstated through old line and thrust protected | As per detail L in sheet 16 and typical details sheet 18 | per connection | Inspection | Photos | AS/NZS 4130 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#88 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D2.7 | Trenching and excavation | M | In accordance with NZS 4407 | AP65 Subbase particle size and sand equivalent | Daily | Inspection | RCP and digging checklist | NZS 4407 | Site Engineer
D2.9.1 | Pressure testing & disinfection (1) | H | AS/NZS 2566:2 Section 6.3 | pressure testing of the new PE main | Prior to link in | Testing | Test records | AS/NZS 2566:2 Section 6.3 | Engineers Representative
D2.9.1 | Pressure testing & disinfection (2) | H | NZS 4404:2004 Appendix C AS/NZS 2566:2 Section 7 | Disinfection of the new PE main | Prior to link in | Testing | Test records | NZS 4404:2004 Appendix C AS/NZS 2566:2 Section 7 | Engineers Representative
D1.3.3 | Engineer's inspections | H | Inspection report | Enginer's inspection for pipe, concrete pre pour, pre sealing | As required | Inspection | Email | — | Engineers Representative
C1.18 | Surface Reinstatement (1) | H | Engineer's Approval | Mark out the trench including overcuts | Prior to surfacing | Inspection | Email | — | Engineers Representative
C1.18 | Surface Reinstatement (2) | H | NDM testing | Provide NDM test results for AP65 and AP40 layers | Prior to surfacing | Testing | Test records | — | Engineers Representative
9.0 Cruickshank Crescent (DN125mm)
D8.3 D8.4 | Lateral connection to house no#38 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#23 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#36 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#21 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#34 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#19 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#17 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant CRUICKSHANK FH 03 at CH40 (1) | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 23 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D5.5 | Fire Hydrant CRUICKSHANK FH 03 at CH40 (2) | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D5.5 | Fire Hydrant CRUICKSHANK FH 03 at CH40 (3) | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#15 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#32 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#30 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#28 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#26 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#24 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant CRUICKSHANK FH 02 at CH177 (1) | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 23 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D5.5 | Fire Hydrant CRUICKSHANK FH 02 at CH177 (2) | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D5.5 | Fire Hydrant CRUICKSHANK FH 02 at CH177 (3) | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#22 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#20 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#18 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#18A Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#16 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#14 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#12 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#10 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#8 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant CRUICKSHANK FH 01 at CH58 (1) | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 23 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D5.5 | Fire Hydrant CRUICKSHANK FH 01 at CH58 (2) | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D5.5 | Fire Hydrant CRUICKSHANK FH 01 at CH58 (3) | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#5 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#6 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#4 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#3 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#1 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.4.2 | Isolation Valve CRUIKSHANK-TERRACE CH12 (1) | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 23 fig.W4 & W9 | Per each valve | Inspection | Photos | — | Site Engineer
D5.4.2 | Isolation Valve CRUIKSHANK-TERRACE CH12 (2) | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 23 of the drawings | Per each valve | Inspection | Photos | — | Site Engineer
D5.4.2 | Isolation Valve CRUIKSHANK-TERRACE CH12 (3) | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos | — | Site Engineer
| Link in at intersection of Cruickshank Crescent and Terrace Street (1) | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail N in sheet 22 of the drawing | Before backfilling | Inspection | Photos | — | Site Engineer
| Link in at intersection of Cruickshank Crescent and Terrace Street (2) | W | Thrust protection to be constructed | As per detail N in sheet 22 and typical details as per sheet 24 | Before backfilling | Inspection | Photos | — | Site Engineer
D8.3 D8.4 | Lateral connection to house no#13 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#11 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#9 Cruickshank Crescent | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D2.7 | Trenching and excavation | M | In accordance with NZS 4407 | AP65 Subbase particle size and sand equivalent | Daily | Inspection | RCP and digging checklist | NZS 4407 | Site Engineer
D2.9.1 | Pressure testing & disinfection (1) | H | AS/NZS 2566:2 Section 6.3 | pressure testing of the new PE main | Prior to link in | Testing | Test records | AS/NZS 2566:2 Section 6.3 | Engineers Representative
D2.9.1 | Pressure testing & disinfection (2) | H | NZS 4404:2004 Appendix C AS/NZS 2566:2 Section 7 | Disinfection of the new PE main | Prior to link in | Testing | Test records | NZS 4404:2004 Appendix C AS/NZS 2566:2 Section 7 | Engineers Representative
D1.3.3 | Engineer's inspections | H | Inspection report | Enginer's inspection for pipe, concrete pre pour, pre sealing | As required | Inspection | Email | — | Engineers Representative
C1.18 | Surface Reinstatement (1) | H | Engineer's Approval | Mark out the trench including overcuts | Prior to surfacing | Inspection | Email | — | Engineers Representative
C1.18 | Surface Reinstatement (2) | H | NDM testing | Provide NDM test results for AP65 and AP40 layers | Prior to surfacing | Testing | Test records | — | Engineers Representative
Comments:
Accepted By :_____________________________________________ |  |  | Sub-contractor | Accepted By :_____________________________________________ |  | Project Manager |  | Accepted By :_____________________________________________ |  |  |  | Quality Manager
Signature:_____________________________ |  |  |  | Signature:________________________________________________ |  |  |  | Signature:________________________________________________