## Master List Templates
Id | Type | Name | Values | Prompting Name
8a4bfb74-04d2-47d1-9d9c-4e0e45c8e71f | checklist | Documents |  | Documents
d27e664b-b8db-4dae-8ce3-cc3995597fdf | section | Details
9483f8e0-de31-4f34-b59b-8778c5e33994 | checkpoint | Document attached
71311430-12af-4de5-b2e1-320343a3d7c5 | checklist | Test ITP | itp | Test ITP
20380797-825e-43d5-b636-1e28953acadd | section | Preliminary Works
107e3d9c-f945-48ad-a893-382139576ad3 | checkpoint | 3.1 Pre-construction Photos
955645e1-125c-52ac-a36d-9f7aaf64fd68 | note | Inspection Point: Quality Control Activity - Photos of worksite including vehicle access points.
de815be8-ff5b-5bbf-8fcf-b6a74f875d15 | note | ○ Photos of any existing defects/damage.
f629ba35-c6c9-5e84-afb6-f12afe19ba50 | note | Acceptance Criteria - Coverage of whole site
b343e756-6236-534e-a04c-adde741f9cf9 | note | Verifying Document - Photos saved
487d2c77-26c6-574d-9f8c-69197b900e60 | note | Reference: Contract Specs/Standards - D1.4
aa7dcc23-975c-5d3e-90f1-e46ecef13a8e | note | Inspection Point/Signature & Date - PM
441f8f47-9e59-4e93-af48-52ea9db74b4f | checkpoint | 3.2 Verify Construction Drawings
5979cb19-48d2-5a0f-8a4a-18a2495e019b | note | Inspection Point: Quality Control Activity - Verify Construction Drawings that are in the site folder are the latest revision.
77adfc3c-637c-5532-a2de-de99b4eb0801 | note | Acceptance Criteria - Latest drawings approved
2e7272cf-1b67-5992-8aea-1c720473b1e1 | note | Verifying Document - Drawings Register
91384230-7de8-55b8-b9f0-cf3094b4e632 | note | Reference: Contract Specs/Standards -
53f92b21-b0f6-50b0-9a66-65c339b74caa | note | Inspection Point/Signature & Date - PM
92a4d361-6a90-4261-aacc-b17a70c5ba02 | checkpoint | 3.3 Road Authority Notifications
a5905a4b-3c67-5ea9-9f5c-3f49ad93a559 | note | Inspection Point: Quality Control Activity - Corridor access Permit.
0158a33e-7ce3-58a8-babd-2c00a85ada9b | note | ○ Block by block Temporary Traffic Management Plans.
c980e384-1324-5a31-ad80-c5f42c7f2909 | note | Acceptance Criteria - Permit & Traffic Plan approved
670802ca-5daf-518d-ba40-b11f61b8bba8 | note | Verifying Document - Work Access Permit & TMP
ae04fd1d-8285-5e71-9dc0-6c451b22a24a | note | Reference: Contract Specs/Standards - C1.09, D1.4
afbe1801-0461-5ff9-9968-d71d709c4667 | note | Inspection Point/Signature & Date - PM
d39f31d1-9f41-49b3-8e2e-f1d32ae48a60 | checkpoint | 3.4 Management Plan
dacc70c9-2410-5db2-bd45-66d975547e52 | note | Inspection Point: Quality Control Activity - H&S Plan
c98cf114-7fba-5cd7-9f75-05f14d1dc0c4 | note | ○ Environmental Plan
ff8ca60d-7b07-570e-837e-2ea6f5924d22 | note | ○ Quality Assurances
6ad36c2d-187f-596a-87f1-b024ccfeeffd | note | Acceptance Criteria - Plans & Safety Measures in place
d5f70aa4-3aed-5da0-b07e-f5410907778d | note | Verifying Document - H&S Plan, Method Statement
79d6f9d4-a271-5202-907c-58e7835bcb83 | note | Reference: Contract Specs/Standards - D1.3
7f636cf1-81e6-5b8d-8b3a-e415c151f5d7 | note | Inspection Point/Signature & Date - PM, CR
5d595464-2779-423b-add8-0d8127f9cada | checkpoint | 3.5 Public Notification
3a84e0b1-0335-5dc4-bb53-a8236469f1e8 | note | Inspection Point: Quality Control Activity - Notice of works to properties in the construction zone in each block
111ac031-f06c-52e2-8d36-657040eef63d | note | ○ Notification to Rubbish collection contractor.
6425c7b3-a4a7-5fc9-b4d2-348fb03ae6aa | note | ○ Project Signage
1fb132d3-92db-5038-aa91-124209dd7f89 | note | Acceptance Criteria - 48 hours prior notification
6a28c857-a4f5-59ec-8a55-c083caf0c3a7 | note | Verifying Document - Letter to residents
c926fb82-add6-5d96-9893-e1996f955a14 | note | Reference: Contract Specs/Standards - D1.10
bdbcb526-3a1e-5e5d-86ef-0a808ab8369e | note | Inspection Point/Signature & Date - PM
83d17dff-2396-439e-955c-8f1f727f65ed | checkpoint | 3.6 Shutdown/Isolation
6ea865c2-ca78-5854-8fa3-2264bf699993 | note | Inspection Point: Quality Control Activity - Shutdown/Isolation process verified in each block closure
1555c1d5-29de-5a42-a7d4-8b3739287984 | note | Acceptance Criteria - Shutdown process verified
cd7f89f3-8fdf-5085-8c83-7bb9094c8b0a | note | Verifying Document - Notification letters
ef26b893-83e8-5557-854d-c80eb7263938 | note | Reference: Contract Specs/Standards - C1.16, D2.7.8
28d7be85-39af-58e3-9302-9376a974da67 | note | Inspection Point/Signature & Date - PS
d167c212-b415-420c-a15c-45c677294de6 | checkpoint | 3.7 Construction Set Out
742868c8-23f0-5452-9b92-ba186649d8d7 | note | Inspection Point: Quality Control Activity - Correctly mark out the position of the new pipelines for construction.
9e97b2cc-ba1a-5815-b8f9-fbfc1eb1d305 | note | Acceptance Criteria - Construction Plans checked
5b2e22e1-e5ff-5dc0-99bf-61f23b16df05 | note | Verifying Document - Construction Plans
62386f7d-45bf-5fb2-8ee5-5645b5fb6848 | note | Reference: Contract Specs/Standards - D2.7.1
d58502cb-242d-55dc-b860-3551207f6eba | note | Inspection Point/Signature & Date - PS, CR
a5600e25-383f-46d4-8512-0c264c1e449f | checkpoint | 3.8 Pre-Excavation Permits
dae1eccc-c23e-53c5-a82d-0efd94bccfeb | note | Inspection Point: Quality Control Activity - Permit to excavate for the location has been endorsed by an authorised person.
4086823b-a3b0-5514-bed4-f7f9e3b60915 | note | ○ Existing service plans & locates
c1e5fd2a-aef6-51bf-8cd0-bb993a96c4c9 | note | ○ Close approach permits
e9ebe2eb-6bb3-5920-af4f-3e5f51dc6ced | note | ○ Notifiable works
c0184131-3963-58e5-89ee-4c85ee5a746b | note | Acceptance Criteria - Permit to excavate endorsed
ef5bff12-f195-5b6f-aa81-cb8850c90580 | note | Verifying Document - Ground Disturbance Permit
64acb508-1d91-553b-8bd2-2bec3032ca97 | note | Reference: Contract Specs/Standards - D1.7
7835cccc-5334-5c60-a2d5-886aa9e0b519 | note | Inspection Point/Signature & Date - PS
02c8290d-79fe-4b01-a4f8-43e9d4c6e881 | signoff | HOLD POINT
abbb431d-e004-44ec-b738-fab1868140b8 | section | Incoming Goods Inspections
2aa07f2e-4aed-4158-88a0-e6abf1872ee1 | checkpoint | 4.1 Pipe & Fitting Inspections
335e2b85-3765-5d7c-823f-1a30f4f4c2cd | note | Inspection Point: Quality Control Activity - Visual check of materials delivered:
3c2f6b16-25d4-518b-a78c-50cd0381e2b9 | note | ○ Correct Material & dimensions
38ce9bbf-d35b-56d0-9094-6888dbbe0772 | note | ○ Condition & Quantity
e0aca729-1137-5fa6-a9c4-e65d8d4be14e | note | ○ Free of defects – surface abrasion, ovality, not kinked or crushed
c7813b84-576f-505d-b003-53fb30070daf | note | ○ Batch/serial numbers present
e60eb730-8b8d-5bbe-9001-2c575dd38607 | note | Acceptance Criteria - Correct material & no defects
775a2f60-1a0d-5a61-a840-33859f5f5380 | note | Verifying Document - Packing Slips
5523d66d-7eb8-57b7-8130-17f63b83eb86 | note | Reference: Contract Specs/Standards - D2.4,D3.3, D4.3, D5.3, D8.3
4815886f-d85b-584d-a8bf-54bb43596b4d | note | Inspection Point/Signature & Date - PS
18a89c7a-07fc-4278-9ab2-46bbdeed02f3 | checkpoint | 4.2 Pipe & Fitting Storage
736fc6ca-0587-58a7-aa66-1e6006900b05 | note | Inspection Point: Quality Control Activity - Stored as per manufacturers specifications including maximum height limits and safely chocked in place.
88679b02-09b0-5f6d-85d2-86abe8c910f1 | note | ○ All pipes are end capped.
ace5e548-9b68-55f8-acb6-13682245a6d3 | note | ○ No scoring of pipe more than 10% of thickness.
0f1df64d-4495-5578-a941-f201cb9bd702 | note | ○ No damage to epoxy coating on Ductile fittings.
1dbf0fff-4157-5283-af1b-f1fa245cb0fd | note | Acceptance Criteria - Stored as per manufacturer
c2c2afc7-5301-5e5c-ba67-ba552d116bc1 | note | Verifying Document - Manufacturer’s Storage Instructions
99bbba7a-beec-5223-939d-15034191d36d | note | Reference: Contract Specs/Standards -
1dbd7e86-bf3c-5e32-8b08-073e38069992 | note | Inspection Point/Signature & Date - PS, CR
6b2618a5-8d30-4b91-a333-0dfd3ca9cf5f | signoff | HOLD POINT
1f6a3545-531a-431b-8950-db0056c6a96e | section | Construction Inspections
5b9fc0f7-1004-4407-be8c-24b464b7f09e | checkpoint | 5.1 Trench Excavation
02e391fc-3a18-522d-9c19-e2a03e270cfb | note | Inspection Point: Quality Control Activity - Trench width to be sufficient to safely lay the pipe (including shoring if required) and compact the side support of the new pipe. Bedding details below;
a6f490ee-48df-5ce7-ad7c-e1ea3aa3e379 | note | ○ Sufficient room to enable the pipe, joint, bed, haunch or surround shown in the drawings to be accommodated.
eec54b15-5ecd-5436-96af-7f3f1ec2feb7 | note | ○ Trench depth to enable pipe to be laid with the designed cover as shown on construction plans.
8fd021a9-e8d2-5b4c-8b4b-5843892fc6d1 | note | ○ If trench bottom to be suitable to compact pipe bedding as support pipe.
fc3f41ae-94b6-572c-ac89-2a9ef6fb22bf | note | Acceptance Criteria - Trench dimensions correct
e3b19d68-be79-52b1-b552-b4069f08f057 | note | Verifying Document - Daily Site Diary
84a404dc-63b4-5583-b4db-f3add2e91694 | note | Reference: Contract Specs/Standards - D2.6, D2.7
5aa888e2-14d6-582f-9a52-d9c849c2397e | note | Inspection Point/Signature & Date - PS
27edf7a6-5c6f-40e4-b0c0-9ab61a806878 | checkpoint | 5.2 Encountered Services
da1255de-facf-5b78-9de0-40b88d5693d6 | note | Inspection Point: Quality Control Activity - Block by block ensure existing live services are not unnecessarily damaged by works.
5fc0b366-4852-5bfe-a581-cba57122ba03 | note | ○ Repair any services that are temporarily removed during construction.
c6c5167f-c5f2-5998-b8d3-01f5f3e9341c | note | ○ Record any services found.
0631e0d3-22a9-5d7c-8b37-c6cbd46c7c91 | note | Acceptance Criteria - Existing services not damaged
81f412b2-a38d-50f2-a598-84775c34f384 | note | Verifying Document - Encountered Services Record
90c9acea-6aa9-5d0a-b22b-e74a722eebd8 | note | Reference: Contract Specs/Standards - D1.7, D2.7.7
7d0df532-6775-5e02-87ef-5933b5113c19 | note | Inspection Point/Signature & Date - PS
0bb6eb81-7e4a-451f-830e-1b4ed2ca3ea2 | checkpoint | 5.3 Pipe Installation
e9a5264d-e34d-57c2-b251-70577ea28002 | note | Inspection Point: Quality Control Activity - Interior of each pipe visually inspected to ensure free of debris.
4de7eba6-7a52-508a-8f6f-3da7ba17c6ad | note | ○ Re-cap end of pipe after installation.
9fcd0740-534d-500d-8189-e0970be0fe0f | note | ○ Check pipe installed at correct depth.
97372ff6-7a61-5b54-b317-dc368cef403b | note | ○ Ensure all collars are free from contamination in McDougall St berm
d141a6e9-ce08-571e-8cfd-8a4080f2f31b | note | Acceptance Criteria - Pipes free of debris & correctly installed
6c48859f-43ee-519f-b185-e2757b35f5ef | note | Verifying Document - Daily Site Diary
d6e34e20-3287-5bb8-accf-914843f1e5ed | note | Reference: Contract Specs/Standards - D2.5, D2.7, D8.4.2
c344ad27-9a7c-5088-8578-ce9de1f06115 | note | Inspection Point/Signature & Date - PS
315ca360-db4e-4b0f-b047-bcd13a88803d | checkpoint | 5.4 Concrete Pre-Pour Inspection
a0c3ca9d-7c53-5f00-a910-1efc9d53070f | note | Inspection Point: Quality Control Activity - Check dimensions of formwork match details in the Construction Drawings.
63a3685f-631f-50f2-b45b-5b550dd42985 | note | ○ Check pipe fitting joints are clear of concrete pour.
23788df5-5f26-5f32-a93c-2b6f87bf050f | note | ○ Thrust blocks to be poured against good solid natural ground.
2e389bbc-ca69-56cc-991e-0c7ae5298cfb | note | Acceptance Criteria - Thrust blocks against solid ground
4630ea02-6452-5ef8-9df0-b7baf484a9ae | note | Verifying Document - Daily Site Diary & Photos
2a52135d-b44a-5d64-8c2f-594fcb8d9444 | note | Reference: Contract Specs/Standards - D5.1, D5.3.2, D5.7
270f8374-94d2-5ff4-afe3-a9f4d98bb457 | note | Inspection Point/Signature & Date - PS, CR
02e5fe15-a3d0-4117-9c59-df286de87b71 | checkpoint | 5.5 Hydrant Depth
c166f8ac-68a4-56d5-a714-45a77c232876 | note | Inspection Point: Quality Control Activity - Confirm depth requirements have been met;
2f2ace55-1dbf-557c-880b-7b6a3dd25264 | note | ○ Hydrant outlet: 200mm min. to 400mm max.
285e10aa-95d7-51d9-ab64-3b2072cdb2d5 | note | Acceptance Criteria - Hydrant depth verified
9803aeb2-9d90-54ba-9e49-df36b5629658 | note | Verifying Document - Daily Site Diary
f8c94654-15c9-51e9-8452-342e59ecae6e | note | Reference: Contract Specs/Standards - D5.5
cc256614-c42e-5f6e-a39f-f68a89b87155 | note | Inspection Point/Signature & Date - PS
a0e3fce6-d131-4d47-b2fa-1afd64dedf22 | checkpoint | 5.6 Compaction Testing
ba0f25db-c515-54bf-af10-241ef05a2184 | note | Inspection Point: Quality Control Activity - Confirm trenches in paved areas are compacted to standard block by block.
49e7f8fd-7c6b-5d23-b61b-854926d2d227 | note | Acceptance Criteria - Compaction confirmed
22f4308c-0c3d-5079-b554-738af731d09f | note | Verifying Document - Clegg Record Sheet
ea3ff20d-d289-5332-88c3-7d7ac37a937a | note | Reference: Contract Specs/Standards - D2.7.10
bb591b35-fe0b-530a-8cb7-36e77516390e | note | Inspection Point/Signature & Date - PS
cdecfdb6-ad87-453e-b692-8fb65eb5cbe7 | checkpoint | 5.7 Watermain Pressure Testing
1da5f833-284a-5b18-99a9-331354fad608 | note | Inspection Point: Quality Control Activity - Hydrostatic pressure test on new pipeline and fittings block by block.
2f9a2668-68c2-5f33-8c5e-ec33a157d16e | note | Acceptance Criteria - Pressure test passed
36849462-809a-58b1-a71f-40568e648c95 | note | Verifying Document - Pressure Test Record Sheet
a57df2e3-9168-58b3-8e23-04a24658c806 | note | Reference: Contract Specs/Standards - D2.9.1, AS/NSZ 2566.2:2002 Section 6
2d130f10-37f0-55a1-8d72-a460b1f28c32 | note | Inspection Point/Signature & Date - PS, CR
a1e1175c-838a-44d4-97e2-105d86a88295 | checkpoint | 5.8 Watermain Sterilization
ce10429c-a3e0-5c3c-b478-43bc65ee371b | note | Inspection Point: Quality Control Activity - Flushing and sterilizing full length of new pipeline and fittings block by block.
14828d25-390c-5376-8cc6-48d3ee750694 | note | Acceptance Criteria - Sterilization completed
72845af4-3a77-57b0-bfd3-8c8b00ad194a | note | Verifying Document - Sterilization Record Sheet
c67f69b9-5827-576d-aa4b-e05ef53cf735 | note | Reference: Contract Specs/Standards - D2.9.1, AS/NSZ 2566.2:2002 Section 6
99631707-3d31-5b31-aff4-efb8e8c21979 | note | Inspection Point/Signature & Date - PS, CR
ddf7462a-b76e-41eb-a36d-0de8b8dd2a87 | checkpoint | 5.9 As-built Information
517e67db-4033-58c1-a6ca-d3362f98ca30 | note | Inspection Point: Quality Control Activity - Capture data for all new construction work.
ba450391-5c8a-5c55-b1c4-c22f0833b96c | note | Acceptance Criteria - Redline mark-up plan submitted
3eb797e2-7275-5590-8fac-676aa04c793f | note | Verifying Document - Redline Mark-up Plan
b2cc15a1-1e88-5f06-9c50-d2d2827d97a5 | note | Reference: Contract Specs/Standards - C1.22
3c06f156-3b4e-51b2-91ab-48d5a7624304 | note | Inspection Point/Signature & Date - PM
6fda002d-0146-4403-8542-79c60a61f794 | signoff | HOLD POINT
8b2fb51e-3dea-4864-85cf-ea6c1f2099ae | section | Final Inspection and Handover
e1185f06-97ee-41c3-ba68-9fa87ec8f197 | checkpoint | 6.1 Final Inspection of Works
937e6486-743d-5157-8e7e-d97207a69798 | note | Inspection Point: Quality Control Activity - Work is inspected by the authorised person and complies with the nominated specification/standards
17149ea4-e39d-5a08-9b34-a5a55b8544b8 | note | Acceptance Criteria - Work inspected & complies with standards
69020570-efe6-5843-a2ad-9a102698555a | note | Verifying Document - Practical Completion Certificate
b28f2ad8-0f63-5340-9f55-310a0e29c35a | note | Reference: Contract Specs/Standards -
5422ff6f-c5f8-5de4-8a22-f168bf4f557c | note | Inspection Point/Signature & Date - PM
aca660fb-dc8b-43a6-b666-e84980ea511b | signoff | HOLD POINT

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
828297a3-59b1-463c-a1f2-c300e80e3fa6 | checklist | ITP - Salford, Moana, Wilton, Waihopai Streets - 1.0 Pre-construction / 2.0 Pre Commencement checks | itp | 1.0 Pre-construction / 2.0 Pre Commencement checks
cbead606-ad79-48b4-9b91-a3617cc8de13 | section | 1.0 Pre-construction - 1.0 General
5c1a05a0-51f6-436a-98b8-246a5440bdf2 | checkpoint | D1.5 - Pre-work site inspection/Existing asset assessment
89ac2773-9201-52db-9830-0deafd1f37d0 | note | ACTION (W, M, H) - H
89ef6130-ac5d-592a-9785-3a89a4197924 | note | Conformance Criteria (What's Required) - Carry out inspection and video existing assets and condition throughout work areas.
2daa2505-7be1-5c5f-b86e-4927c7fb086b | note | Detail - Existing asset assessment completed
3dd23180-a7be-5b07-b06d-f905161839be | note | Frequency - Pre-Construction
f8fcd670-5fc0-5d2d-8d52-9ad13f3e80d4 | note | Inspection / Test Method - Inspection
2711717b-57d4-573e-91b6-0e0c5001aa7a | note | Verification Records - Copy on file
9841336b-36dd-5cbf-aff9-14215d13deae | note | Signatory - Engineers Representative
710e8f3b-0e11-4000-8a01-7de3cc71cd27 | section | 1.0 Pre-construction - 2.0 Project Plans
28149626-dc2a-4ea7-8bbf-b863704f8f20 | checkpoint | D1.19 - Contract Programme
65952356-8a40-51ec-a341-d0a1a0b48821 | note | ACTION (W, M, H) - H
90dc0055-8ba9-5b36-92d3-1f213615c027 | note | Conformance Criteria (What's Required) - The Contractor shall submit to the Engineer an appropriately detailed programme for approval.
5a6046f0-2875-592c-a543-2973ed901e84 | note | Inspection / Test Method - Submission
97b764b6-0311-579f-af3a-456147a6f5e6 | note | Verification Records - Approved Contract Programme
4c06f578-9b6b-51ee-9a07-de3c5477ff13 | note | Signatory - Engineers Representative
0d2a13b8-f7ec-48bb-922c-28e5a2e12913 | signoff | HOLD POINT
480de9fe-e285-48dc-88b0-774128f288c6 | checkpoint | D1.3 - Site Management plan
7fb19dd7-ff00-55fa-b723-aa0cad4f3500 | note | ACTION (W, M, H) - H
cd5ff337-59ac-5081-8988-b49c7960d9c3 | note | Conformance Criteria (What's Required) - Engineer to accept the CMP prior to any work commencing on site
a89571d1-21ae-5237-bd10-2ce602c74f54 | note | Detail - CMP including safety, quality and environmental plans submitted for approval
3409b356-9453-545d-a8c1-511e8ebaab6c | note | Frequency - Prior to any work commencing on site
15a8ab95-6282-50c4-8b86-c37cb05e7450 | note | Inspection / Test Method - Submission
be429778-a7b3-52ca-aacf-352753575819 | note | Verification Records - NTC
173bac0e-73fe-5ae6-a9a3-f8c25e863af9 | note | Signatory - Engineers Representative
68255d69-afe9-484b-a05b-3afd851047d6 | signoff | HOLD POINT
98fbd21d-0e3f-4de4-802e-41f7b92ab919 | checkpoint | C1.7 - Traffic management Plan
554cf8d5-5e92-526d-bf33-37666dd4b6ef | note | ACTION (W, M, H) - H
c766ff41-d2fe-5ada-b22f-894efba2b2a4 | note | Conformance Criteria (What's Required) - Approved by road controlling authority
94747962-35e1-515a-be7a-8347a295b1fc | note | Detail - Traffic Management Plan to be approved Pre-construction
c947ba73-bcd3-5aab-a8cd-6317c994bf53 | note | Frequency - Pre-Construction
e2b32d5b-3996-55f5-b5ae-aa29d98c25b9 | note | Verification Records - TMP on file
2e8d0536-f763-53f0-b3d8-e001d0f062e2 | note | Signatory - Engineers Representative
ee302288-f494-4b99-8810-1718d190271d | signoff | HOLD POINT
9fab30a9-d75c-45de-a78c-7a6d6b6bf4d7 | checkpoint | D1.6 - Heritage Authority induction
dc194489-6b1d-53b3-87c7-c162fc89b387 | note | ACTION (W, M, H) - H
ba20eecf-de03-571d-a833-e292980a9fef | note | Conformance Criteria (What's Required) - Heritage induction to be completed
1cc42cd4-7383-56ae-8d86-0b95bcfddae8 | note | Detail - All personnel who are undertaking work are required to be present at archaeological induction
f2049cdf-69ab-5011-95f4-251bafa8f8b5 | note | Frequency - Pre-Construction
9acc68ab-9dd3-4691-8941-55eced662831 | signoff | HOLD POINT
3c1e2abb-556d-455f-a5c4-48410c19d2b1 | checkpoint | D1.3.3 - Inspection Test plans
9bf5f42d-1613-572c-9ebe-f580523849d3 | note | ACTION (W, M, H) - H
bda7904c-b48f-53e7-b5f6-e85d0833c7eb | note | Conformance Criteria (What's Required) - Approved by the Engineer
e5b08cb2-4a7c-5f9b-8ed6-ae16a0a7db6e | note | Detail - The ITP is a Contractor-generated document that outlines the specific inspection and testing requirements used by the Engineer’s Representative to monitor the Contractor’s quality.
3beefe4e-0fe7-5919-9689-7c0ba8331424 | note | Frequency - Pre-Construction
d53a2726-7339-5b23-a36e-0b6fa1b39896 | note | Verification Records - NTC,Copy on file
bcfeab5a-fda2-5225-90eb-a4638bca13fc | note | Signatory - Engineers Representative
50e037d1-04fb-4cc3-b016-f0b15513c71f | signoff | HOLD POINT
edfa4156-e2c0-43fe-981a-445620d16b1b | checkpoint | D1.11 - Residents notification
4a686137-bc59-5d36-9002-5f75d6125e75 | note | ACTION (W, M, H) - H
c19498e3-6bbf-5f43-b31e-11e71f0024c9 | note | Conformance Criteria (What's Required) - Enginer approved letter distributed 48hrs prior to construction commencing.
a7e6c53c-06dd-5b45-a293-410d012222ee | note | Detail - Residents notifications completed
a937bf51-dc3e-59ae-9ede-313c629f6780 | note | Verification Records - Letter on file
58a91535-566e-5e84-a49d-f37ab7f57696 | note | Signatory - Engineers Representative
a014e588-aae6-4eed-bc6c-5b15de4ff348 | signoff | HOLD POINT
790b3f28-0aaa-4102-9d64-3c0e03b7ef94 | checkpoint | D1.7 - Customer and Stakeholder Communication Management Plan
21467e74-e290-5272-8434-b0c10c7d18d3 | note | ACTION (W, M, H) - H
f19b0883-0664-58d8-9412-b7beea81ef4c | note | Conformance Criteria (What's Required) - Engineer to accept Customer and Stakeholder Communication Management Plan
b5d1fdf8-2bce-5504-9d9c-ddd33ce38084 | note | Inspection / Test Method - Submission
f0240a4c-d0df-5e21-8529-74c5431cda72 | note | Verification Records - Approved CMP
837a4843-4786-5659-b00b-334f440ab18a | note | Signatory - Engineers Representative
b3185a3b-d031-4e87-9c8c-3e4ede48abd2 | signoff | HOLD POINT
9603613c-69e2-4349-aef2-813b581f6ff1 | section | 1.0 Pre-construction - 3.0 Service Location/Potholing
c180d97f-c4fb-420e-84ad-3afe8b20a890 | checkpoint | D1.8 - Service Plans
a00dc771-76a4-5ac2-a7b3-6c800bf86fa3 | note | ACTION (W, M, H) - H
2c143aa4-c3d6-5436-841b-10d468d0c420 | note | Conformance Criteria (What's Required) - All Service Plans onsite and understood by all
3418f7e8-d2d5-5e0f-bc34-62c1eb329a9c | note | Detail - Apply for BeforeUDig, contact anyone not on BeforeUDig
4ece235b-badb-5ac5-8c88-ac08f34baec8 | note | Frequency - Pre-Construction
d0857f05-993f-52be-8424-46a284aed535 | note | Inspection / Test Method - Witness
09a11545-99ea-56fa-ad1a-8e47c2157c84 | note | Verification Records - Plans Onsite & Signed ITP
05e36ab0-fcf8-5fea-ac92-6392137ed917 | note | Signatory - Site Engineer
889bf1e5-331a-47f2-9d14-040ec8e0c0a2 | checkpoint | D1.8 - Service Location Investigation Completed
941ec3ab-d82f-54ca-be84-9a2bbba0c6e2 | note | ACTION (W, M, H) - H
15453ec3-462b-5027-a30b-59c40efe45a4 | note | Conformance Criteria (What's Required) - Complete the service locate with the authorised people
18f9a8ca-096e-5882-80ab-73c7c10c6671 | note | Detail - Inform Engineer about any significant clash
3ce1cf73-3bdc-5e7d-849f-b1bc9f77f227 | note | Frequency - Pre-Construction
94b92b6a-3f8b-5f6b-bb81-5affb3b6094c | note | Inspection / Test Method - Witness
efd6a8dd-778d-5313-9b9f-1451c0b2c553 | note | Verification Records - Plans Onsite & Signed ITP
df02e66c-b5ac-5130-9527-3f702c7a33bd | note | Signatory - Engineers Representative
0f1e5de1-e24e-4e7c-b961-00cfeaa5c702 | section | 2.0 Pre Commencement checks - 4.0 Material checks
98eee9d0-dd69-4313-9873-422b1e541004 | checkpoint | D1.29.3 - AP 65 Tests
bcb15a62-9170-5e46-b81a-98efea7070c6 | note | ACTION (W, M, H) - H
46ea7907-e4df-5e10-99f0-8ff7cd8d7547 | note | Conformance Criteria (What's Required) - In accordance with NZS 4407
3488745d-96c3-5cde-a057-6c3fefa7c4e1 | note | Detail - AP65 Subbase particle size and sand equivalent
5efa9f72-ba94-5eb6-b255-c0265cb2bcb1 | note | Frequency - one initially
f613c3e6-8e92-50ae-98c6-a9a027441e63 | note | Inspection / Test Method - Testing
da57d897-f65e-5603-8bfb-f82aae0fdda8 | note | Verification Records - Test result
ed0ee82b-b6d5-5e2b-97fe-b3379f9241e0 | note | Standard - NZS 4407:1991
0807f1d8-b302-5e46-bb8b-c84b7e9fb7d6 | note | Signatory - Engineers Representative
3dd68cbd-796c-4a6c-9773-2855d4de263d | signoff | HOLD POINT
b2e1efe2-6c7b-49dc-b380-5ed3cd4bf373 | checkpoint | D1.29.3 - AP 65 Tests
3cc9fccb-90db-591c-b939-f06e64877b69 | note | ACTION (W, M, H) - H
ed91c4ed-533d-5176-b91e-8812b4dbe8be | note | Conformance Criteria (What's Required) - In accordance with NZS 4407
dcf835fb-d793-5cbc-a681-7629d9bfc628 | note | Detail - AP65 Subbase MDD
1721519c-9170-59ea-8f3a-f468b8b787f0 | note | Frequency - one initially
6bed927b-71d9-5abb-a9b2-61a0c56c470d | note | Inspection / Test Method - Testing
ba7c5396-c0f4-5c20-ae93-1459fe23d5fe | note | Verification Records - Test result
02945798-f34b-5a9f-a9c0-7ed7a1fb2a77 | note | Standard - NZS 4407:1991
70b3a713-3959-58f0-ac48-d26bde5ed196 | note | Signatory - Engineers Representative
49ecdbce-e33c-41f2-b801-5e763b1e1599 | signoff | HOLD POINT
e71b8f0e-1e86-40c0-9f51-d024a03dfdd9 | checkpoint | D1.29.4 - AP 40 Tests
37afcaa8-dbff-58be-802c-4129120bfeef | note | ACTION (W, M, H) - H
a2bd06c0-56ea-58ff-968d-eaa05516ac15 | note | Conformance Criteria (What's Required) - In accordance with NZS 4407
521c092a-75c8-5959-9f72-56e68d76395c | note | Detail - AP40 Basecourse particle size and sand equivalent
666d96aa-bb18-5e37-96cf-00d37a76a0c8 | note | Frequency - one initially
616509ec-965d-590d-b8d6-c5e5dc7cd684 | note | Inspection / Test Method - Testing
44e103c8-8655-58f0-a759-cbb2d5053b66 | note | Verification Records - Test result
6423535a-cebd-58d3-8a50-6c0fe6374671 | note | Standard - NZS 4407:1991
98d297d3-c537-57ca-9b84-51f451aa9ddd | note | Signatory - Engineers Representative
5a1072bc-9d5e-4637-9f51-a7bd63ab0972 | signoff | HOLD POINT
2b956819-ded8-4a1a-a58d-6e9a25ee53d0 | checkpoint | D1.29.4 - AP 40 Tests
252db08b-8bc1-557d-a98d-b8f112fa9f73 | note | ACTION (W, M, H) - H
d0ac7dcd-e36e-555d-80c0-881151df155c | note | Conformance Criteria (What's Required) - In accordance with NZS 4407
0031c27b-9239-55c0-bf39-16e1155f3c29 | note | Detail - AP40 Basecourse MDD
3dbb4b4f-4aca-5fdd-967c-47b87838f776 | note | Frequency - one initially
0b93e649-9d64-584a-bad7-1d373b785d5a | note | Inspection / Test Method - Testing
0ddabf6e-6c54-5ea7-94d4-396e720979a3 | note | Verification Records - Test result
6493d880-da0e-5570-a028-98e413a17e63 | note | Standard - NZS 4407:1991
c4fd2a69-c5f4-541c-b726-a8a19db2a0f0 | note | Signatory - Engineers Representative
5f3575d6-fe61-404e-ad55-cc7e384acf4d | signoff | HOLD POINT
60d9a802-8c9e-45bf-a298-2865c78e8e7f | checkpoint | D2.5.3 - Butt Weld joint
730b27a8-94f3-5340-849a-5ef70f0d90b8 | note | ACTION (W, M, H) - H
f19d2af6-282c-59d9-aa60-49ba34e82ec6 | note | Conformance Criteria (What's Required) - Butt weld samples to be tested by independant laboratory
9b2c5066-555a-592d-9bbc-e3bcfccc2082 | note | Detail - Should meet the requiremnts of AS/NZS 2033, the PIPA guidelines and the manufacturer's specifications.
c78ba348-5b00-515f-a251-3311d64a1005 | note | Frequency - 1 test weld from first 100m and 1 from last 100m and 1 weld test for every 50 weld
dbda0ef9-71d3-5e77-bf16-9e35054939df | note | Inspection / Test Method - Testing
adfbafca-bbe9-5146-9ffe-e333eacc10ce | note | Verification Records - Test result
b0689471-cd40-5034-8bb2-a826c88f2b11 | note | Signatory - Engineers Representative
0fce90fc-f4bb-463b-8b63-65e4d6b98929 | signoff | HOLD POINT
a2c28f51-164c-4ca9-9552-b222df86d413 | checklist | ITP - Salford, Moana, Wilton, Waihopai Streets - 3.0 Salford Street - Layard Street to Cruickshank Crescent (DN180mm) | itp | 3.0 Salford Street - Layard Street to Cruickshank Crescent (DN180mm)
4ce413bf-a275-4014-99d0-f4f6964d6e51 | section | 3.0 Salford Street - Layard Street to Cruickshank Crescent (DN180mm)
cba08ee1-420f-4d27-b553-5c2f333021c3 | checkpoint | Link in at intersection of Layard Street and Salford Street (1)
feb30032-7075-5548-86e5-53ef41b77663 | note | ACTION (W, M, H) - W
4aa4a3bb-84a2-5f1d-a4e9-d0877527dffe | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
d38f6e8d-d18d-5cbd-bfbd-9d9c002e3f42 | note | Detail - PE to DI connection to be done as per the detail A in sheet 15 of the drawing
7cbcc52f-4ba7-5cf5-8b0d-2e258e825d17 | note | Frequency - Before backfilling
7571b21b-51c2-5933-820c-9434d19d6690 | note | Inspection / Test Method - Inspection
47f43204-424e-530e-af6a-e66838cfed85 | note | Verification Records - Photos
07f07753-6dd7-541b-ac0a-133cbdc85110 | note | Signatory - Site Engineer
4cfc2f64-c078-4431-8c3f-57f5776c9cde | checkpoint | Link in at intersection of Layard Street and Salford Street (2)
ecf89807-dd40-57b0-8edc-b60fcb06db4d | note | ACTION (W, M, H) - W
1e5c0de4-0db7-5809-9af6-1e355769c0ad | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x6)
a4bc0c32-024f-59f8-a2e9-df8e1fdf8179 | note | Detail - As per detail A in sheet 15 and typical details as per sheet 18
1309bed6-197d-59b8-a77e-e9b9a9100ae7 | note | Frequency - Before backfilling
a1cfb308-385d-59f1-8109-584046f32d88 | note | Inspection / Test Method - Inspection
1db0d35d-4fa8-5deb-bc5a-8d981a428751 | note | Verification Records - Photos
e737a2ee-16d6-5225-af86-8b685f2e7ba5 | note | Signatory - Site Engineer
2ba9bdd8-1178-4697-8f35-eda440ac7ae2 | checkpoint | D5.4.2 - Isolation Valve SALFORD LAYARD VALVE CH16 (1)
974babd4-8dfc-53be-8960-9c401cfb473c | note | ACTION (W, M, H) - W
ffb41c6f-c9bc-5ae1-a898-2ec85a1149ac | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
143e50ac-2573-57eb-8fcc-a21df03221d6 | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
483a3b27-2871-5d84-bbc4-27db48174f5e | note | Frequency - Per each valve
6bfe0df4-202f-52cc-bbcb-cf37a8b4b047 | note | Inspection / Test Method - Inspection
5744f60e-5bdc-5024-8098-512357bdeaec | note | Verification Records - Photos
6cf20b08-ab43-5b10-b4c5-a49109ea45a2 | note | Signatory - Site Engineer
d30301ae-60b2-4b5f-8979-db3dcbbce77f | checkpoint | D5.4.2 - Isolation Valve SALFORD LAYARD VALVE CH16 (2)
f412e523-f2de-5e42-a3ce-a3985bd18d9f | note | ACTION (W, M, H) - W
ccf4fec9-7a8f-56ae-8132-6fcf039bb0bc | note | Conformance Criteria (What's Required) - Thrust wall installed
e741e9e3-7d77-5690-8700-d7437bab245f | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
75bbcf5b-46c8-5515-a428-6b808d0d99a7 | note | Frequency - Per each valve
9b7cb01b-4db4-5f1e-9f6c-a9ba8c939069 | note | Inspection / Test Method - Inspection
2c12dfd9-d311-5658-bf99-f21526b1cee4 | note | Verification Records - Photos
44b83072-9163-5fe4-bba4-753218ace188 | note | Signatory - Site Engineer
1ed96aa8-3178-4c64-aafa-350803d84f69 | checkpoint | D5.4.2 - Isolation Valve SALFORD LAYARD VALVE CH16 (3)
65374043-83a4-5636-af68-63eda82b9635 | note | ACTION (W, M, H) - W
8929fed3-6376-506e-97d4-43c18a19b7e1 | note | Conformance Criteria (What's Required) - Surface box finish
7cc9a1ca-ce79-5056-a664-a11c82660f90 | note | Detail - cast iron valve box to be flush with the finished surface level.
f410f6d3-b66d-5263-8a2b-f5a2a4f59752 | note | Frequency - Per each valve
22ae1c62-b658-5f90-bfc0-53c7597e491c | note | Inspection / Test Method - Inspection
463fc4a5-4344-546e-95c9-5be8fde554f1 | note | Verification Records - Photos
08237c5c-f0f4-57e2-8ed4-c706e9462559 | note | Signatory - Site Engineer
fa9dd5d4-d568-4acb-88b7-d7a0d876b90c | checkpoint | D8.3, D8.4 - Lateral connection to house no#107 Salford Street
207cc578-328f-5896-bf40-f923f93dc491 | note | ACTION (W, M, H) - W
b3eb86cd-2d54-526d-a535-2a65bdb5127c | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
92c12c11-d24f-59dc-a9c0-946c223a0d26 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
2b32304f-c0aa-51e3-b994-a65cfdfe6418 | note | Frequency - Per each connection
2add3b87-1e0d-50b3-b7e0-b1d7dc027cf5 | note | Inspection / Test Method - Inspection
f81692c5-b6e1-51c9-9981-6f1d9b436d46 | note | Verification Records - Photos
e8c043ac-8daf-515f-ab22-98bf550b85b3 | note | Standard - AS/NZS 4129
6886355d-23ea-5abd-90ab-829b4e7bd693 | note | Signatory - Site Engineer
578f6550-45be-4320-a854-d6ff54aaa07c | checkpoint | D8.3, D8.4 - Lateral connection to house no#108 Salford Street
6b3f795b-0f80-517e-bd4d-82fd36885e32 | note | ACTION (W, M, H) - W
1c83b9a6-cf07-520d-b6c4-ee087a3040e1 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
12442f91-3b3d-5de6-a83e-95c94e40f15b | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
fcb14a60-b5d2-5243-9488-18adcb0b97e1 | note | Frequency - Per each connection
c829b158-eb9b-51c4-b4a7-96de2914d27b | note | Inspection / Test Method - Inspection
90d26d46-c52f-5ccb-b90b-76d68f796eea | note | Verification Records - Photos
a79aa151-bd54-5700-8c1e-45fd737e4cb8 | note | Standard - AS/NZS 4129
2cb95c5d-5045-50bd-aa93-08481e176424 | note | Signatory - Site Engineer
c6842503-270a-4319-8fd2-dfbe8cc25498 | checkpoint | D8.3, D8.4 - Lateral connection to house no#111 Salford Street
e31fc825-35c9-52a7-aff0-a9542f620a28 | note | ACTION (W, M, H) - W
e6a3d74d-180d-5b65-8e78-b278be2890a7 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
888e1a4c-dfcc-56ff-9fa0-c3f34e831d37 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
7047c617-3374-56af-8211-b595b06b51ca | note | Frequency - Per each connection
0eb8a958-36cc-51bf-a2b9-f248adc047ba | note | Inspection / Test Method - Inspection
13c6cd7b-debf-57c2-9832-ec41f98d041f | note | Verification Records - Photos
4bc2d448-a379-5483-b311-1a3d3527dfe2 | note | Standard - AS/NZS 4129
b1bdb73c-cb2b-5dd9-8bdc-66384b96c74f | note | Signatory - Site Engineer
1981ede2-1663-435a-ae05-dff8b91a6e45 | checkpoint | D8.3, D8.4 - Lateral connection to house no#112 Salford Street
d97b3c80-851d-5bb0-bdcf-0d262ac5240c | note | ACTION (W, M, H) - W
5a9a6ddd-e60c-5bbf-83f9-04922e118c2c | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
9f532427-93a6-5dee-94c5-cc3ae1650a1a | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
a5c55f85-3e08-5e7f-bb60-05147e1369e9 | note | Frequency - Per each connection
a1a66756-5ec9-5401-8acb-cf66df4a8798 | note | Inspection / Test Method - Inspection
f89845d7-6f86-54db-a278-0c5208084957 | note | Verification Records - Photos
f41b6605-9025-5ed7-916f-e843c2da385a | note | Standard - AS/NZS 4129
b51fbbae-c090-52ac-be07-b03769675220 | note | Signatory - Site Engineer
25000369-7988-46e1-ab7c-5b493f7fe56a | checkpoint | D8.3, D8.4 - Lateral connection to house no#115 Salford Street
348f95df-28f2-506d-8ae7-aad525361905 | note | ACTION (W, M, H) - W
1a2fc1ae-1a4b-5579-a931-cf0b216a2d9d | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
9c7ac6a7-2739-54a4-bce6-2e4a3962d021 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
36ec85d5-ecd2-5c65-a8af-7c1e62ac3ba6 | note | Frequency - Per each connection
4573a498-6e46-5a82-bf38-b2493037fe39 | note | Inspection / Test Method - Inspection
993550fe-ffa8-58e4-bded-9bbf10ef635a | note | Verification Records - Photos
34a6f3bc-70c5-5b05-920b-c06f9269c342 | note | Standard - AS/NZS 4129
bcbaccc6-64a4-58b5-b123-9e3bcd2a9a13 | note | Signatory - Site Engineer
c1bdf2d3-2d62-4194-b4b5-d650d34fe96c | checkpoint | D8.3, D8.4 - Lateral connection to house no#116 Salford Street
c4b8bdcd-a652-5f90-8c52-82d9e4e87d6b | note | ACTION (W, M, H) - W
10093423-69c8-5295-b27d-a024d6716cf1 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
43e6eb72-91da-53fc-bc54-353a77526592 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
8328a395-585a-5c89-b30a-f5d514e064cf | note | Frequency - Per each connection
880e73aa-a94c-5f9d-9ddc-1594e3df5bab | note | Inspection / Test Method - Inspection
78e231c4-3def-5499-a8e3-cf7c572b5529 | note | Verification Records - Photos
595232a7-ea8b-5dae-8d1c-c682ae4c6b2a | note | Standard - AS/NZS 4129
08006507-645c-5e65-84fc-577a0bbd34d6 | note | Signatory - Site Engineer
8353d003-44a8-423f-a99d-803ab50cef74 | checkpoint | D8.3, D8.4 - Lateral connection to house no#117 Salford Street
eeb77b9a-1ad1-526e-a6d0-709cf4ff99a0 | note | ACTION (W, M, H) - W
5f0c5bb4-c2ea-5cb9-b367-3ded74a227e9 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
e62375ca-ea7b-5c9b-828f-011afb5f7c67 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
f09196da-1375-5001-a1fd-e04ccf4d7090 | note | Frequency - Per each connection
cb385586-5cd5-5eeb-9495-dd74822cfbc4 | note | Inspection / Test Method - Inspection
e8a01eac-c32e-554d-8f68-48b5bfc98e27 | note | Verification Records - Photos
96505fea-b0cc-5792-8cdc-89f3d12e2956 | note | Standard - AS/NZS 4129
dafb4a88-59cf-54d4-8f37-22b12c6a91a8 | note | Signatory - Site Engineer
2975f5c8-1ba6-4bb7-9dda-66844b753856 | checkpoint | D5.5 - Fire Hydrant SALFORDFH1 at CH 90 (1)
84e7b392-7d23-5fd6-8c76-57990c1340da | note | ACTION (W, M, H) - W
a43880ca-bcfd-5247-af4e-3fbadc449c32 | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
6a1c7aaa-82a4-5412-857b-0abc09ad169f | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
5491f381-bdba-5aee-b1e5-34355922aebe | note | Frequency - Per each hydrant
62d95389-216a-5282-ab69-7a7cd81cbd25 | note | Inspection / Test Method - Inspection
6282a1e8-1873-5f8d-a440-46cfe85bf0f4 | note | Verification Records - Photos
0af44f79-7eb3-5a61-83c3-3201094774d2 | note | Standard - NZS 4522
84e5831c-e150-569b-8ef0-40270aac8620 | note | Signatory - Site Engineer
54786f39-5d01-42f7-96e9-0f970b0c3ea8 | checkpoint | D5.5 - Fire Hydrant SALFORDFH1 at CH 90 (2)
2eb20002-7fb4-53d9-9374-015e9dbc17d0 | note | ACTION (W, M, H) - W
b8706651-f94f-59ad-bb09-2da80e204250 | note | Conformance Criteria (What's Required) - Surface box finish
091c8217-d44d-5865-bcb0-9a44a331942a | note | Detail - cast iron valve box to be flush with the finished surface level.
b417e5eb-6cca-5574-8848-3f30e6e0a91b | note | Frequency - Per each hydrant
aa63e525-94c5-5551-b063-f2a97dd69c12 | note | Inspection / Test Method - Inspection
fd5c6ac7-b241-5f81-adcb-7cec844b1696 | note | Verification Records - Photos
00a70285-757f-5ac3-8bb4-abbf7fa4673a | note | Standard - NZS 4522
e54ef246-2bc1-5e0f-849f-8f4e4050a1c4 | note | Signatory - Site Engineer
8ddb1bdd-2550-4812-9689-7238269e2316 | checkpoint | D5.5 - Fire Hydrant SALFORDFH1 at CH 90 (3)
65ae1ee9-b640-5662-a009-6f396b7bc923 | note | ACTION (W, M, H) - W
1f9c76bb-09e3-539b-ac20-c3bae26bb962 | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
3054dff2-2af0-5491-bd80-ad64e11d8ad6 | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
f9229906-a59d-5147-9048-f43fba76d25f | note | Frequency - Per each hydrant
1c7400b8-df09-547d-b297-fcecb9f91ff3 | note | Inspection / Test Method - Inspection
49b88a68-a0e5-56a5-af8d-f363fc27b71a | note | Verification Records - Photos
f8d3a1f5-6576-559b-9d35-28b98a45eb0a | note | Standard - NZS 4522
c9d09041-80a2-5551-bb5f-83d39a8e7680 | note | Signatory - Site Engineer
558955ae-1cb2-431f-b54d-3734e00d948a | checkpoint | D8.3, D8.4 - Lateral connection to house no#121 Salford Street
06464e02-4171-5fdd-9e79-5761f669ca39 | note | ACTION (W, M, H) - W
21942041-b254-5c03-adbd-119cc65063b8 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
f7a7194c-e1c3-5563-82ed-2a4ace3e7946 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
c8ff2f62-99ad-50c2-a9f3-8835a64eeef6 | note | Frequency - Per each connection
0ade0626-08d6-5525-bb32-9d07b8381761 | note | Inspection / Test Method - Inspection
d37e6f28-f4df-59ea-9cc0-d6265172cc9f | note | Verification Records - Photos
eb9ae092-7b54-504f-8823-d95a1ee7c559 | note | Standard - AS/NZS 4129
e76487ff-263c-5d68-8032-6da04abc25ab | note | Signatory - Site Engineer
9aa3d594-d683-40a6-bb7e-795df206f3d3 | checkpoint | D8.3, D8.4 - Lateral connection to house no#125 Salford Street
35e78d1f-0ccc-5441-84c6-afc188e544f8 | note | ACTION (W, M, H) - W
c150049e-be99-59f0-93d1-00522ba1e3c7 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
acdb879a-78a6-5a72-ad32-15354261a5d2 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
bf1bc37c-62ca-588a-a064-e1fc532e126c | note | Frequency - Per each connection
b4509a59-979c-5749-b488-4ba42ebb001c | note | Inspection / Test Method - Inspection
71f0b911-faa2-58ec-9ae9-ee9ef8be0a90 | note | Verification Records - Photos
1e28f205-732b-56c8-b5f0-c537a31c8882 | note | Standard - AS/NZS 4129
4c873253-02ec-5d8c-93d2-188dac89bd44 | note | Signatory - Site Engineer
dc8dafb4-e7d6-407e-8fd7-696d0f0e1872 | checkpoint | Link in at intersection of High Street and Salford Street (1)
c5f10866-c395-588c-bda0-25da38f33df7 | note | ACTION (W, M, H) - W
58658315-cfff-5dbb-adc7-e1b30ebcfc55 | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
349f8e94-4050-5b45-b91f-81f1b7d3e4b9 | note | Detail - PE to DI connection to be done as per the detail B in sheet 16 of the drawing
219a7e4b-fc89-57cb-a773-5b53160ca253 | note | Frequency - Before backfilling
509cda99-d956-5b59-b346-99a1158b53f2 | note | Inspection / Test Method - Inspection
5e365fc7-a813-5fc5-84c6-54d3e5222039 | note | Verification Records - Photos
0363ce90-9eca-53a5-856e-682d086527cb | note | Signatory - Site Engineer
21b21404-4cf7-4ac0-abd7-ce3736a0bb9b | checkpoint | Link in at intersection of High Street and Salford Street (2)
6fe42b18-fc6a-56d7-8e7d-865ddfe06bce | note | ACTION (W, M, H) - W
38074ffc-aea2-5204-bbec-a3dcc82b1de5 | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
8faba3b6-29c6-552b-a50c-02fc79910ed5 | note | Detail - As per detail B in sheet 16 and typical details as per sheet 18
f024aba6-387e-5d5e-ac7a-89b2d883ff6d | note | Frequency - Before backfilling
b21748a9-17fc-5b60-84b6-564fe74c205e | note | Inspection / Test Method - Inspection
953587af-0cdc-5829-a569-aef0c2f97fab | note | Verification Records - Photos
eeb821f1-a2cf-5e92-a0f1-bde3687554ea | note | Signatory - Site Engineer
5d8a8b4e-87aa-4470-89e8-29720d6a9d05 | checkpoint | D5.4.2 - Isolation Valve SALFORD HIGH VALVE CH127 (1)
15088fa8-3a4f-550c-901d-60c5d43e3270 | note | ACTION (W, M, H) - W
3b9192d1-690f-5ff4-a4dd-e7f5f2d5752c | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
4b4bc3fa-66e4-5455-ab5a-e59df8f64765 | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
10609249-a579-5e08-bb7f-fb87ce2db17a | note | Frequency - Per each valve
d89ceed9-7f5b-5df4-a9f3-ba91a3e71352 | note | Inspection / Test Method - Inspection
f2f535d5-f022-594d-806d-ca7662258d6b | note | Verification Records - Photos
8f9bfba8-1d97-5d71-9108-4665cfbc9862 | note | Signatory - Site Engineer
00687f52-ef80-4cc8-b2bf-eaa37e4084ff | checkpoint | D5.4.2 - Isolation Valve SALFORD HIGH VALVE CH127 (2)
a035bf29-281b-5041-93c1-37f00ebacb4b | note | ACTION (W, M, H) - W
7f097bb8-46a8-520a-8392-ab775b549f1e | note | Conformance Criteria (What's Required) - Thrust wall installed
6845f7b3-12b7-53b5-b13e-caf2341c7b1e | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
f5801fcb-0796-5837-89c0-62770386eb47 | note | Frequency - Per each valve
c62fc65a-6807-55b5-9e7d-f03fd7594c53 | note | Inspection / Test Method - Inspection
8607f34f-d680-53a2-acee-2a5acc7d9a5d | note | Verification Records - Photos
9d2a15dc-4648-5699-bef4-d635e8c26295 | note | Signatory - Site Engineer
449db03d-41e2-4339-9145-bfe777539c81 | checkpoint | D5.4.2 - Isolation Valve SALFORD HIGH VALVE CH127 (3)
075cc813-9b54-51c5-849a-f5c4ab58022a | note | ACTION (W, M, H) - W
32ec3289-959e-53f0-b098-c17d010ba821 | note | Conformance Criteria (What's Required) - Surface box finish
149931b4-d549-54d9-b219-c0225b3ba7cc | note | Detail - cast iron valve box to be flush with the finished surface level.
a7a2df1b-7d36-5d46-84b3-5094a36c5e7f | note | Frequency - Per each valve
fd8c0aed-7ac3-5a01-92f8-fe457bd96409 | note | Inspection / Test Method - Inspection
ca0e4e41-1d1e-568b-ba01-ffc4734e1259 | note | Verification Records - Photos
5cd3925c-6436-5675-b120-46bcb99842f6 | note | Signatory - Site Engineer
619bef09-da76-4674-8802-b37847360084 | checkpoint | D8.3, D8.4 - Lateral connection to house no#127 Salford Street
dde89bd0-d079-5281-9580-da1544de2e3d | note | ACTION (W, M, H) - W
02937708-e32b-560e-bf96-9a9c8eb3e272 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
e74957dd-52a9-59ee-8538-107b714f117b | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
13dffcbc-98dc-589e-a855-025851227d4f | note | Frequency - Per each connection
caf8bfb4-f499-581a-bc81-43767ff1ae37 | note | Inspection / Test Method - Inspection
58bb63c8-5e51-5713-bfd0-6274e2cfdf0f | note | Verification Records - Photos
5c158251-fdb1-5d8e-85b6-34160882faa4 | note | Standard - AS/NZS 4129
8270644b-7a69-560e-ad5d-ac3638288b26 | note | Signatory - Site Engineer
105597db-76b3-4c90-97c1-f7558a2fe49a | checkpoint | D8.3, D8.4 - Lateral connection to house no#131 Salford Street
e57aec8a-ee23-517c-833f-155bd44ead78 | note | ACTION (W, M, H) - W
a50b8ea5-f47f-526d-804e-309d306992d2 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
2c2f7329-5f57-5d9a-b6f6-e1c965150b24 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
57b00b01-dd6b-5cca-8b86-361d491f7203 | note | Frequency - Per each connection
aef76aa7-5744-56c6-99df-1ab05a2ea2ca | note | Inspection / Test Method - Inspection
ba35afce-52b4-5cfc-bdfb-4e6db33a7e54 | note | Verification Records - Photos
b9bac3be-e960-5363-afe5-e1e05d0d3945 | note | Standard - AS/NZS 4129
59fce667-cb0d-5bbb-8f12-aeebb247e9c3 | note | Signatory - Site Engineer
7782d7cd-72a9-406b-b388-11ffb925c69a | checkpoint | D8.3, D8.4 - Lateral connection to house no#133 Salford Street
085d744d-fa1a-5ffd-b939-f4c8d6762d32 | note | ACTION (W, M, H) - W
4d27432c-f2b9-5834-9f8b-8fc8dafb5853 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
8484f235-96d4-56c5-a674-5dfa97b439ab | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
2cdfaad1-7899-5b26-bd4a-cebedb37e9bf | note | Frequency - Per each connection
ebd41d1f-7400-55e4-b760-5bd4c971fed0 | note | Inspection / Test Method - Inspection
8734c920-91d5-5cdf-b746-3fa831c10b13 | note | Verification Records - Photos
79d95aef-dfbb-54db-b5c8-0535bd25f566 | note | Standard - AS/NZS 4129
6ff15514-cee9-54aa-bcaf-f36d83af29e0 | note | Signatory - Site Engineer
81d77a4c-355d-4275-ac14-4cfb0ffcc587 | checkpoint | D8.3, D8.4 - Lateral connection to house no#132 Salford Street needs confirmation
b549d286-99c5-57b8-8673-ea95e29528fc | note | ACTION (W, M, H) - H
cdfbd15a-c5bf-5165-81cc-d151c1acaf61 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
0c679907-4281-5749-895f-f52fd69d75ad | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
5a82a690-83d4-5ae7-8585-4ee66c100cc2 | note | Frequency - Per each connection
ec43999b-5259-529b-8270-d33b70af0ec7 | note | Inspection / Test Method - CONFIRMATION REQUIRED
0eafa0dd-7a3e-51fe-a451-92e0a7f46b34 | note | Verification Records - Photos
3ed6b97c-48da-54e7-a4e1-f99de25bfa24 | note | Standard - AS/NZS 4129
208526f1-c7e4-599a-8118-2f2783ed6b39 | note | Signatory - Engineers Representative
4e1735a9-894a-4bd5-95c1-45fadbf00112 | checkpoint | D5.5 - Fire Hydrant SALFORDFH2 at CH 175 (1)
e0af2077-365a-5812-906e-151f2dcf7bed | note | ACTION (W, M, H) - W
2852d91d-3c66-5d60-8941-6f1cbc529caa | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
8ec83934-4446-5677-9e4a-f1ca020972cd | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
e8284fe8-7d96-5b65-806e-aa5bca0960bd | note | Frequency - Per each hydrant
fa0fc4ba-952a-5f1e-9c9f-81ad063790ca | note | Inspection / Test Method - Inspection
364ae8c1-5bd4-5f6b-bb11-0e00a186f8ab | note | Verification Records - Photos
e7237819-a6a3-5dc9-b2d4-26f8a911f6b4 | note | Standard - NZS 4522
3d407f07-283b-56c7-b132-15178b6eed0e | note | Signatory - Site Engineer
5fdc3321-cde3-4026-9151-827f2ed7a98e | checkpoint | D5.5 - Fire Hydrant SALFORDFH2 at CH 175 (2)
dc381b51-6bce-512d-ab9f-2f5e07d39ed4 | note | ACTION (W, M, H) - W
2a21be97-b651-585b-9fca-c54989d28e80 | note | Conformance Criteria (What's Required) - Surface box finish
05bf22c3-0773-5dfc-8bb1-27b331b16998 | note | Detail - cast iron valve box to be flush with the finished surface level.
d7f1a858-4768-5ce6-ad62-3ec031fe4b85 | note | Frequency - Per each hydrant
5c22b556-32e7-52ae-9f63-8c50966b9fc5 | note | Inspection / Test Method - Inspection
8f08b0ba-17f0-5525-ba1e-321bc197b65b | note | Verification Records - Photos
31544e21-ad47-5b1a-899b-3ef4be06a889 | note | Standard - NZS 4522
a5954059-55db-5c2f-9c7e-f84d54c294e8 | note | Signatory - Site Engineer
8d13665a-5294-4553-9fec-bc3ac464d5f6 | checkpoint | D5.5 - Fire Hydrant SALFORDFH2 at CH 175 (3)
b74e8da5-8555-5f51-b75f-ee7936d5d260 | note | ACTION (W, M, H) - W
b195ac6f-828a-516c-a8c5-b412e48c462d | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
f146dab8-79e8-547c-a332-c541883a4006 | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
db71ac4c-4332-5030-83e7-6c60686b73bb | note | Frequency - Per each hydrant
da42419e-121b-5107-9c06-fb3e5862fd38 | note | Inspection / Test Method - Inspection
faa6b5f4-a930-5144-9d2a-9bdb600042d2 | note | Verification Records - Photos
e50206dc-6e8a-54dd-9dec-33f80d9b3b70 | note | Standard - NZS 4522
4f9ba3a8-4305-5a80-bbdb-d63f5936db46 | note | Signatory - Site Engineer
f7315d75-035b-4573-b977-fbcfe9ecb748 | checkpoint | D8.3, D8.4 - Lateral connection to house no#137 Salford Street
b2a53883-3027-5e2a-9d57-e5e55bd417f6 | note | ACTION (W, M, H) - W
e171ecfe-12e3-575a-a8f8-3a961cbe5a9a | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
9b47c29a-1aaa-5b92-a85d-f69d7a51a067 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
901c655d-95a6-5f90-a6e2-c5eb10f27196 | note | Frequency - Per each connection
b12c032a-8f62-582f-a0d2-edf473341909 | note | Inspection / Test Method - Inspection
cb7fcbe7-1c88-53e8-a005-bf920e126a32 | note | Verification Records - Photos
872019ab-9bd2-5b09-b78e-9c74a51de1f8 | note | Standard - AS/NZS 4129
862e982d-cbd4-5f8e-a6db-ec3da2e4d63b | note | Signatory - Site Engineer
24cdaebf-0f51-4deb-8cd7-134bdc3fce2f | checkpoint | D8.3, D8.4 - Lateral connection to house no#141 Salford Street
447f2046-e5d1-5e9d-9e1a-72069a1caaae | note | ACTION (W, M, H) - W
871a115e-3a6e-5dd3-bce9-9add24d96395 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
0f0fc3e2-c900-50ce-ae5f-63a521d0c4b9 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
b6cc2d86-99cc-5121-ad98-c2b6c9bf2642 | note | Frequency - Per each connection
148f450e-428c-59a1-acc4-e2da99a1329a | note | Inspection / Test Method - Inspection
63963da7-0a69-5f3b-b7ad-0d1ba847d762 | note | Verification Records - Photos
596a55ae-1531-5ffc-88a7-2f1707a476d2 | note | Standard - AS/NZS 4129
ed781fd3-1cc7-5244-bcae-1f7322c54f30 | note | Signatory - Site Engineer
8a5c2b70-cbdd-4d87-bc56-97416ddeb813 | checkpoint | D8.3, D8.4 - Lateral connection to house no#143 Salford Street
7cd7e7b8-a854-5282-94ef-509380d7890c | note | ACTION (W, M, H) - W
f9b4a5b2-9231-5dac-bf1c-c0c1e844e107 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
7be00d28-09a6-5436-93e5-7ef99bbbdcfd | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
c8cc62b6-b323-5e75-af97-59b9361f051a | note | Frequency - Per each connection
20f8b594-0c0b-503e-92f1-e3e1e395415a | note | Inspection / Test Method - Inspection
de3b0f77-2f40-5b2b-a944-7207d5d49ab7 | note | Verification Records - Photos
99c2697e-c128-56a0-a691-6a5951b81350 | note | Standard - AS/NZS 4129
fe4faaa4-19a7-56a0-a9b1-fad1612cf2e0 | note | Signatory - Site Engineer
2ccab6c5-0b0b-430e-8453-d220c5333ff9 | checkpoint | Link in at intersection of Terrace Street and Salford Street (1)
f96666d2-1c08-5ef6-bd54-9bff32f329b9 | note | ACTION (W, M, H) - W
467e4afe-4540-5677-83ea-fae3ad6d5e66 | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
a26971c3-2bca-5915-8f2b-ffaf03f885d5 | note | Detail - PE to DI connection to be done as per the detail B in sheet 16 of the drawing
f565c9fb-9f09-5553-9b41-cf0d54c60e53 | note | Frequency - Before backfilling
5b05ba9e-47a0-543a-999f-0d39d1bd70e4 | note | Inspection / Test Method - Inspection
73e849c0-027e-53db-b96b-91442fefa96b | note | Verification Records - Photos
f3a703b6-9e80-5d95-a17d-ab2e6ba9e320 | note | Signatory - Site Engineer
fa08952e-e4ce-42cc-9416-98bbe8d410a1 | checkpoint | Link in at intersection of Terrace Street and Salford Street (2)
d0ae0c75-237c-5ffb-b932-e064719b3051 | note | ACTION (W, M, H) - W
06333c0d-a08c-5a14-913f-667b2ee86a11 | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
72cd6094-3a0c-5c59-9b73-7edfd7501e83 | note | Detail - As per detail B in sheet 16 and typical details as per sheet 18
fcb91e9d-a055-5b63-b06f-a6677b287c0e | note | Frequency - Before backfilling
2a6f9570-8e96-5801-8df2-6adb160b5124 | note | Inspection / Test Method - Inspection
2e0bf0a6-9443-562a-b4a2-833d7180cf6d | note | Verification Records - Photos
73776963-83d6-5399-8cb4-4132fa4cc9ee | note | Signatory - Site Engineer
b209d585-fa2a-41a3-873f-f7c60cf35f1c | checkpoint | D8.3, D8.4 - Lateral connection to house no#147 Salford Street
0e6ecd9f-691f-5146-bcee-1d1b1b78805f | note | ACTION (W, M, H) - W
c9850f6b-674b-57a4-8d33-6a064ea2d4af | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
76d6a833-59da-5b8f-9ea6-f42114cd9588 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
868b2769-57ae-5245-9496-f7416fe5d319 | note | Frequency - Per each connection
5f4eb885-c914-5ac2-ba98-03a7e4558213 | note | Inspection / Test Method - Inspection
3416b09b-4575-5e62-9c61-cf66231b2af9 | note | Verification Records - Photos
9bd878dc-ed4a-581f-9d42-53dbdcc0bdf4 | note | Standard - AS/NZS 4129
0cb95d7d-b85e-5d0a-8587-28fa5cd2ad71 | note | Signatory - Site Engineer
b3f0311f-0c4c-4c10-a946-97a980241732 | checkpoint | D5.4.2 - Isolation Valve SALFORD TERRACE VALVE CH237 (1)
2336b70c-8427-5a0c-8294-9e21bd62cd1e | note | ACTION (W, M, H) - W
52c93326-b433-572b-9df5-6ef3d12bfc9c | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
2500a2b7-2ce2-5abb-9bad-1bcfb1e85443 | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
fa786fdf-5ee6-5d55-80b3-24c9e27de83b | note | Frequency - Per each valve
6d96699c-098e-5b30-8321-b55d73517fbd | note | Inspection / Test Method - Inspection
8fe08f2e-4ecc-57f0-95f5-222bff23d604 | note | Verification Records - Photos
15ac3f15-48f1-5862-86a8-008f7f2f8551 | note | Signatory - Site Engineer
98a7ffb5-c26a-4a1a-a4bc-6e9b23a9ef7e | checkpoint | D5.4.2 - Isolation Valve SALFORD TERRACE VALVE CH237 (2)
d56e9d84-b077-53fe-a18e-75b251e4861f | note | ACTION (W, M, H) - W
6590cf79-0bde-538e-aa0d-e0a926650f97 | note | Conformance Criteria (What's Required) - Thrust wall installed
18729bbe-a3a6-52af-ad9c-7c87058ad505 | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
f69fbfb7-b91b-53bf-a14a-681ff1a655c4 | note | Frequency - Per each valve
7d68b4f0-3c67-522d-b8ff-49ea050b1a2b | note | Inspection / Test Method - Inspection
c19351be-3845-5b00-9e51-b0ce0af3b04d | note | Verification Records - Photos
190fcd36-210a-5246-a31d-b8f3aeed77c6 | note | Signatory - Site Engineer
7f205f36-0880-4a55-ab65-65e1aa45800a | checkpoint | D5.4.2 - Isolation Valve SALFORD TERRACE VALVE CH237 (3)
d90501c6-eb54-59ce-9a22-31a30347dbbe | note | ACTION (W, M, H) - W
da4216ef-41cc-536d-a2fa-bacd85ef94a0 | note | Conformance Criteria (What's Required) - Surface box finish
bba1c7f5-9381-530b-a2f1-56933e5f03e9 | note | Detail - cast iron valve box to be flush with the finished surface level.
c4aeb93d-67ba-5357-bf5f-f202c84cc682 | note | Frequency - Per each valve
1def8bce-0135-5148-98f1-c5ffe86062d9 | note | Inspection / Test Method - Inspection
72a0628d-46c7-5ae8-98c8-f891a03b0619 | note | Verification Records - Photos
3c948ba1-592a-5256-99ff-a7a8e18382b6 | note | Signatory - Site Engineer
df9b84aa-1d70-4124-8743-34d018251590 | checkpoint | D8.3, D8.4 - Lateral connection to house no#151 Salford Street
de8bd63c-fb66-5d58-9561-da282a98c8e5 | note | ACTION (W, M, H) - W
fba99879-f3db-522e-a5e0-706130d21a4e | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
b24afbf8-4960-5943-8d5f-7cd750c19e84 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
b59b7c16-8742-5c74-965f-b5f57efe0d2c | note | Frequency - Per each connection
a1d2107b-107b-5209-b993-2f22cfb6ea1b | note | Inspection / Test Method - Inspection
6e81366f-6653-57bb-9898-439cdf53a970 | note | Verification Records - Photos
b161af22-91d8-5c7d-ab36-180ec8185242 | note | Standard - AS/NZS 4129
33ad325d-a17c-58dd-8c66-29b4849fc794 | note | Signatory - Site Engineer
a3fb0cfc-9dfc-4fd6-824c-a81c3e3bd9d7 | checkpoint | D8.3, D8.4 - Lateral connection to house no#202 Terrace Street
ff5d4558-27b3-568c-be88-3250a8faa471 | note | ACTION (W, M, H) - W
4d37a684-bdce-5abe-a362-fd1c15c20546 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
4b2f157a-8dc8-5313-b4e3-b5bfea1f3ee8 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
1259e1a5-dfbb-53aa-bc60-651c15b6b0e9 | note | Frequency - Per each connection
0ef68e23-9cf2-5581-a409-4803399e37b6 | note | Inspection / Test Method - Inspection
a7ee317c-b885-5a84-8bc7-d08338675a7f | note | Verification Records - Photos
5aecf5f7-fd4b-5788-b7b5-c9cfd0cee117 | note | Standard - AS/NZS 4129
e42f8ec8-3801-5454-9b41-f33b5ec26756 | note | Signatory - Site Engineer
61c4d117-d260-434e-a307-332e6240988b | checkpoint | D8.3, D8.4 - Lateral connection to house on Salford Street needs confirmation between 202 Terrace Street and 154 Salford Steet
d15bf6cc-1e95-56d8-be5e-8471a5ceda9c | note | ACTION (W, M, H) - H
da3788bd-ffd9-5cd8-b83a-1be2bdc62dc1 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
517881b9-d668-5ca5-b2a2-60987b98c858 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
e6e0f42b-0b1c-55ae-8eab-e43e1be174ce | note | Frequency - Per each connection
e08d3560-d761-54ae-82f6-057c0b9a1a1d | note | Inspection / Test Method - CONFIRMATION REQUIRED
47ba4378-a041-51ab-acdb-2e1ac10cc329 | note | Verification Records - Photos
dd368ab4-4417-50dd-a7c1-2444b652d91f | note | Standard - AS/NZS 4129
cf57f40d-1c21-5bb8-9e2d-25ad30cbd447 | note | Signatory - Engineers Representative
708ff15f-2819-4268-8bb3-9a30ab325339 | checkpoint | D8.3, D8.4 - Lateral connection to house no#153 Salford Street
18664af6-2392-5c8a-ada0-dc35890dc4a9 | note | ACTION (W, M, H) - W
0eab5cc3-21b8-513b-81db-68779e66f476 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
7bb46208-7368-5e3e-afd3-7e637639552a | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
6929dee7-057c-5518-b559-4a6abd46ed32 | note | Frequency - Per each connection
77bcb129-2d3b-5ed4-9741-04b5158d9ec9 | note | Inspection / Test Method - Inspection
9bc142fa-098b-579c-9584-f12648d400d6 | note | Verification Records - Photos
cb8a8950-ea8c-5b26-9ed1-27c6c01dfd0a | note | Standard - AS/NZS 4129
c0be50a1-9f2d-5e57-b92b-d1c335ee6e72 | note | Signatory - Site Engineer
e2fc7f50-a8b9-4108-983a-c9aa43d77465 | checkpoint | D8.3, D8.4 - Lateral connection to house no#154 Salford Street
173e2ae2-8633-5629-8d9a-8cb02b426b95 | note | ACTION (W, M, H) - W
a706270e-c81f-5d48-84ea-fe03d8a93550 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
fbbbca6e-1d71-547a-abfb-aee0176457be | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
634fac12-e9c2-5d95-abc3-592f20ff7279 | note | Frequency - Per each connection
5fea3033-632f-53c7-81ab-a45905736cf8 | note | Inspection / Test Method - Inspection
c53eada5-9f36-5d1e-914e-8e21380cdf68 | note | Verification Records - Photos
e1c6b794-8b27-539a-be38-5fd100aeb1fa | note | Standard - AS/NZS 4129
65cf5d63-f713-5c59-b7ba-64aec4829c22 | note | Signatory - Site Engineer
8c9c4366-7563-42b9-9fa8-db6edf78ad54 | checkpoint | D8.3, D8.4 - Lateral connection to house no#157 Salford Street
965c2ba6-76db-5ec4-ba3e-300147dbb294 | note | ACTION (W, M, H) - W
401f8e4d-d52b-588f-aaf8-1cad76087702 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
fd369ab6-688a-57e9-915c-4677dbce9787 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
cca5ae95-c608-5f31-923e-bd97f0a96426 | note | Frequency - Per each connection
41fb43ff-cd41-5add-8fdd-4ef5c736770d | note | Inspection / Test Method - Inspection
98cb833a-5805-56d1-ae29-ba1cd1a29c43 | note | Verification Records - Photos
767da80c-8f28-5562-862f-fbe573a9de82 | note | Standard - AS/NZS 4129
3584400f-5967-5a4f-a7af-80803a63e47a | note | Signatory - Site Engineer
026895cf-cb08-475b-9004-ed37259813ab | checkpoint | D8.3, D8.4 - Lateral connection to house on Salford Street needs confirmation between 154 and 156 Salford Steet
24ea770d-dec1-56a3-a7a4-33e8878490a4 | note | ACTION (W, M, H) - H
a8d6ad8f-05cc-5e47-ae60-02488d2f75f1 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
84589f56-f995-5810-992b-5184143e784a | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
cb52d0b8-27d8-5664-9c6f-a27cdebb3118 | note | Frequency - Per each connection
1aefe251-15d9-5628-bd31-8268751bc736 | note | Inspection / Test Method - CONFIRMATION REQUIRED
c80431c9-885f-52c8-aaa6-30b16c2d9bf4 | note | Verification Records - Photos
5c01b9cb-aa97-5803-b0a6-e3313fdeecb6 | note | Standard - AS/NZS 4129
647202a6-c0e8-5a13-bfe1-189abdd25af6 | note | Signatory - Engineers Representative
39c98129-4e35-4d62-bf14-179af70d3ef5 | checkpoint | D8.3, D8.4 - Lateral connection to house no#156 Salford Street
f6e29bec-2141-5dd6-bb30-fb93438b6b7e | note | ACTION (W, M, H) - W
3380cbf5-f2de-58fc-8abb-a9c4ae14f011 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
c4542120-0aab-5804-a01f-46559c5a624a | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
01a4c68b-8566-549f-8786-653152018f2b | note | Frequency - Per each connection
00b83fbd-5bad-58be-b278-24f53b68280f | note | Inspection / Test Method - Inspection
1d87627f-2688-5131-a7c1-085b93d71855 | note | Verification Records - Photos
29035c30-8088-57d7-b7a5-6325e2eee296 | note | Standard - AS/NZS 4129
9430c7fe-d33b-563f-9c8e-2f0404d96d81 | note | Signatory - Site Engineer
e5bf500e-6fba-4bd3-b147-0a2fad464492 | checkpoint | D5.5 - Fire Hydrant SALFORDFH3 at CH293 (1)
f5915ffa-c7f4-558a-b045-6a5fd7f5d244 | note | ACTION (W, M, H) - W
b0acf1d5-1271-53bb-b8d1-688f43b13437 | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
6934c9f2-3e3b-5e1e-bba1-7df42637f647 | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
63b03163-c623-5226-b675-f245a650424e | note | Frequency - Per each hydrant
a9d2b40e-a63c-518d-bf39-c971fac744ef | note | Inspection / Test Method - Inspection
3a14422f-e869-5365-84ab-3b81361f6abd | note | Verification Records - Photos
296f6e61-49da-5edc-9de7-bea674f48060 | note | Standard - NZS 4522
a5f90e37-cd97-53c9-a10e-1e136fc941ad | note | Signatory - Site Engineer
56a31293-2b38-4226-a5ff-7c5be9bce932 | checkpoint | D5.5 - Fire Hydrant SALFORDFH3 at CH293 (2)
28a02a92-659a-5451-97cd-c45e07ad914f | note | ACTION (W, M, H) - W
d8291b41-8c57-5bfb-9637-e3ae77f868a1 | note | Conformance Criteria (What's Required) - Surface box finish
e3c8556b-9b02-5c2b-95c7-c29b94feddfa | note | Detail - cast iron valve box to be flush with the finished surface level.
d95dcf57-cb4d-526a-a2c1-7291effbc797 | note | Frequency - Per each hydrant
e8dbe459-8e30-5e5f-993a-d07707ace478 | note | Inspection / Test Method - Inspection
041a15bf-2054-5003-b08e-24cb620cfb12 | note | Verification Records - Photos
9a690af6-f7ea-5338-8ee3-85110c9a07e0 | note | Standard - NZS 4522
1ac4bbb9-0ac8-55c3-b772-1e557746731b | note | Signatory - Site Engineer
c3ca69f8-a309-42d1-ba86-6b8910a353bc | checkpoint | D5.5 - Fire Hydrant SALFORDFH3 at CH293 (3)
5fd1ff9e-80c6-56b7-9d2d-65778a3ca9ab | note | ACTION (W, M, H) - W
83d12e43-c7a6-5185-bf80-01422a594f97 | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
d0ca2bc9-9689-544d-9193-c2919449bca5 | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
7abf6e06-b122-5f8b-b006-978e55811b4e | note | Frequency - Per each hydrant
caabb4eb-eeb4-5ce2-a4ba-90ea920ffe76 | note | Inspection / Test Method - Inspection
6a1cf320-40b4-5ab5-a04b-a400f829ad4f | note | Verification Records - Photos
c6aa6148-d31c-5e5c-90b7-1ce0d032705b | note | Standard - NZS 4522
19f2150a-22d5-57ae-b440-bd45732807ad | note | Signatory - Site Engineer
6cf50b12-6b7c-4b3f-9e06-c0b1185ba84a | checkpoint | D8.3, D8.4 - Lateral connection to house no#161 Salford Street
b10ac144-3790-5136-a211-84458acbb814 | note | ACTION (W, M, H) - W
10adf2d1-9a74-5606-b758-e4bf224480e7 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
5022f0e9-264d-53b9-8cf1-b99fe950f814 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
7736b6df-51d7-5c1b-8008-5156e7c47cde | note | Frequency - Per each connection
06df2623-d598-5df8-ac0c-5db011b8af89 | note | Inspection / Test Method - Inspection
bb0f5141-c3ab-539f-b5d2-fb121252bad0 | note | Verification Records - Photos
e0fe8da4-2c0a-5d71-a6bd-bb196efffddb | note | Standard - AS/NZS 4129
dab85d93-e8a1-562a-9f76-de6210739603 | note | Signatory - Site Engineer
3a5ad1a5-bf45-481f-bf74-b57a5480fdb8 | checkpoint | D8.3, D8.4 - Lateral connection to house on Salford Street needs confirmation between 156 and 162 Salford Steet
8cd99db8-44fa-581e-8f8d-c694d00968fc | note | ACTION (W, M, H) - H
2cc25e18-ea63-5469-8457-bbdff25b5727 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
fe0ddc93-5db3-56a7-ba39-29187e5710d3 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
0d0e2e10-9ffa-5ee7-a519-20eea633d79a | note | Frequency - Per each connection
54e7c7a3-25d1-5d5f-a8bb-2d51744244dd | note | Inspection / Test Method - CONFIRMATION REQUIRED
c27430e2-9a44-53b8-bd5a-d56a008c00fb | note | Verification Records - Photos
7b3fbda8-4c88-5aeb-8520-c8ae2091f790 | note | Standard - AS/NZS 4129
fe5f4dcf-5d35-5140-817b-a37d8cc10b67 | note | Signatory - Engineers Representative
d3c3a03b-ff32-47dc-899b-5fb8d9102ae9 | checkpoint | D8.3, D8.4 - Lateral connection to house no#162 Salford Street
6db35a5f-cd11-55e6-8187-ef5c32f14c80 | note | ACTION (W, M, H) - W
bd64c0fb-894c-5101-94ac-decb9457a23a | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
ed9d4b82-da88-5a5c-ab98-1f5a93f13438 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
7c641519-794b-5864-9ac5-7b3b3fb1d3d0 | note | Frequency - Per each connection
026c0a55-6596-57b3-9d1d-e1e9580248fa | note | Inspection / Test Method - Inspection
2189caa1-34b9-5377-8d6d-fd4d34806007 | note | Verification Records - Photos
2c6fc374-0d69-5749-9de3-ba2cd52523ec | note | Standard - AS/NZS 4129
ec985463-b6ff-52b3-87cd-538be05954e0 | note | Signatory - Site Engineer
4b59c46c-2598-4a0d-ab2e-55eb8b13207b | checkpoint | Link in at intersection of Lamond Street East and Salford Street (1)
0fa5582c-b0eb-5397-873a-b5951158d27c | note | ACTION (W, M, H) - W
c6841d53-db3c-5d90-8f51-7ad05f8415e3 | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
56f20692-5e1c-5ca0-b52d-f69f23f68d91 | note | Detail - PE to DI connection to be done as per the detail C in sheet 16 of the drawing
11433881-3e4a-5cfc-b74f-84f4696b31c5 | note | Frequency - Before backfilling
c8d387e0-0840-5d7d-9f0b-50ee2bacc9e2 | note | Inspection / Test Method - Inspection
1ba09648-c9d9-5d6d-8097-7067506662e2 | note | Verification Records - Photos
e511aeca-9bec-549d-9aa4-4de0f450049b | note | Signatory - Site Engineer
bb4dfbed-0592-4162-a986-4eb4552843c6 | checkpoint | Link in at intersection of Lamond Street East and Salford Street (2)
f95d1207-89cd-5aa5-ba09-2b6f6c84ce28 | note | ACTION (W, M, H) - W
79ccc145-2b0f-5fcd-9c78-f6a8d376bf8a | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
5f59a0c0-1513-5962-a72e-ebdb2d6a0035 | note | Detail - As per detail C in sheet 16 and typical details as per sheet 18
0ec173bb-daa5-5cfa-b96a-a78b6d81c958 | note | Frequency - Before backfilling
e65631f6-a4a2-594d-b0d4-ab93b0e1aa49 | note | Inspection / Test Method - Inspection
df0e4cf9-8bc5-5c2f-b615-7732f5238c99 | note | Verification Records - Photos
68ea2409-bdb9-5983-a6ff-27afbbb45cfd | note | Signatory - Site Engineer
2efa5723-2698-4bff-b6c3-48d1cb0e4eee | checkpoint | Link in at intersection of Cruickshank Crescent and Salford Street (1)
9ce2a9fe-33e5-57f8-a2aa-a27440a10538 | note | ACTION (W, M, H) - W
fa5cccb6-1a62-5164-9ba8-1ffb5f72aa4a | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
4b9b5525-4a40-58f8-b0f3-5a71bcba619f | note | Detail - PE to DI connection to be done as per the detail B in sheet 16 of the drawing
89e5e85b-d6f8-57ab-807a-8cf4f24d6333 | note | Frequency - Before backfilling
cdef7596-48c8-5525-a58a-b388d6eb1978 | note | Inspection / Test Method - Inspection
48ac8caa-6c27-5807-9615-e62525d9ca49 | note | Verification Records - Photos
be45e98e-04d1-51d6-b4b3-ec5b8151e559 | note | Signatory - Site Engineer
a7ae5845-7c72-4f7d-9f23-83b423a6279a | checkpoint | Link in at intersection of Cruickshank Crescent and Salford Street (2)
1fd8527f-cccc-5c6c-864b-3806123f7a61 | note | ACTION (W, M, H) - W
951bca02-921d-5a8f-8b04-bd5d08d4c178 | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
3c82607e-44ca-51a5-9cf2-d8f7941dbbea | note | Detail - As per detail B in sheet 16 and typical details as per sheet 18
d07ed5df-488d-530e-8536-d2af8460675f | note | Frequency - Before backfilling
a3389011-1fc3-5de8-a40c-156701d79fed | note | Inspection / Test Method - Inspection
3a43c4f6-c7a5-5511-9545-8f822ff78ec0 | note | Verification Records - Photos
cef13ecc-5a3d-5450-8c89-5d7583304b82 | note | Signatory - Site Engineer
38d21829-71b2-4acd-bd62-14eb8175cc83 | checkpoint | D2.7 - Trenching and excavation
5d5c0512-ae3f-59a1-af8d-546bbdd1ac6d | note | ACTION (W, M, H) - M
2e9d60a7-7079-51f0-bd60-d5ee5886ada7 | note | Conformance Criteria (What's Required) - In accordance with NZS 4407
ad9acdf8-0234-5acc-b161-f81d4b7fe7bd | note | Detail - AP65 Subbase particle size and sand equivalent
64b92842-e262-5ac7-bb8a-d391e93dbac6 | note | Frequency - Daily
219bbd1b-5d93-54ed-b9fc-8264ecbbdf7c | note | Inspection / Test Method - Inspection
a81fdab5-8c5b-52d1-a581-9b66415cd936 | note | Verification Records - RCP and digging checklist
a0d4cb45-d6b5-506c-b04c-6fd301f96cc5 | note | Standard - NZS 4407
8b60cff5-7248-5e13-baf6-6fc9bb70b359 | note | Signatory - Site Engineer
7f8fe9c7-cb28-4f7f-88b4-56704c34f935 | checkpoint | D2.9.1 - Pressure testing & disinfection (1)
e0f05e28-0133-50b0-9972-505b7534557a | note | ACTION (W, M, H) - H
5a0272fa-3e78-59f3-97e3-2b9f073586b0 | note | Conformance Criteria (What's Required) - AS/NZS 2566:2 Section 6.3
fc781ca7-7662-501f-a6fd-0ce25f2c627a | note | Detail - pressure testing of the new PE main
e705b2ea-8702-57ad-8955-e936e13387dc | note | Frequency - Prior to link in
f8c45c10-8d60-56f1-ac7b-cca15fdef9d5 | note | Inspection / Test Method - Testing
790de4f5-db19-5956-bb8d-04feb526d8f8 | note | Verification Records - Test records
861b54d9-717a-5d41-a52b-868cde820266 | note | Standard - AS/NZS 2566:2 Section 6.3
1367a039-f367-57d5-b127-f40f33c95d41 | note | Signatory - Engineers Representative
6426da14-b965-41f2-bb62-10b9e3f7ccc1 | signoff | HOLD POINT
30d8b422-b2ff-4137-a96b-e70dd9d591eb | checkpoint | D2.9.1 - Pressure testing & disinfection (2)
dbde7b7f-2dd3-55ee-8671-905d375d9c84 | note | ACTION (W, M, H) - H
33e05197-552c-5bbe-b616-9971da63cf58 | note | Conformance Criteria (What's Required) - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
9f5f5861-6bb9-5dd7-b30c-a5aa3e193e4b | note | Detail - Disinfection of the new PE main
14b250e9-cad9-53de-b60e-f3bb22aec64a | note | Frequency - Prior to link in
d0140826-611a-54ea-8cd6-bc7ddcfea7e3 | note | Inspection / Test Method - Testing
13216ae6-7b46-5d43-9bdd-31b0597981ac | note | Verification Records - Test records
02396d62-60f2-59a0-808e-b5414d020f5a | note | Standard - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
e7b9cb24-040c-5824-828e-64bdd0e539b8 | note | Signatory - Engineers Representative
9bf0ef78-24c0-4330-a94f-113d69efc617 | signoff | HOLD POINT
83dc8747-2736-4155-a00e-d85abee90e5e | checkpoint | D1.3.3 - Engineer's inspections
b627904b-aa91-5edc-85f0-a6b90663af15 | note | ACTION (W, M, H) - H
c31282d9-89ad-5f76-960f-d98cc32c33b6 | note | Conformance Criteria (What's Required) - Inspection report
e5886c5d-8164-5211-a144-38eedc11f7e3 | note | Detail - Enginer's inspection for pipe, concrete pre pour, pre sealing
09dbb7a0-7b2a-5b95-a4b6-e22fe97e761e | note | Frequency - As required
0362e3d6-f263-5658-9336-6c30c9e8a553 | note | Inspection / Test Method - Inspection
33594358-26fa-5429-8220-6d1d2c247e0b | note | Verification Records - Email
2e2e32d3-9efc-5e45-82d8-b29c404ed039 | note | Signatory - Engineers Representative
15c65148-8448-417f-8eb6-271820806379 | signoff | HOLD POINT
7ffc9f0b-312d-423d-8679-1919b90e9b6a | checkpoint | C1.18 - Surface Reinstatement (1)
4b7fc07a-d159-58ea-84ac-8b19b6eace6f | note | ACTION (W, M, H) - H
68debd19-a924-55cd-9ad3-ba0ddab67cae | note | Conformance Criteria (What's Required) - Engineer's Approval
428d7bf4-2251-5596-8d13-97b94621d459 | note | Detail - Mark out the trench including overcuts
6bce33fc-1021-51ce-9e4c-3b50c1a19ba7 | note | Frequency - Prior to surfacing
4374e1d9-79ef-5d19-9dbb-52b05b428649 | note | Inspection / Test Method - Inspection
367b81ad-a567-53d4-b866-f903c36f49ab | note | Verification Records - Email
39c09700-fd8a-5b7c-b922-7378769cd411 | note | Signatory - Engineers Representative
56ebc2d3-68e6-430e-bb12-eff3b146368b | signoff | HOLD POINT
11ea412e-6817-4cb6-927c-fb7fd81f1a92 | checkpoint | C1.18 - Surface Reinstatement (2)
a9cc9c7f-c881-593a-8861-5e3bee8bb3a6 | note | ACTION (W, M, H) - H
dfcd159c-90ce-5edc-903f-2c168ca1bcd5 | note | Conformance Criteria (What's Required) - NDM testing
179c8367-36a7-5658-bc72-58e54f2727d6 | note | Detail - Provide NDM test results for AP65 and AP40 layers
921c9f56-488e-5178-8166-649310aa49bd | note | Frequency - Prior to surfacing
38aef6e0-df9e-59ed-806b-559e37f82e3f | note | Inspection / Test Method - Testing
4e0745f3-7664-5c3d-8a54-6a9618ade092 | note | Verification Records - Test records
37641fc1-b50b-50a5-ba9d-caf6161dfc98 | note | Signatory - Engineers Representative
5dea9f5c-22f7-42f4-8763-0545ca2fa636 | signoff | HOLD POINT
54b36b5b-3ae1-43ae-95c4-c344fe4e6aec | checklist | ITP - Salford, Moana, Wilton, Waihopai Streets - 4.0 Salford Street and Moana Street - Cruickshank Crescent to Wilton Street (DN180mm) | itp | 4.0 Salford Street and Moana Street - Cruickshank Crescent to Wilton Street (DN180mm)
8b709852-332d-48cc-8b9c-e6e5c0fe881a | section | 4.0 Salford Street and Moana Street - Cruickshank Crescent to Wilton Street (DN180mm)
4d549b46-22db-4920-a986-d4e4fa52bf2c | checkpoint | D5.4.2 - Isolation Valve CRUICKSHANK VALVE CH358 (1)
c2129be0-da02-5ec4-957b-74e6c91f854a | note | ACTION (W, M, H) - W
a084874e-9f4e-56c1-9076-2ba72d0b04a5 | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
f6a84916-ca8f-59ae-966c-7cfdb223e045 | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
449bab27-7cc0-5f2f-a289-19580400bd96 | note | Frequency - Per each valve
6a58d68b-68ea-5403-a47d-e0f3526c330c | note | Inspection / Test Method - Inspection
06bc337a-ae4c-51d5-8d73-0253c0b3747d | note | Verification Records - Photos
360f4cfe-7cbc-503b-bcd6-37302ff48c67 | note | Signatory - Site Engineer
de18cef2-2814-4a02-a65a-358a147623c0 | checkpoint | D5.4.2 - Isolation Valve CRUICKSHANK VALVE CH358 (2)
9118b5c4-c6cc-591f-a254-d66e7bbc6c3d | note | ACTION (W, M, H) - W
75feac04-f1ad-5a7a-814d-ba751c29375d | note | Conformance Criteria (What's Required) - Thrust wall installed
d955a0e5-f665-5abc-9ce8-0b7d04d34c5a | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
01c666c8-2e26-5c88-8c81-c8bcb269c924 | note | Frequency - Per each valve
4addec91-715d-5660-8149-d925143aefd1 | note | Inspection / Test Method - Inspection
a9c34084-5b00-5c0e-b050-c2083d74ad2a | note | Verification Records - Photos
2271f1a5-eca4-5cf1-bb21-8ce89e97a46e | note | Signatory - Site Engineer
7da32b55-e5c1-4992-904b-94866ecb3e55 | checkpoint | D5.4.2 - Isolation Valve CRUICKSHANK VALVE CH358 (3)
6a4c6786-5ed0-53ca-b692-e50717270eec | note | ACTION (W, M, H) - W
f436f9fd-35a9-54c3-9f5d-094fda0f2ebd | note | Conformance Criteria (What's Required) - Surface box finish
2f1a40e1-d3d2-53d4-adff-991538faaf01 | note | Detail - cast iron valve box to be flush with the finished surface level.
4096fe48-3032-5387-b2fe-6644ffb81aac | note | Frequency - Per each valve
609346cf-cfe5-550d-be8a-5b725e0ff604 | note | Inspection / Test Method - Inspection
7a5ad1d3-df83-5f68-87ed-558f2aba6578 | note | Verification Records - Photos
d3932092-a6f6-55b4-81d5-4e0072a9596e | note | Signatory - Site Engineer
3f6d2d79-9e20-444e-ae24-66197aa3e307 | checkpoint | D8.3, D8.4 - Lateral connection to house no#178 Salford Street
ad8134eb-1d53-5813-b3d3-a37b26c44d81 | note | ACTION (W, M, H) - W
2fc1d783-4773-589c-8090-fc5262c52290 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
c7dd6742-9723-53bc-9709-09d6ff7ae956 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
f91830bf-b4eb-5906-b338-c037e7795183 | note | Frequency - Per each connection
71614183-6a6b-5ad5-b9f4-b3c662f70cd5 | note | Inspection / Test Method - Inspection
e9067490-ed0c-5c53-a55e-3a33a5a675cf | note | Verification Records - Photos
00ded495-7b6c-5a5b-87e4-b2c7fe04a332 | note | Standard - AS/NZS 4129
5c95eb04-2bd9-58c2-a329-9898ed2a5307 | note | Signatory - Site Engineer
cd2d2e6a-7e45-42ce-a223-9e5df6fce5a7 | checkpoint | D5.5 - Fire Hydrant SALFORDFH4 at CH397 (1)
342d23ed-5e07-5f5c-b142-87ce946280be | note | ACTION (W, M, H) - W
43f90ffe-e403-510b-ae16-473bf9c75b2c | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
34ed1259-52b0-5cf6-943f-4d3ced589255 | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
a68da078-5202-5fb8-868e-bb4ed2d246a7 | note | Frequency - Per each hydrant
f389411b-3cc0-566a-8d53-8301f2699f06 | note | Inspection / Test Method - Inspection
d6dec95f-7f6a-5580-bd75-5856838555a1 | note | Verification Records - Photos
cf64aef7-62c1-5e65-bc80-b3fe21adf0da | note | Standard - NZS 4522
d3d18d7a-fd33-5130-ad0f-68e85352438d | note | Signatory - Site Engineer
f865fc06-6837-4e0f-b1dc-1a156a81862b | checkpoint | D5.5 - Fire Hydrant SALFORDFH4 at CH397 (2)
9743fabd-7d20-5b9a-8b7b-f1a93db21f1b | note | ACTION (W, M, H) - W
385bbe87-1e57-568a-b1a5-1e373cc2b3a6 | note | Conformance Criteria (What's Required) - Surface box finish
7f6c4c45-a9f7-5f07-a837-e619d5b922c8 | note | Detail - cast iron valve box to be flush with the finished surface level.
b144f6b1-eae2-5740-af05-0589fb2ed750 | note | Frequency - Per each hydrant
50e8ede4-77e2-5d64-bbf6-ac2903740e87 | note | Inspection / Test Method - Inspection
62e7a611-0bdd-51a8-8f1f-acb1b5eca638 | note | Verification Records - Photos
f04ca9d1-f005-595b-adfd-d730482808d0 | note | Standard - NZS 4522
c6296662-e039-55b9-8ba8-89332966e387 | note | Signatory - Site Engineer
ea9389c1-68fe-4932-99ad-6964e5e038c2 | checkpoint | D5.5 - Fire Hydrant SALFORDFH4 at CH397 (3)
1823fd17-ff6e-5c13-a865-186a695e162a | note | ACTION (W, M, H) - W
61fcae03-ad8d-55f6-bfc9-8c96957b1d87 | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
324bdb41-9247-5360-9d2a-5efdeba6d414 | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
5968c7d0-7d6f-50b5-9b44-f4b4fd1af148 | note | Frequency - Per each hydrant
cb626d5e-761d-54d5-8ae5-1731f578920f | note | Inspection / Test Method - Inspection
67b319fb-a229-554e-b6b1-c1502e4ade61 | note | Verification Records - Photos
0e76a5cf-e4d7-58f3-8d54-a6694eff097a | note | Standard - NZS 4522
c3116a69-8160-5f7c-b17e-2928f7773872 | note | Signatory - Site Engineer
5ace445c-6508-43d6-a83b-02482f1c00c5 | checkpoint | D8.3, D8.4 - Lateral connection to house no#182 Salford Street
991126d6-86a1-5c87-a4a6-de60561c0b1f | note | ACTION (W, M, H) - W
6f962fce-8927-5ecd-b020-297aa73eb032 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
833b57aa-88e5-55d0-b248-5fa69ef399df | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
8b6c9c53-d0f7-5b8e-a9f4-01a0e87a7721 | note | Frequency - Per each connection
27c9585e-40c5-508b-b1f7-3bec77976c41 | note | Inspection / Test Method - Inspection
a6820bbd-ddcc-58c6-94b7-e7351a6a43fb | note | Verification Records - Photos
87e48743-c253-59c5-8d6a-e523bf9fc7fe | note | Standard - AS/NZS 4129
f98912d5-09a6-505d-b914-c964041c7fae | note | Signatory - Site Engineer
fe432d67-33ee-4fdc-bed9-7a56caf9bc60 | checkpoint | D8.3, D8.4 - Lateral connection to house no#192 Moana Street
f9eb26a8-6da0-5b9a-9991-bccc6d775fdf | note | ACTION (W, M, H) - W
f089b511-a190-507f-95c4-d384dbbf84a5 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
d7913fbb-cb74-5970-9d8e-b103dd39836e | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
78666de0-6a04-59fc-b3d2-a8502ce9d18b | note | Frequency - Per each connection
b9b96de1-0a59-57a3-bfd8-18b8c883399d | note | Inspection / Test Method - Inspection
ee67fd4a-d369-5573-93b3-4f00041112c0 | note | Verification Records - Photos
88e78f83-3080-5000-8b32-6b74ef0e00b2 | note | Standard - AS/NZS 4129
472a2fc3-983c-5b6a-b53e-4562f6b2a4e8 | note | Signatory - Site Engineer
0866bf44-41c2-45d1-ba76-d57b11118e14 | checkpoint | D8.3, D8.4 - Lateral connection to house no#188 Moana Street
6c7af68c-e3ac-5255-885d-62376b32d976 | note | ACTION (W, M, H) - W
b6901cba-5cea-525c-af62-cf9584b624e8 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
d0f83374-a5d0-539a-9134-dcc1bf51d36b | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
69745200-3bc2-57a2-ae1b-078479493b17 | note | Frequency - Per each connection
18d86c8c-1bba-5a61-ae9d-241f63aec00b | note | Inspection / Test Method - Inspection
6883d72e-49d2-5b8e-a1ac-a45d34d01f66 | note | Verification Records - Photos
25773592-a650-5aa0-ba97-bb0c61b1df7d | note | Standard - AS/NZS 4129
a5abbb0e-37c7-57be-bd6a-c1b913357319 | note | Signatory - Site Engineer
bd147599-83f5-4d6d-93db-bd0fe2a0758f | checkpoint | D8.3, D8.4 - Lateral connection to house no#8 Sommerset Lane
c00893bc-3aa5-5d9c-9185-0cc5364af522 | note | ACTION (W, M, H) - W
a3cec68f-b440-5337-b6ff-c51b49513908 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
63f287ef-afd1-5673-92d9-10a5338dfc5e | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
a2967ffa-dc2c-5fe6-b60f-e235191c4361 | note | Frequency - Per each connection
5dcad7eb-5c6e-53f2-a28c-05d85f4684bb | note | Inspection / Test Method - Inspection
43daccbc-f559-5302-af58-7149651446d0 | note | Verification Records - Photos
c35f9d5b-a58b-5809-a304-339471776bed | note | Standard - AS/NZS 4129
b4c838d2-482b-5f59-8517-42238b10a3f5 | note | Signatory - Site Engineer
775d2b40-f5be-4c5a-a1d6-7074e4386ad0 | checkpoint | D8.3, D8.4 - Lateral connection to house no#185 Moana Street
3bc3814c-0d4c-5606-a7f1-a7e262cc8aeb | note | ACTION (W, M, H) - W
39980e42-0109-5b7d-bd4c-0e39fe249f6e | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
7bb88f38-72e6-5a87-a83c-12664913e5a3 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
4338ea3f-0a79-5a7b-8c25-93bc70f69507 | note | Frequency - Per each connection
9c286c4e-c1fe-5c9c-a3a6-240f3e6cd847 | note | Inspection / Test Method - Inspection
047966d4-8a9c-598b-87aa-4f99d84f4bf7 | note | Verification Records - Photos
d11c052a-f0df-5b8e-844e-40c06718aa43 | note | Standard - AS/NZS 4129
2749bdc5-c683-57e4-a530-e126d40eb5d4 | note | Signatory - Site Engineer
4f0bb64c-b098-4f43-94fd-6bbfb665b3ed | checkpoint | D8.3, D8.4 - Lateral connection to house on Sommerset Lane needs confirmation at #8
23c84bba-7010-513a-b0bd-200e08922577 | note | ACTION (W, M, H) - H
2267a39e-607a-50da-bdfd-5dbc704a7670 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
edd16ed9-6d11-511b-956e-d515436616fc | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
6717901c-dfb9-563a-b198-3b96762bf4fb | note | Frequency - Per each connection
5c9dcaf5-229c-5a0f-ad9d-8075491c5059 | note | Inspection / Test Method - CONFIRMATION REQUIRED
3c413f08-cf5a-59fd-8a4d-cb4323288251 | note | Verification Records - Photos
4ac1fbb2-23df-523b-a344-746d129b8886 | note | Standard - AS/NZS 4129
728af240-e319-5b53-ad7e-dc220ecfbbb8 | note | Signatory - Engineers Representative
b3ed56f4-beba-484f-860a-f39bfc962e09 | checkpoint | D8.3, D8.4 - Lateral connection to house no#1 Sommerset Lane
907a4d35-68e5-5919-8a61-9a4da01754e3 | note | ACTION (W, M, H) - W
d42a5ec6-c3d7-5180-b247-a8f04d83bac3 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
84740fbf-b652-5ad6-b88c-68481fe4376b | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
86d15a30-8b7d-58ee-9be0-d1586ebc2a34 | note | Frequency - Per each connection
1efd81df-7900-5d3c-be3e-6c75ba7b4a46 | note | Inspection / Test Method - Inspection
6a3b869b-8579-523b-8345-bc3457b41a25 | note | Verification Records - Photos
cf1a5b3f-c72d-5484-99f9-e337c6286b0a | note | Standard - AS/NZS 4129
43e2eea9-02e0-5523-925f-37b78cf8edcd | note | Signatory - Site Engineer
92313d4f-ea50-4f46-bcfb-97e58227f79f | checkpoint | D5.5 - Fire Hydrant MOANAFH1 at CH512 (1)
0d1dd91f-bb01-56c2-a523-109a73c94a7c | note | ACTION (W, M, H) - W
1a679bf8-5ca4-5483-b4cb-30b30facd5dc | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
649e00f7-aa87-5479-b9b5-980c628a261b | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
6afd6700-3be4-5cd7-b551-c1df0458069c | note | Frequency - Per each hydrant
a4e60862-2d5a-555f-a1bf-6784489ca150 | note | Inspection / Test Method - Inspection
dfaefe18-8978-5bf5-aff4-6806b7e688ff | note | Verification Records - Photos
14db3bd5-9a4c-5c10-981d-faef7b79da4f | note | Standard - NZS 4522
8b24d3fd-da94-5cba-bd60-1ed85b2b76ef | note | Signatory - Site Engineer
f66e9fc7-5db3-4f46-9391-8f4561102d9d | checkpoint | D5.5 - Fire Hydrant MOANAFH1 at CH512 (2)
04b0ee02-bce9-5786-b9d8-7a53a77950e5 | note | ACTION (W, M, H) - W
4e5f3f86-7071-50cf-bd8a-070bcd56abf7 | note | Conformance Criteria (What's Required) - Surface box finish
e3021d82-0e1f-5455-9d08-8313a6c2f9a3 | note | Detail - cast iron valve box to be flush with the finished surface level.
b86180f6-1843-5156-bb27-d187422ac1c2 | note | Frequency - Per each hydrant
1d9cfa8f-ddc2-5d7d-a75b-a3f99f8ed38f | note | Inspection / Test Method - Inspection
df6c3cfd-ab3f-5d07-9ff3-fa37d4328d9b | note | Verification Records - Photos
b5b272d5-8d8f-51b7-8fe8-ec9f0f57292e | note | Standard - NZS 4522
fd405dc7-52f9-5b71-b49a-167eca76757f | note | Signatory - Site Engineer
c6d3220e-6fc3-4232-b536-9991bb2e4282 | checkpoint | D5.5 - Fire Hydrant MOANAFH1 at CH512 (3)
04907f91-1a10-5398-b3a9-4922cc1b0c75 | note | ACTION (W, M, H) - W
f568fa9b-97cf-56d6-ab42-6a07ac1ee181 | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
4071fdae-6a95-5eb4-8481-5634c8311b65 | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
c5b373b1-0c85-5436-8833-87b40db5045d | note | Frequency - Per each hydrant
cf0196b1-7c24-5545-b372-8cfc35a78f3d | note | Inspection / Test Method - Inspection
6aa07cbf-788a-543a-bb8b-aacbe7d5f55e | note | Verification Records - Photos
dff984f9-07f5-5366-98a2-fd96574f4533 | note | Standard - NZS 4522
d2145d08-4666-5834-afae-1d71f6cc2750 | note | Signatory - Site Engineer
fa43b759-09ab-4f98-ac6e-82425e8d8a75 | checkpoint | D8.3, D8.4 - Lateral connection to house no#183 Moana Street
aa4b9472-fed2-528e-8029-dcc1344bca76 | note | ACTION (W, M, H) - W
3047b0a0-8a75-53a5-ae3d-b437d768f905 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
d16bcd57-588f-552c-8db6-19e7df7e360f | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
9783fa5f-89bd-54c9-aeef-0669ac2c4f35 | note | Frequency - Per each connection
222fd7f4-edc3-56a0-a416-b42e4777736a | note | Inspection / Test Method - Inspection
7e611c51-d4cd-5cd9-9db9-1b1812d1295f | note | Verification Records - Photos
da0150b1-bfe6-5915-a19f-80a2851ad3e4 | note | Standard - AS/NZS 4129
2cb6bad3-3f1f-5de6-8268-5a3a746808ff | note | Signatory - Site Engineer
8b4455b0-f486-4bd5-8de8-b84f6ef87ee6 | checkpoint | D8.3, D8.4 - Lateral connection to house no#177 Moana Street
e95f48f9-e380-594f-948a-8b873877071b | note | ACTION (W, M, H) - W
48cfbc66-394c-5e8b-af13-026162cb3cbb | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
fb8d5942-cea4-5a8f-8959-0265885723b3 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
23622096-ae29-5da5-acfc-fbad1e4de130 | note | Frequency - Per each connection
f878a0ad-9494-5aef-b7be-871f992775aa | note | Inspection / Test Method - Inspection
08ea7782-bc9d-58bb-9f10-58026d1dc13a | note | Verification Records - Photos
082dfa61-f0a0-5612-9669-a7c947413175 | note | Standard - AS/NZS 4129
12951282-7d98-5312-9473-cded53daee73 | note | Signatory - Site Engineer
7b0251b0-1def-40e2-8fd9-db1b297cbe7d | checkpoint | D8.3, D8.4 - Lateral connection to house no#171 Moana Street
da65c5f7-2ca0-5a5d-b2c9-165b2d01bcc4 | note | ACTION (W, M, H) - W
a1cb9dba-33e1-56d8-b1a8-faad8063878e | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
1763dae3-6293-5c65-9b94-8d9d3c22e32b | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
10192136-9eac-5957-b668-e277a05100ff | note | Frequency - Per each connection
759f1765-7bb0-53bf-811e-6c4df7ed40c2 | note | Inspection / Test Method - Inspection
ad5643b7-e58f-5f75-adf2-3baa2a6a8c6e | note | Verification Records - Photos
fd9cf6c0-f9c6-52af-b77e-6082d5d79f03 | note | Standard - AS/NZS 4129
77b9247f-3f5b-5c1e-8715-68d64b44788f | note | Signatory - Site Engineer
c3381259-8131-46f9-aea1-7017e1b60851 | checkpoint | D8.3, D8.4 - Lateral connection to house no#176 Moana Street
0311bcc2-8154-5ba4-b2c9-ab363911e143 | note | ACTION (W, M, H) - W
85487b6c-3bb2-52ef-9755-c47cfd033909 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
af209329-d0f7-5c1e-808b-ac13d648e762 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
05ddb60f-c1bf-51cb-a536-8617c71d2260 | note | Frequency - Per each connection
c0885d9e-f05c-5f13-b415-4c874fb88c87 | note | Inspection / Test Method - Inspection
a0a72004-1850-5edd-b6a2-833c8aa9bfb3 | note | Verification Records - Photos
d775ceb7-3a33-5df0-b0df-2e61b041a771 | note | Standard - AS/NZS 4129
3fa5f8b2-14f8-5e5c-a796-73594cc27640 | note | Signatory - Site Engineer
ff3555ea-3867-41b1-88a2-f18accd351fa | checkpoint | D8.3, D8.4 - Lateral connection to house no#165 Moana Street
7829b344-ccf3-579e-a21a-6f68e0effdd4 | note | ACTION (W, M, H) - W
1cd9f900-79f2-5ae0-9e37-535a3a8e8baa | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
4edc37f1-447e-51f4-bbce-26f40ba85741 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
1a64f328-e100-578d-a99c-9547b5807f34 | note | Frequency - Per each connection
9af99404-165f-558b-b837-654d6438814f | note | Inspection / Test Method - Inspection
cf48583d-dd74-5ea1-b029-99d6b4df275b | note | Verification Records - Photos
eb3cac38-05ee-52b6-9246-fe4920eb0603 | note | Standard - AS/NZS 4129
f6ddb431-74ea-5c88-af44-ebda149ca766 | note | Signatory - Site Engineer
a1d518c9-3dee-4a72-95c5-02ce5d0cf4f0 | checkpoint | D8.3, D8.4 - Lateral connection to house no#174 Moana Street
b18242c3-3420-5039-9505-512728aa1e9d | note | ACTION (W, M, H) - W
ef770eed-5d11-59a0-8002-b4ccf2ba65b1 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
27b24ed0-172b-5a7a-bff4-ea1593731c88 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
63ebecef-0ca7-5638-9fb4-2100dc4ecb68 | note | Frequency - Per each connection
595201ba-045a-59ef-b5d6-b6539b3f6754 | note | Inspection / Test Method - Inspection
c63f402e-2192-55c3-aadf-54bfc72ffcee | note | Verification Records - Photos
d4935d77-5c0f-57ab-af92-e19931a9ba8d | note | Standard - AS/NZS 4129
a7383911-0840-593c-a917-a5ab50e1ab37 | note | Signatory - Site Engineer
a0b88663-98ad-40e6-ac45-d8f8aed618ff | checkpoint | D8.3, D8.4 - Lateral connection to house on Moana Street needs confirmation at #172
6eb0a833-5953-578c-83a2-3e421a48df1f | note | ACTION (W, M, H) - H
0749fd06-a280-51dd-85e1-571929f55857 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
8a239430-fd19-54c5-9413-13b7416e1bcd | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
8f80f659-b5af-553b-a18e-725520629157 | note | Frequency - Per each connection
35f87a2b-cbf2-5713-9925-a9b3bafb33b5 | note | Inspection / Test Method - CONFIRMATION REQUIRED
07cb8441-f40a-586d-9852-5d042f0899d2 | note | Verification Records - Photos
038e6492-4e60-5b2c-b3f0-5c70ffe96388 | note | Standard - AS/NZS 4129
0b2ab716-fd68-5e81-8d55-e2d6b593c612 | note | Signatory - Engineers Representative
447fca06-4650-40b8-bce1-0f3c5d7c0e97 | checkpoint | D8.3, D8.4 - Lateral connection to house no#170 Moana Street
faf15dc3-f171-54ad-aadb-29ca7930255d | note | ACTION (W, M, H) - W
937673ef-3dc6-5deb-9550-7c7f7be9547a | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
534830f5-f09d-5bc7-ba68-7695bd67ed94 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
cab43a00-c3f3-5dcc-9e13-558fa2e54b7a | note | Frequency - Per each connection
22ac4e45-14ef-5ec4-9db2-0e8e7d05727e | note | Inspection / Test Method - Inspection
57c57ccd-7078-5383-8bf6-8e9368413617 | note | Verification Records - Photos
485c969c-83a2-5579-b7fa-b3b8a51f7898 | note | Standard - AS/NZS 4129
9bb4eba9-3f73-5355-ba95-128ac2ade7b1 | note | Signatory - Site Engineer
aac07927-a9a6-465d-8c72-fd6c0a09217e | checkpoint | D8.3, D8.4 - Lateral connection to house no#163 Moana Street
44513c16-94f8-5ac0-9575-7869564ab308 | note | ACTION (W, M, H) - W
9da799d6-f084-59db-85f5-1b1cc6cb358f | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
b5625741-ba2c-541b-9e32-60850d4f5bc9 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
856ff9f9-cbd5-5661-8f3c-accf9765c380 | note | Frequency - Per each connection
5561290f-a6f6-5622-82d4-89c1e18f41e5 | note | Inspection / Test Method - Inspection
2dc2a360-b9ad-5673-8932-a523318cc315 | note | Verification Records - Photos
b82328d2-bc0d-5122-8ad0-317fadbaac28 | note | Standard - AS/NZS 4129
d546c651-feb8-5bd5-b251-e4ab1fc53cae | note | Signatory - Site Engineer
80f740c0-290f-4c66-a7cc-4b4a996f0c15 | checkpoint | D8.3, D8.4 - Lateral connection to house no#162 Moana Street
4b2a8315-3a19-5211-af0b-ebf31da3b3cf | note | ACTION (W, M, H) - W
7f51d169-b8ad-57bf-b1fc-1f28e68856d0 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
ece31579-4d34-5363-994a-70c9784201bd | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
f5ea2b1d-f671-5d4e-a96b-3fa4e8492bb1 | note | Frequency - Per each connection
3a9b35a7-e6da-5bed-9aae-5d57f28a1ad3 | note | Inspection / Test Method - Inspection
a0e61a73-3ec4-5dbc-8ea3-2b7b8ae95025 | note | Verification Records - Photos
90afa8db-4b14-5a2b-858d-0209051110d0 | note | Standard - AS/NZS 4129
76a6b358-9a06-5a31-ae44-d286b1de6f50 | note | Signatory - Site Engineer
ca063a93-0b22-40f9-81a9-33a40796ce55 | checkpoint | D8.3, D8.4 - Lateral connection to house no#159 Moana Street
dcb93866-d68d-53a1-b868-1715dedab0c6 | note | ACTION (W, M, H) - W
44f8bb36-d173-5740-9abb-8e9922bef1ab | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
98723edc-f3ec-53d0-b956-7f4e0a251759 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
1e86ffd6-5e5d-52c4-a486-726677f2a571 | note | Frequency - Per each connection
8e9d2bbe-8cfe-5679-9402-4840eb9f69ec | note | Inspection / Test Method - Inspection
1fbe63d8-bf5c-5394-b7c2-ff879fe9c76c | note | Verification Records - Photos
f83b5e96-b070-5688-ad74-766473f0dea4 | note | Standard - AS/NZS 4129
f82574ca-5c49-5bbc-b92c-bade8e3c709c | note | Signatory - Site Engineer
3eb570a8-ebbb-4b55-800c-8da88e0dae1d | checkpoint | D8.3, D8.4 - Lateral connection to house no#158 Moana Street
44544443-5dfa-5431-b764-ab3dac723a0b | note | ACTION (W, M, H) - W
f1d3af13-1061-509e-960c-2b001a848535 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
0aff51d0-89ec-5d99-8c30-8052131003bd | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
e992aac8-02ea-52d0-ab31-5c413fabf75a | note | Frequency - Per each connection
3a297555-cc82-58cf-8baa-3b1d338a5a65 | note | Inspection / Test Method - Inspection
f1653716-b5ec-5aff-b52b-fed141c87d30 | note | Verification Records - Photos
c999c684-dd78-5a66-862e-1551b4a24e82 | note | Standard - AS/NZS 4129
87832fc2-8841-5d6d-bf66-13b69b0cb906 | note | Signatory - Site Engineer
3c2f3b2b-9ec5-4c3d-bb54-f7f88d3e5603 | checkpoint | D8.3, D8.4 - Lateral connection to house no#154 Moana Street
89459815-d3fd-5848-b2c9-62bd27d665ae | note | ACTION (W, M, H) - W
95d2c869-40dc-5371-9e5b-189cfebd2a85 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
5758899d-aa22-5a67-af02-f45e649f2f2f | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
d051a68e-11d6-55dc-bb5e-73527d84e5e3 | note | Frequency - Per each connection
80300acc-027e-5d6e-8196-b4346ed51745 | note | Inspection / Test Method - Inspection
daa3f2f1-8794-599f-88c7-34dbdfe70ecb | note | Verification Records - Photos
1d6512ac-2d64-5389-bd96-3f5f0384fca1 | note | Standard - AS/NZS 4129
3e93e74e-6f44-50ea-92b3-e3697b0ebab6 | note | Signatory - Site Engineer
45020545-f075-413e-a957-b3dfb7f30a49 | checkpoint | D5.5 - Fire Hydrant MOANAFH2 at CH647 (1)
6047358d-749d-5ccb-ab9d-df7ee362c14c | note | ACTION (W, M, H) - W
8ef8cea7-12a8-5684-a61a-dd3bc1105195 | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
4825a6b3-52af-5ca4-91c9-2073f82b8ec5 | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
c815ec76-6be5-5433-b1f2-2ed27779d036 | note | Frequency - Per each hydrant
2eaee4fc-4fd6-5163-923f-c4ac2585960d | note | Inspection / Test Method - Inspection
d46d8b24-7206-5529-9b14-5de2d844027b | note | Verification Records - Photos
495f32e0-3a48-59ab-b1c0-272e6962409f | note | Standard - NZS 4522
0f95784f-c953-5852-91cd-0c9a94226e2f | note | Signatory - Site Engineer
a10f0d88-610e-4978-acc3-27758ef86699 | checkpoint | D5.5 - Fire Hydrant MOANAFH2 at CH647 (2)
0e19f324-45b0-54a5-88cb-4ba36c5e1882 | note | ACTION (W, M, H) - W
581e013c-b404-511c-8c24-bef14bef5495 | note | Conformance Criteria (What's Required) - Surface box finish
965fcd09-9080-5783-971d-e03b78568487 | note | Detail - cast iron valve box to be flush with the finished surface level.
f056a18e-79c5-5f65-ba54-f725ebb3852a | note | Frequency - Per each hydrant
c5e160df-0d15-5561-899f-ea99ff5492d9 | note | Inspection / Test Method - Inspection
a9f7e9eb-30b1-51de-bb0c-1520114f5bea | note | Verification Records - Photos
18cf9632-84ca-5ff1-858d-d5b5164cf76d | note | Standard - NZS 4522
5101b4a6-1c6e-5883-b4da-b08656137b6e | note | Signatory - Site Engineer
a32795ea-1638-4dea-958f-28cf191f614f | checkpoint | D5.5 - Fire Hydrant MOANAFH2 at CH647 (3)
60a0866c-9cf0-5663-9884-937f24017e5d | note | ACTION (W, M, H) - W
cbb6aa59-9fed-5a77-83d4-1494e87d261c | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
8ee25d80-f27d-561d-9086-ef77021ac36a | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
2f3629eb-c9e9-51e3-9a41-742d6d710c18 | note | Frequency - Per each hydrant
5a27c30a-d2ce-5799-8a84-9a47093f3bc2 | note | Inspection / Test Method - Inspection
ebb0dd98-cbde-50fc-bffe-0ab4e23886d9 | note | Verification Records - Photos
d74c397f-deef-5fb4-8107-7a09839009b6 | note | Standard - NZS 4522
131f4b78-6a52-513d-aee2-c5f69b92a8e6 | note | Signatory - Site Engineer
6de2dc10-10f5-4e96-961d-2587802bf674 | checkpoint | D8.3, D8.4 - Lateral connection to house no#150 Moana Street
9d47418c-74cd-5489-824d-192b50e79910 | note | ACTION (W, M, H) - W
2120612b-8638-58c5-b0d8-01cac586574a | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
05bb5850-ed1a-51ac-9563-d1296d535069 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
10f1b472-1b54-5bf9-8fd0-e6c889c5662f | note | Frequency - Per each connection
3ff7cf3e-5910-5c08-8e6f-e64bc501ee1f | note | Inspection / Test Method - Inspection
8eb9aa71-c1b8-55ed-be7f-0045dc512056 | note | Verification Records - Photos
d10700eb-2e49-5aee-9b42-983f40505622 | note | Standard - AS/NZS 4129
da35185f-6dc5-5cc3-a42a-b4c7c6e4f78a | note | Signatory - Site Engineer
6b4246cb-8d3a-4eed-9022-309c322cd187 | checkpoint | D8.3, D8.4 - Lateral connection to house no#151 Moana Street
77dafd28-33c8-582f-8d10-6c920ddf0bf3 | note | ACTION (W, M, H) - W
482a6df8-bc73-5adb-9ca6-c6aa8340b404 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
e079512d-9cad-58ad-b439-6be77f7bc005 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
386088ea-2eb4-535a-9661-3051872546ae | note | Frequency - Per each connection
264fffd3-0012-5806-850f-6a8d8a1d123f | note | Inspection / Test Method - Inspection
858fcf3e-4d68-518c-98cb-23848d8f3d29 | note | Verification Records - Photos
63761211-0723-5da3-a02e-57833dc90bf3 | note | Standard - AS/NZS 4129
736d237a-fe56-55fb-bb5e-a5eb3915ce1a | note | Signatory - Site Engineer
de7b70a3-e759-4bd3-b285-e0fbe80a9c91 | checkpoint | D8.3, D8.4 - Lateral connection to house on Moana Street needs confirmation at #151 - potential duplicate
5e765387-2214-5790-9453-04906334dad0 | note | ACTION (W, M, H) - W
36f1fef5-9909-59d0-ac1b-9bb2ff9335df | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
c1d368cf-8041-5f2f-915a-84e149c51979 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
d9ddd052-2053-50d9-a4e6-c450cf21358c | note | Frequency - Per each connection
643993e3-cb83-5bcf-a067-75a3211a0e4c | note | Inspection / Test Method - Inspection
ee4a0211-b0ca-526c-bcc7-659aae44da53 | note | Verification Records - Photos
c6e8bd9f-a653-5414-ac0e-d2d5049def26 | note | Standard - AS/NZS 4129
1e2b7420-4a7d-51f6-9a2e-d7e24df470a1 | note | Signatory - Engineers Representative
d5c89dca-53bf-4a1f-bf13-da50bf6ce11c | checkpoint | D8.3, D8.4 - Lateral connection to house no#145 Moana Street
2308f0f8-55ef-5a9a-baab-25953a8db46f | note | ACTION (W, M, H) - W
cc1a94ed-55ea-5126-86ce-d14edd502742 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
e1519bfb-76e0-5ffd-b4d2-2040d4f7342a | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
16927154-2b7c-5e92-adad-bab64ab99556 | note | Frequency - Per each connection
d1b472b6-d5c6-5b91-9211-c0c52b70d476 | note | Inspection / Test Method - Inspection
6a005d1d-61af-5565-9af9-c84f93d92954 | note | Verification Records - Photos
4cd0ec44-7c46-5b34-88e2-5ac9eb494077 | note | Standard - AS/NZS 4129
00d8ac30-67c7-52a2-ac29-bfef285008c5 | note | Signatory - Site Engineer
1131792b-6ca4-4c5c-85e2-5f290a182fcd | checkpoint | D8.3, D8.4 - Lateral connection to house no#146 Moana Street
60c5bdf1-2050-55df-8c29-3561780ee4e0 | note | ACTION (W, M, H) - W
c7603180-bcf6-51a1-90ff-5bf262d8d372 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
f69fbf81-f556-5245-9dcd-5d16af30119a | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
aa755777-bd96-5d82-ab50-67304c2d7fc0 | note | Frequency - Per each connection
f045e165-7b6d-5428-8991-c9163280f8e9 | note | Inspection / Test Method - Inspection
ceef791a-d2fd-59e9-a688-f860e6de2538 | note | Verification Records - Photos
83bac5c7-3539-5e87-939d-ac4c1b9fdca2 | note | Standard - AS/NZS 4129
3c7e5423-d357-516b-8fac-942e179f093b | note | Signatory - Site Engineer
4f472a69-432d-4b0c-b4d6-f9ea5b53d171 | checkpoint | D8.3, D8.4 - Lateral connection to house no#141 Moana Street
1a91b5ee-e959-59af-bf91-5a22fb65dfb5 | note | ACTION (W, M, H) - W
5b34e454-cbc1-5e78-97ee-b9eb119105e7 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
16ec2f17-2ffd-52df-bee5-9a7dd16ebecd | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
1c3311ed-0408-59ed-924a-b5735b2c7536 | note | Frequency - Per each connection
0a85ca2e-85b2-5704-a9a4-080badf995aa | note | Inspection / Test Method - Inspection
8afb166b-f355-5322-9f03-aca9d06f4e1f | note | Verification Records - Photos
76552743-a3c3-5c00-b4ac-5d60a2a6c263 | note | Standard - AS/NZS 4129
c208818b-f75c-5440-8f3b-b843702e3d95 | note | Signatory - Site Engineer
cb0bfeb6-e545-47d8-9851-5ac669eab2df | checkpoint | D8.3, D8.4 - Lateral connection to house no#142 Moana Street
bc050f89-6116-5ccd-84e0-9945f831f465 | note | ACTION (W, M, H) - W
131ac689-dfd2-5dfc-8d94-d3633fbfcd60 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
5b26cde9-6ec1-568b-97b2-187ee6da314b | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
2b37d5f8-fd70-5784-9462-92f74f7a164f | note | Frequency - Per each connection
8b71130e-a7a6-5996-be40-2e7d05fa3563 | note | Inspection / Test Method - Inspection
b042b0dc-f573-5099-85e6-cdcd0e1c3083 | note | Verification Records - Photos
2e296435-aea9-57ef-a312-0dee74819a1a | note | Standard - AS/NZS 4129
ffa21bd9-7895-5f37-ae89-501ea8b3207b | note | Signatory - Site Engineer
82c7f48a-b96e-4508-a9df-f35f2dec47ee | checkpoint | D8.3, D8.4 - Lateral connection to house no#138 Moana Street
022f9ebb-19c8-5e63-9308-f56b59c0d1b8 | note | ACTION (W, M, H) - W
adf81d0a-8c05-5d78-9621-a57c17f1d743 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
83ef3a76-5af3-526e-8a37-f4bc6c0a524c | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
9c958937-a340-505e-a08a-6a9c77783dca | note | Frequency - Per each connection
4f4b69c8-aa4a-5f6c-ba85-f803e25cfd71 | note | Inspection / Test Method - Inspection
dd07aa4b-0d61-5d7c-bcde-b94e9bc8d457 | note | Verification Records - Photos
2ff38940-d039-52e2-8083-3eb0fa6d41b9 | note | Standard - AS/NZS 4129
6ac8b3e1-1f11-520b-9bb7-b431123ea418 | note | Signatory - Site Engineer
87c6788f-c2d7-4946-845a-1dca1adf9a8e | checkpoint | D5.5 - Fire Hydrant MOANAFH3 at CH725 (1)
0576548f-c554-516a-aa46-2564098ba4e7 | note | ACTION (W, M, H) - W
0fb8a8ab-d141-5c3b-a6e8-06b33495354a | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
1222591b-c6f2-585e-8ee7-43b3c2de3c1e | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
e0bf8ffc-e958-5df5-9ce8-e3ccdb6fd10b | note | Frequency - Per each hydrant
9722e417-d1c8-5078-8273-a27110e8a0c2 | note | Inspection / Test Method - Inspection
c4a42111-9d59-570a-9ab7-6dbdd36627cd | note | Verification Records - Photos
1d68f952-1cbc-54aa-8867-9870d5dde1bd | note | Standard - NZS 4522
bd5bcff5-9ed2-5faa-9a89-ee81b97ddcef | note | Signatory - Site Engineer
a6aac143-691c-4a08-b924-f9c50378356e | checkpoint | D5.5 - Fire Hydrant MOANAFH3 at CH725 (2)
98638b1a-6227-51bb-a3bf-acb17c53c334 | note | ACTION (W, M, H) - W
829a5cd8-4dff-5c82-90f3-54bca2093739 | note | Conformance Criteria (What's Required) - Surface box finish
726c896d-244c-5486-b332-afad62d68459 | note | Detail - cast iron valve box to be flush with the finished surface level.
25fd05c7-2790-51c7-a33f-9d92b22c6fe6 | note | Frequency - Per each hydrant
29e59974-b070-5874-94cd-e43ded5277d8 | note | Inspection / Test Method - Inspection
ecca3174-8309-57d4-b7fb-83c32c3a2c98 | note | Verification Records - Photos
c2c1ace1-2782-54d5-9c68-8454e03b8d86 | note | Standard - NZS 4522
4e252010-d032-5b9b-8e92-c55c3afdb6b5 | note | Signatory - Site Engineer
8c31f797-1748-46c4-b6df-049459538f02 | checkpoint | D5.5 - Fire Hydrant MOANAFH3 at CH725 (3)
a2bfd4e5-2c1e-5ef5-84d1-85164a0a0815 | note | ACTION (W, M, H) - W
0a3eb9bb-7c6c-5820-b06f-e7ec5d94b9e3 | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
75383310-9f40-583c-9952-a2ef0219c0b9 | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
c5721372-ca0a-591b-824f-6b3750b9d437 | note | Frequency - Per each hydrant
828d76dd-56a4-5bb5-9919-5d4c57cd01b2 | note | Inspection / Test Method - Inspection
7d4b9070-c27c-5cf9-a5a4-4c0d3782c321 | note | Verification Records - Photos
afd745ee-5cba-5b5d-b950-82916bc85e26 | note | Standard - NZS 4522
33780ab9-8232-5051-b8d2-9031daf2f450 | note | Signatory - Site Engineer
77b80956-44fb-462f-935b-685427d9a0f5 | checkpoint | D5.4.2 - Isolation Valve MOANA-WILTON CH748 (1)
dead2117-9d8f-5472-8bc9-386d8304a31b | note | ACTION (W, M, H) - W
8b08f2ee-4403-5ad1-9d30-df20846287d0 | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
ba817aff-d45d-5041-818b-44205ba0a040 | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
5fdaf188-630e-57f2-a86c-581ce606a60d | note | Frequency - Per each valve
f5f01e1d-8b66-54e8-9111-772d6590d280 | note | Inspection / Test Method - Inspection
65d25eb8-555c-55ab-8cac-3318e535c5dc | note | Verification Records - Photos
7f82247e-fd95-57f4-8a30-a35dda1d71bd | note | Signatory - Site Engineer
7fc768e6-5b9b-4e6f-9f85-d8b991d3c18e | checkpoint | D5.4.2 - Isolation Valve MOANA-WILTON CH748 (2)
04058f81-8721-5f78-8b1a-1e1e61e0c517 | note | ACTION (W, M, H) - W
c62ab581-9e3f-54c3-9dc2-0d04bd43e968 | note | Conformance Criteria (What's Required) - Thrust wall installed
00faa685-650c-5b90-bb93-21e7d152d9f7 | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
61c2f5eb-7b65-517c-9a5f-b08c67371851 | note | Frequency - Per each valve
a0e128be-34c6-5bb6-8433-a6181673c5f5 | note | Inspection / Test Method - Inspection
04257bc2-98fd-5db9-9044-c10f36eec39b | note | Verification Records - Photos
a5b8d8a8-141d-52eb-abba-47e56d6f31e9 | note | Signatory - Site Engineer
4b16e085-91c9-4816-a10d-bfc5fd4ee859 | checkpoint | D5.4.2 - Isolation Valve MOANA-WILTON CH748 (3)
c4b79361-9c3b-5638-a8b2-b1d64195911b | note | ACTION (W, M, H) - W
a36cdc39-baf9-5b26-8c5e-0c1a4b3792bc | note | Conformance Criteria (What's Required) - Surface box finish
87e84a3a-acb9-5c11-a79a-d111e5693e00 | note | Detail - cast iron valve box to be flush with the finished surface level.
94f35b10-0185-5330-b798-d81a90726b52 | note | Frequency - Per each valve
22ae77ff-33f6-5c79-a5f6-c428be89c07a | note | Inspection / Test Method - Inspection
a5166ce0-e30e-5635-b795-ffd9acaf0475 | note | Verification Records - Photos
fc3ce3c2-bd08-53bb-9dda-fed68277e6e9 | note | Signatory - Site Engineer
628714cc-e656-4b7c-8834-0d667a2b1e3c | checkpoint | Link in at intersection of Moana Street and Wilton Street (1)
ab65de95-5250-555e-bdb6-4e0056cff145 | note | ACTION (W, M, H) - W
b1b9faf0-82df-50cb-8e9a-ed6f45d06c8e | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
eb039291-9c31-5758-9308-0bbb537091b4 | note | Detail - PE to DI connection to be done as per the detail D in sheet 15 of the drawing
f4fd841f-70eb-55c2-bda9-33fe708f20b1 | note | Frequency - Before backfilling
fd537754-e2a8-54e8-8d9e-c93b75213cc4 | note | Inspection / Test Method - Inspection
1521eccf-cb24-5919-9640-09e1eff3c26f | note | Verification Records - Photos
ecb50047-9a17-56d9-b1d7-bca0b0886ff6 | note | Signatory - Site Engineer
c0ecebf4-c735-4f31-a60a-d3fe9cbf3d86 | checkpoint | Link in at intersection of Moana Street and Wilton Street (2)
952a4d33-19c9-544e-82fd-2ffb3a174b39 | note | ACTION (W, M, H) - W
12c433ea-973f-5b7b-8e10-7565cf053002 | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x3)
6d6d1660-5548-5b03-965f-cec0784770c6 | note | Detail - As per detail D in sheet 15 and typical details as per sheet 18
cb2c4283-caef-53f2-997e-053847c89e63 | note | Frequency - Before backfilling
e64a21f8-8d08-5453-bf68-9fc5943b21f2 | note | Inspection / Test Method - Inspection
97cbc2bc-b92c-544f-b63d-e98a53972632 | note | Verification Records - Photos
9a8fcc99-fe58-5752-95b3-b7d02389bbd3 | note | Signatory - Site Engineer
c8ea47a0-cdfc-4abd-8074-c73f2543d0b2 | checkpoint | D2.7 - Trenching and excavation
3e029b60-4f75-58ec-a650-4cba5d12f033 | note | ACTION (W, M, H) - M
ac53f1a6-9d6f-55be-bc57-af40a36084b5 | note | Conformance Criteria (What's Required) - In accordance with NZS 4407
e7f3e6ea-bb02-55e6-a032-b92f04673c8d | note | Detail - AP65 Subbase particle size and sand equivalent
d5dbe404-f6f5-5727-b634-98f59ce0beb9 | note | Frequency - Daily
1943f0b5-f335-5db4-9ac6-93d683e8cac4 | note | Inspection / Test Method - Inspection
01e1c64c-f1c4-5215-93d6-2d1d065cd70e | note | Verification Records - RCP and digging checklist
8e92773b-9aab-5467-9b2a-3e0adcb33551 | note | Standard - NZS 4407
5459d460-8184-55bc-a013-00dcb412a1d0 | note | Signatory - Site Engineer
67a6961c-ae4a-443f-bc47-f6e0b4000095 | checkpoint | D2.9.1 - Pressure testing & disinfection (1)
690036f8-c629-5da9-b8cc-fd4da1ac1fb5 | note | ACTION (W, M, H) - H
f235e8eb-25b3-58b4-8dd2-93f603db659f | note | Conformance Criteria (What's Required) - AS/NZS 2566:2 Section 6.3
3458e3d2-dc3a-512d-8359-967311fa99b3 | note | Detail - pressure testing of the new PE main
70fc3ed1-f016-5309-b5cc-3880edfa0561 | note | Frequency - Prior to link in
6f50a11b-ec08-5f13-96b0-92fb9abb5f4a | note | Inspection / Test Method - Testing
745b1f03-8792-5c10-8648-532069a868c9 | note | Verification Records - Test records
b36c953f-cdb5-5309-8ae1-16134e4ab79b | note | Standard - AS/NZS 2566:2 Section 6.3
f0a33f3f-21dd-515c-aa33-810f09f4bb80 | note | Signatory - Engineers Representative
452d977b-c7e0-43d0-bafe-9752e7e6426b | signoff | HOLD POINT
531b1c94-2352-430a-9124-270b4ea0ee37 | checkpoint | D2.9.1 - Pressure testing & disinfection (2)
c306b62f-5215-5c5f-9e1c-71176dbc10b7 | note | ACTION (W, M, H) - H
c7aad2ec-3c97-5afe-9096-6eb4cb147fe8 | note | Conformance Criteria (What's Required) - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
e99fe88e-67b7-5a8e-839a-3e0e669827bd | note | Detail - Disinfection of the new PE main
f2eadce9-36d7-5b27-a499-5930a6dd5603 | note | Frequency - Prior to link in
f4e2b485-f311-5208-9538-990a2904f817 | note | Inspection / Test Method - Testing
c53db840-29da-5df0-9784-b7ea31a8c96b | note | Verification Records - Test records
f1f22117-7f93-52b8-918b-4731863d055f | note | Standard - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
77864300-4b12-5501-a937-8edcaee72b58 | note | Signatory - Engineers Representative
9b94af7c-aacf-4ea0-bc69-dd041ccf6790 | signoff | HOLD POINT
c82618a9-ba62-4d11-b8e8-540374f192ce | checkpoint | D1.3.3 - Engineer's inspections
a047653c-74c3-5039-b072-d36ca289dc88 | note | ACTION (W, M, H) - H
d9abd032-0130-5a07-bacc-26e444752b92 | note | Conformance Criteria (What's Required) - Inspection report
f67f1e16-3db0-5066-82b2-949bb996ee63 | note | Detail - Enginer's inspection for pipe, concrete pre pour, pre sealing
6fab9f91-79ce-5a44-8e72-a3f82687edc2 | note | Frequency - As required
fab1be9c-29fe-55ce-96bb-8390db6cb94e | note | Inspection / Test Method - Inspection
0b6ad957-6a28-5452-b84a-10ee8482af70 | note | Verification Records - Email
24ab2228-d661-59f1-abb8-eaaa05e05c76 | note | Signatory - Engineers Representative
d76d45f9-f628-4ed5-b2a8-12f940192ca8 | signoff | HOLD POINT
f4473b8e-861c-4d1a-85b7-466723ba4cb5 | checkpoint | C1.18 - Surface Reinstatement (1)
402be360-4864-58a4-bbf4-809a30ef3621 | note | ACTION (W, M, H) - H
3224a2ae-f893-589a-8ed9-ca1aa5654aec | note | Conformance Criteria (What's Required) - Engineer's Approval
4c8b4bff-470d-538d-9a61-3cdc9811178d | note | Detail - Mark out the trench including overcuts
37849ff3-c9b8-5104-8f1c-b491a2a5031d | note | Frequency - Prior to surfacing
33d407c2-3412-5905-b930-3975cc3b50cf | note | Inspection / Test Method - Inspection
5fcc6fa9-2be3-5a4e-9e8a-2efd6919d449 | note | Verification Records - Email
b28a22fd-7d76-5b82-ac0a-133494e22c49 | note | Signatory - Engineers Representative
899eeaa3-46e9-4e13-8746-38b6304d7f77 | signoff | HOLD POINT
c3773bb9-65d1-4e25-9e40-7a3ec29e2d76 | checkpoint | C1.18 - Surface Reinstatement (2)
af11554c-4af2-59e7-b6f9-6114bf4e4a24 | note | ACTION (W, M, H) - H
4094b2d7-a419-5ae7-9f1b-8ad1abed9915 | note | Conformance Criteria (What's Required) - NDM testing
f4d7b610-f11c-5a95-a183-8ee6aa19ac02 | note | Detail - Provide NDM test results for AP65 and AP40 layers
11abb441-e1aa-547d-9094-3fbf4c171912 | note | Frequency - Prior to surfacing
d637225a-4349-50fc-b6eb-3612afc5b2ba | note | Inspection / Test Method - Testing
3ee98ae7-5fce-5a20-b865-49d73c8a5feb | note | Verification Records - Test records
a832c5fa-bfc2-5975-9524-3cd034e96dbf | note | Signatory - Engineers Representative
7b9e1d43-076f-4694-8380-93f3627ad640 | signoff | HOLD POINT
64e03563-2852-4672-853d-89db88f63c1e | checklist | ITP - Salford, Moana, Wilton, Waihopai Streets - 5.0 Wilton Street - Layard Street to Moana Street (DN125mm) | itp | 5.0 Wilton Street - Layard Street to Moana Street (DN125mm)
3c757b44-9787-4016-b46b-4cbf85ef51f1 | section | 5.0 Wilton Street - Layard Street to Moana Street (DN125mm)
cb5c5f6a-e25d-4bc0-866e-d74d404b5c08 | checkpoint | Link in at intersection of Layard and Wilton Street (1)
700d2557-cb66-5a84-89ca-2fc033220a17 | note | ACTION (W, M, H) - W
c483d8d0-1c87-5322-87ea-654138f5c630 | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
9d423f3b-2c51-567a-bffc-2bd1a729e4bc | note | Detail - PE to DI connection to be done as per the detail M in sheet 15 of the drawing
94448227-7f36-5755-8db9-e27f157b1158 | note | Frequency - Before backfilling
23efb229-f39d-53ca-bcf7-898744419703 | note | Inspection / Test Method - Inspection
2c5b28b8-1e99-54ae-b522-ee0fa29a524d | note | Verification Records - Photos
be8b7aca-56ee-5dc5-9de3-97e9af5ba066 | note | Signatory - Site Engineer
2c83e7da-22b3-47c9-881f-36d88fcf379f | checkpoint | Link in at intersection of Layard and Wilton Street (2)
7aa21f80-8a57-5efe-81b9-e6c6e7134db8 | note | ACTION (W, M, H) - W
4baba07e-2dfb-5fdb-8d93-4a944ae07d68 | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
382c2f9a-7a7a-591a-9376-10b28bbadef8 | note | Detail - As per detail M in sheet 15 and typical details as per sheet 18
1188ad21-82ec-5c2d-b961-d29d811df0e0 | note | Frequency - Before backfilling
68b09890-7122-51f5-ad0d-612f039b128d | note | Inspection / Test Method - Inspection
b2e1075a-074f-584a-8057-c5e53673bdab | note | Verification Records - Photos
d665ca01-d377-5916-894a-1acc3d794d07 | note | Signatory - Site Engineer
5553e9de-9859-4fa9-9478-b5ecf0a0110a | checkpoint | D5.4.2 - Isolation Valve WILTON-LAYARD CH14 (1)
c07bc4b1-6c40-5d4d-af2a-e2706c8ab4a8 | note | ACTION (W, M, H) - W
5f74a213-98e3-59e3-9ecc-dba143623279 | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
abbce033-1a9c-5bde-8f12-93b6b42dc530 | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
43d674d1-03ed-5572-84d8-65a011bf25de | note | Frequency - Per each valve
298fc06f-b83b-5759-9439-d525d7c06777 | note | Inspection / Test Method - Inspection
fc87b0b4-4a50-5e25-b11a-12c14531c5d0 | note | Verification Records - Photos
d93ab11a-a8e1-5708-ade0-fcb68bb950a4 | note | Signatory - Site Engineer
524370c3-b376-4ced-8658-81439e689ca1 | checkpoint | D5.4.2 - Isolation Valve WILTON-LAYARD CH14 (2)
2bd6393a-f4ad-5af7-b7b6-fc0c4d3157a4 | note | ACTION (W, M, H) - W
042acc08-89c7-5e20-a4a5-9f5eb1277983 | note | Conformance Criteria (What's Required) - Thrust wall installed
6f8d62db-17f0-5663-bf9e-8c22f1b0057d | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
4d23cb51-ff45-512e-8e9d-1ac713f196d9 | note | Frequency - Per each valve
20b0155f-bcd0-5577-be2e-399b31481021 | note | Inspection / Test Method - Inspection
dda17541-2cbc-526d-a569-6e7afb8e8f03 | note | Verification Records - Photos
fff6bccb-cf57-516c-8bdb-eab943d9e435 | note | Signatory - Site Engineer
651654c8-f07e-4801-a991-003702e11a43 | checkpoint | D5.4.2 - Isolation Valve WILTON-LAYARD CH14 (3)
5e8d08af-641b-516d-9e8a-90e266dcdf18 | note | ACTION (W, M, H) - W
4898d36f-a28b-54e5-a751-3adeb5a3a0b5 | note | Conformance Criteria (What's Required) - Surface box finish
4b8d483e-1f8d-58fa-86ae-6cf9ca4b7e82 | note | Detail - cast iron valve box to be flush with the finished surface level.
2c57ecae-0475-500d-bb5c-f55c09ae91ba | note | Frequency - Per each valve
e59e6b51-1fe3-51c8-89b2-928adb4c6a65 | note | Inspection / Test Method - Inspection
c75eb985-4c22-5bdc-b825-12d1f452d1b8 | note | Verification Records - Photos
638f0db6-1f50-50ab-8dd9-2c7f14f526fe | note | Signatory - Site Engineer
2c477ce1-2dc5-42c3-bbe7-c7cd1de86b2f | checkpoint | D8.3, D8.4 - Lateral connection to house no#126 Layard Street needs confirmation
f2ac2afa-363b-5278-8d72-570596039b68 | note | ACTION (W, M, H) - W
f4c54558-f156-5127-9f29-709b24448148 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
ed6a6e18-21e6-5d4c-b3e5-e3fa516a657d | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
6f744853-0919-5239-b592-c5a11c2ce292 | note | Frequency - Per each connection
5fe5bad8-1401-5ef5-bc6a-37efc1adb72e | note | Inspection / Test Method - Inspection
94ad2962-5468-51da-8561-f2eebf6376dd | note | Verification Records - Photos
a57ce7df-0e34-5e46-b0e0-a89c15904861 | note | Standard - AS/NZS 4129
4591cee1-3376-5940-b4b4-957332109c67 | note | Signatory - Engineers Representative
c64cf072-a61a-4116-9e56-42d1b1ebf0a8 | checkpoint | D8.3, D8.4 - Lateral connection to house no#125 Wilton Street
dde194ad-928d-5980-afe5-adee04a2bb7b | note | ACTION (W, M, H) - W
ae05705f-639d-5098-89fc-9bbc7a8fb4be | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
7d5c9607-6da6-56b5-82f9-cd2e6090f819 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
7d0f80aa-6754-5980-865d-cc4afa1a0c91 | note | Frequency - Per each connection
e0d2f60e-d3b5-5b9f-9889-05df7b99ea3f | note | Inspection / Test Method - Inspection
33450bc6-56e0-5517-9e6c-7b74f5b9af78 | note | Verification Records - Photos
3a2764f9-6a07-5c4f-b1da-3101aa848b44 | note | Standard - AS/NZS 4129
c01ebc01-e484-5161-be75-23a16de77c35 | note | Signatory - Site Engineer
4245c8a2-1450-44fd-80cf-93f885008a0c | checkpoint | D8.3, D8.4 - Lateral connection to house no#131 Wilton Street
63171d11-6d1f-57dc-b0af-65ccc83426cc | note | ACTION (W, M, H) - W
2c7d38e4-8005-58e1-b8bc-537f118930ee | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
5389fec8-d612-558f-ad17-21d32fb43dac | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
4736d50a-3c88-51a9-8ada-dcc3218553dd | note | Frequency - Per each connection
6c57320c-bc60-57aa-bff6-3870a0098cdf | note | Inspection / Test Method - Inspection
9e552c19-7d61-5840-a714-670e5fd9ec7e | note | Verification Records - Photos
2db8f4ac-f5e3-55f1-943d-81b1584b9f6d | note | Standard - AS/NZS 4129
1691ddb7-159f-5497-8d27-d6bca71b7f87 | note | Signatory - Site Engineer
f4646d3e-e310-4c94-a464-ea6c6a74b325 | checkpoint | D8.3, D8.4 - Lateral connection to house no#128 Wilton Street
b3b7c69b-869e-5b42-8970-91e767885fcc | note | ACTION (W, M, H) - W
11d7190a-07e7-5e97-aa59-d2aaa69425fe | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
bba3534f-14d9-51c8-8809-bcd3729dafdd | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
e2a40041-6aa1-5ca7-8e59-754baa781b93 | note | Frequency - Per each connection
c84048d7-dc01-531a-98d5-919bb703aa42 | note | Inspection / Test Method - Inspection
4069f8ad-5cba-53cb-8878-6b512f19be89 | note | Verification Records - Photos
29f32d29-ebf4-5700-8ffc-d8b562ba48e7 | note | Standard - AS/NZS 4129
9182918e-9dc0-59a3-abd8-351e84e86277 | note | Signatory - Site Engineer
733b9d5d-9e13-46e3-9342-09bcd20abc3a | checkpoint | D5.5 - Fire Hydrant WILTON FH01 at CH83 (1)
330dc345-969a-5e81-a97e-2ab2a2421ad9 | note | ACTION (W, M, H) - W
6b8ff571-89c4-5381-9730-30a2b068455e | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
d3d4c7e9-3843-55e0-89d0-5046b794de5b | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
41085bc9-8678-5b10-b676-27eeccccf95d | note | Frequency - Per each hydrant
5c94db74-5dc9-5293-8b04-f446ed1f2d47 | note | Inspection / Test Method - Inspection
b018c6cd-104d-5b2a-b1de-e5aeb9b4c379 | note | Verification Records - Photos
3f9e0820-955f-5347-8df2-b2f7068bd309 | note | Standard - NZS 4522
09b4365a-5eca-5b0d-8b1c-d5bcbffd6fa1 | note | Signatory - Site Engineer
608d540b-992e-4f9e-92b3-6d14571ced84 | checkpoint | D5.5 - Fire Hydrant WILTON FH01 at CH83 (2)
d305b09e-4d30-5fff-a631-51e8e9d5be3a | note | ACTION (W, M, H) - W
1bec8c9a-786f-5fd6-acef-3006cc298f1a | note | Conformance Criteria (What's Required) - Surface box finish
8518f578-06bf-529b-b782-dbd5d9cbe43c | note | Detail - cast iron valve box to be flush with the finished surface level.
d07df15c-0261-5e48-8bbb-b022880487a5 | note | Frequency - Per each hydrant
a12377aa-cb2d-55d1-b13b-fbce816988ef | note | Inspection / Test Method - Inspection
b4b9b8e5-91f7-5f7c-bfe9-2fdd0efbaf7a | note | Verification Records - Photos
ae6ce6a0-bffc-51d2-80ae-42714c858ba0 | note | Standard - NZS 4522
fddffa4c-b81a-5408-a86a-30181e69c85e | note | Signatory - Site Engineer
5276597f-f11b-42ec-81f8-dd2f4bf2a076 | checkpoint | D5.5 - Fire Hydrant WILTON FH01 at CH83 (3)
169c677f-e198-5b06-a6cf-9a06e60d4c1b | note | ACTION (W, M, H) - W
d3e51fd9-22c5-51c5-a988-94b8dbabb9a3 | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
4f220e05-a769-5c00-a265-5c08ef99150d | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
38cd2f68-3126-587a-a665-3a1c2c5208bf | note | Frequency - Per each hydrant
dac46a8e-ed8e-5f77-9575-fd203866d619 | note | Inspection / Test Method - Inspection
98cfc979-5c6a-5fcb-a5c4-23f20d3232f6 | note | Verification Records - Photos
d88f3ec4-d4fd-531f-93fb-046adf36a02b | note | Standard - NZS 4522
65f01eff-ab10-5928-8e93-f1632dad0b76 | note | Signatory - Site Engineer
1f2cdd63-12e7-49c5-82df-f72c4c980348 | checkpoint | D8.3, D8.4 - Lateral connection to house no#37 High Street
7e83bbbd-29e4-52e5-9d75-0131ab7311b0 | note | ACTION (W, M, H) - W
3759c296-9d86-5093-a45f-9339498275f5 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
9029c325-d907-5420-8ace-972df0414e45 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
1a88d399-c2ca-5c27-8328-dee7e7c6b6e3 | note | Frequency - Per each connection
cb3846cd-7df7-5ff5-9b14-a2e00674a9bf | note | Inspection / Test Method - Inspection
d8cd1e86-b235-562c-8819-e8ae952c2d13 | note | Verification Records - Photos
90047d5d-54f7-5251-a56e-f4be62ed1ac1 | note | Standard - AS/NZS 4129
e5d78a08-7958-54d3-abdd-f2431bf0ce9b | note | Signatory - Site Engineer
644faa85-1f58-4a78-be6f-96f771388b00 | checkpoint | D8.3, D8.4 - Lateral connection to house no#41 High Street
f1b11c1a-d8fe-5763-9d5e-c7636c2d89fd | note | ACTION (W, M, H) - W
9f932d37-f974-5bf2-ab2a-bccd53334aa9 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
32e0fa79-8e51-5e02-89ac-74d23896a36d | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
f498587c-27cd-5d71-a5e9-2c9fb7775536 | note | Frequency - Per each connection
1dd4dd18-8ae0-5bd6-931c-631db4e3d91d | note | Inspection / Test Method - Inspection
56d0473d-b55c-5886-b5dc-df19dab65565 | note | Verification Records - Photos
333534f2-03d2-5150-a784-f28bcea10441 | note | Standard - AS/NZS 4129
6cfdbe6f-dbc9-5149-ae4f-c46cc0d9a7e4 | note | Signatory - Site Engineer
f142cfde-290b-474c-9834-3a71c632c825 | checkpoint | Link in at intersection of Wilton Street and High Street (1)
dbba612e-7bf1-5f92-bb5a-f523fdc27aa2 | note | ACTION (W, M, H) - W
813d3002-bb94-5352-af35-9e7937fab3a8 | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
d1ddd945-68df-5501-b199-6224743286ca | note | Detail - PE to DI connection to be done as per the detail E in sheet 16 of the drawing
62e78a86-35f3-50e6-aa6e-1d80bee0d4f5 | note | Frequency - Before backfilling
0216c79b-d3f6-5354-bd21-a37e9d046611 | note | Inspection / Test Method - Inspection
0ce1bb10-ec72-5b41-81fd-0f21d0ef09dd | note | Verification Records - Photos
cb702bae-86c6-5251-a058-ca0992cc14f3 | note | Signatory - Site Engineer
627f303b-93fe-4878-9ea1-d057e73448a6 | checkpoint | Link in at intersection of Wilton Street and High Street (2)
1cf6b5f6-7183-5aba-9896-260b1a603257 | note | ACTION (W, M, H) - W
c71e0e23-2b6a-52ac-aa59-c58b544403eb | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x1)
f75ce460-7750-5924-8655-1a039d248ddb | note | Detail - As per detail E in sheet 16 and typical details as per sheet 18
cdd6ef5d-06da-50e3-8aad-25fd60c306e9 | note | Frequency - Before backfilling
9a7a16c8-416a-5fa4-8c30-9b1225aeba23 | note | Inspection / Test Method - Inspection
dbb6ad9e-65dc-5adb-8216-66bfed64beaf | note | Verification Records - Photos
c2888b9d-666d-5faf-a0ed-6f72f4b877e4 | note | Signatory - Site Engineer
d5f69ba4-b24d-4511-857e-343a9b9766b6 | checkpoint | Removal of existing cross and reinstated with straight through pipe at SW corner of Wilton Street and High Street
07d1e2be-2c12-59f1-9288-7a791bb13e1a | note | ACTION (W, M, H) - W
802444f2-1e88-55a3-a522-af11bc8e0c23 | note | Conformance Criteria (What's Required) - Pipe reinstated through old line and thrust protected
5c54d0f3-6e76-58b0-8af9-6cd8a4158a1d | note | Detail - As per typical details sheet 18
a37e7760-317c-5e3c-a45f-97de6fdf7d5d | note | Inspection / Test Method - Inspection
21ac6085-aaed-5608-8587-d0c3df24b7d7 | note | Verification Records - Photos
7a551114-3319-500a-bf09-b2de696fce92 | note | Standard - AS/NZS 4130
5778db7f-c275-56c8-8d3e-80eaef4d86e9 | note | Signatory - Site Engineer
986e37b5-4953-4d29-bbe6-5427021f0e91 | checkpoint | D5.4.2 - Isolation Valve WILTON-HIGH CH125 (1)
8e10df25-c565-5676-99af-40d7422022b1 | note | ACTION (W, M, H) - W
4e8ad943-c223-5ee1-8a7a-2b7be41bc150 | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
e0bc0620-f41f-5b3c-889a-962e0014ccb5 | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
9d86204a-5537-50cc-891f-28bb20ed8c45 | note | Frequency - Per each valve
9905ade5-ae47-55e9-aab9-15d3b6cb23ed | note | Inspection / Test Method - Inspection
81793e37-cd4b-58ee-89a2-52899ee98034 | note | Verification Records - Photos
bac8a810-4935-5597-84c6-0a8c6827087b | note | Signatory - Site Engineer
7cde4222-c993-47b3-8b2a-5510a187eb1e | checkpoint | D5.4.2 - Isolation Valve WILTON-HIGH CH125 (2)
862b07a9-3586-5103-a759-6795083b52a4 | note | ACTION (W, M, H) - W
0d487735-0137-58c6-ac76-130eadb14f8c | note | Conformance Criteria (What's Required) - Thrust wall installed
2bdd6a35-627a-52f2-8fe1-d3cf0a2c420f | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
a8ba7a01-b960-5345-975b-4bcc175ff0f3 | note | Frequency - Per each valve
6a131ba2-58cb-571f-b9aa-a51b9128b881 | note | Inspection / Test Method - Inspection
c8ebe581-6ecc-5c91-808d-441ef81a1068 | note | Verification Records - Photos
96fa0d64-a055-5bec-9a31-85e61726e927 | note | Signatory - Site Engineer
73e17d9f-089f-449b-bbc1-ca99e5fb74c6 | checkpoint | D5.4.2 - Isolation Valve WILTON-HIGH CH125 (3)
10ff0cc2-5844-5d7d-b0f2-8e87a8287927 | note | ACTION (W, M, H) - W
cf665e6c-40a2-5087-8a28-b4ecff24ce28 | note | Conformance Criteria (What's Required) - Surface box finish
3f8c25fe-7001-586c-90b1-9750921ace7b | note | Detail - cast iron valve box to be flush with the finished surface level.
9fa8f19d-f3fe-540d-8da2-8c840a3af72b | note | Frequency - Per each valve
5fa2d440-631f-5cc9-bb65-d067ac05a952 | note | Inspection / Test Method - Inspection
3d558934-a029-5d79-81f6-9bad84f1d9e5 | note | Verification Records - Photos
4c5abbe1-1f2d-57a1-8161-8ea11f4c7f53 | note | Signatory - Site Engineer
8169e511-9092-46b6-8184-019ccff370b0 | checkpoint | D8.3, D8.4 - Lateral connection to house no#40 High Street
d65cb942-ad0c-57ed-9425-5a4bf7eaa590 | note | ACTION (W, M, H) - W
200e1cfc-fb35-5c7a-a9e3-4d24c1b78946 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
d4cbb762-5bff-50c8-b684-4fd9b71313dc | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
7fd79790-fe5c-5465-849f-1113fb1b6679 | note | Frequency - Per each connection
61df9e6a-8aa2-5947-9a3b-cb14e63dee44 | note | Inspection / Test Method - Inspection
01168be9-b68b-539c-943e-d16641a394e3 | note | Verification Records - Photos
9150e96e-c905-5906-a5a6-eb8d217152a3 | note | Standard - AS/NZS 4129
8e81ef73-e4cd-5472-a950-388fbb9c49dd | note | Signatory - Site Engineer
3be5573b-fde2-4b08-b6b0-327857877882 | checkpoint | D8.3, D8.4 - Lateral connection to house no#143 Wilton Street
beb710b4-9e0e-5c98-9771-ceb7df88b581 | note | ACTION (W, M, H) - W
5c02c70f-a22f-5dae-87ed-1d2b54c251db | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
243f7ed5-cbeb-5743-835f-5eccf1ed6cc6 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
779df453-4602-519c-86a2-d48669c94262 | note | Frequency - Per each connection
d6ae668b-c7ca-58df-af26-00ddd0ea3ee0 | note | Inspection / Test Method - Inspection
3f323ed3-67c0-5b55-82ab-c4e074019ded | note | Verification Records - Photos
86555774-e6f3-5f9b-a96f-d97347f13583 | note | Standard - AS/NZS 4129
e2bd31c7-9fcd-5c97-b64b-6300d6f54778 | note | Signatory - Site Engineer
966f19f1-6677-4eaa-a023-a569d62692a2 | checkpoint | D8.3, D8.4 - Lateral connection to house no#147 Wilton Street
4c5f3c6b-673f-572e-b3e3-358ce01500d1 | note | ACTION (W, M, H) - W
8fb61cc5-3186-5c2f-bca5-530052f2f662 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
dff926ca-4542-5314-89bd-b6d0cad094c6 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
094b534b-ac64-513f-b55b-db4e7af96a45 | note | Frequency - Per each connection
a45fbed3-79a6-51df-adac-f51a5431aa94 | note | Inspection / Test Method - Inspection
d260336e-7d0e-5b66-a136-d7d34e0a097e | note | Verification Records - Photos
def1e517-eefb-58f0-aac6-3985edaa8ab5 | note | Standard - AS/NZS 4129
69d193b4-0ff4-59ff-91d6-519ab1fc1678 | note | Signatory - Site Engineer
bae45831-e336-408a-b907-83bad3ec296a | checkpoint | D5.5 - Fire Hydrant WILTON FH02 at CH179 (1)
6e2b9e47-9754-5a74-8195-41908cdec3f5 | note | ACTION (W, M, H) - W
c86c4d2e-d29d-572a-bffe-56676f283b74 | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
ebbe8e58-25e5-50de-8d5e-c39dfbcd5693 | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
5d5eb0f1-ba38-508c-8532-1be5c37a58b7 | note | Frequency - Per each hydrant
06458ffa-975f-54af-9d25-1758f58375e7 | note | Inspection / Test Method - Inspection
597534ca-18ab-5329-9442-426de502e977 | note | Verification Records - Photos
1b4d6c0d-f7d0-5c51-b51f-27b458dbd007 | note | Standard - NZS 4522
62f1ba72-2c76-579c-b984-5f3a8bc4cfd9 | note | Signatory - Site Engineer
c9426246-793c-4a35-a84a-b9f9aa03b712 | checkpoint | D5.5 - Fire Hydrant WILTON FH02 at CH179 (2)
b89c1647-0098-5c17-bc3d-27b975f6b7be | note | ACTION (W, M, H) - W
c8013466-b972-5111-a0ac-e8046b3045a5 | note | Conformance Criteria (What's Required) - Surface box finish
cfe4d600-22c6-56ee-935a-52993fbac017 | note | Detail - cast iron valve box to be flush with the finished surface level.
860aebcd-b4c3-5df1-b5d0-e1b513e83051 | note | Frequency - Per each hydrant
e72e8dfc-766a-58a1-9f3c-cf6eecafd756 | note | Inspection / Test Method - Inspection
1347ef1f-4aee-5c30-b2fd-3393aa72cb3e | note | Verification Records - Photos
83059d95-3723-585a-b888-19e1df9a98b1 | note | Standard - NZS 4522
8deffdee-f52d-5123-a2ee-9935b1ba410f | note | Signatory - Site Engineer
b6756954-b999-4668-a59a-4420ae35000c | checkpoint | D5.5 - Fire Hydrant WILTON FH02 at CH179 (3)
3454aaf6-bf6c-583b-93ae-1f53759b0bd7 | note | ACTION (W, M, H) - W
cd49321f-9417-5796-9584-58cabfaeda7f | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
a8bc74ab-4710-54f1-8223-2ba441e95b79 | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
a0c4184b-d488-5019-8027-ca3d1b074001 | note | Frequency - Per each hydrant
3aea6d82-0ae8-5916-88c7-3df40f9082d1 | note | Inspection / Test Method - Inspection
c1d67f2f-8414-53cd-9afd-9b49c0e85049 | note | Verification Records - Photos
c0d8f0d3-6212-53c5-874c-3385ad417bf2 | note | Standard - NZS 4522
be47703a-5412-591e-94c4-afa175abe8f7 | note | Signatory - Site Engineer
0f49d556-f1de-442d-b168-bd00ba909603 | checkpoint | D8.3, D8.4 - Lateral connection to house no#150 Wilton Street
4dab7268-5d0e-5608-a114-345f4b5306d5 | note | ACTION (W, M, H) - W
7edd9d32-f0f8-5f59-8b92-40d34bbfe0dc | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
4c0e2b09-88f6-53f2-a069-24f009e6d67e | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
f76e44f0-2e93-5727-b835-653a8ce77617 | note | Frequency - Per each connection
85491daf-eef0-513a-94e7-611ab866c9ac | note | Inspection / Test Method - Inspection
a9c2745b-641f-56ef-8e8c-9c1083d9fdee | note | Verification Records - Photos
228fb08f-90be-5539-b5b2-a58c64ad9c30 | note | Standard - AS/NZS 4129
b5221152-3362-5aac-868c-8d1384ca13b3 | note | Signatory - Site Engineer
198d1c98-473e-4e42-803c-19fed6262b21 | checkpoint | D8.3, D8.4 - Lateral connection to house no#149 Wilton Street
d9828022-e176-52a2-b22d-c237e9caa0ce | note | ACTION (W, M, H) - W
704b976e-92bc-520f-ac07-e0bd6bfe7e42 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
b7ec5b05-8ebd-54e6-a601-ba29ef7e71d6 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
a9d39eae-d39d-51d3-b8e5-f06cdb091837 | note | Frequency - Per each connection
d4f6c9f5-0114-58bb-be40-70015a8132bd | note | Inspection / Test Method - Inspection
6dc1e197-cedf-578b-963c-27f526b2c767 | note | Verification Records - Photos
6de76271-be63-579d-8184-4093f9d71264 | note | Standard - AS/NZS 4129
8868a84c-8b99-58ea-b8f8-a656f14e5117 | note | Signatory - Site Engineer
2b180810-6640-4596-9dcd-1395d41573da | checkpoint | Link in at intersection of Wilton Street andTerrace Street (1)
26ec874b-c92a-5f2e-81bc-4054f11cc625 | note | ACTION (W, M, H) - W
7e0dd442-0e71-53b8-9891-fc07589472fe | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
475d8c50-a01c-59c3-afe1-490e2aff51ce | note | Detail - PE to DI connection to be done as per the detail F in sheet 16 of the drawing
c6ae8635-fe94-5023-99a7-2612def7727e | note | Frequency - Before backfilling
d785a37e-f3fa-5779-a53f-7c906ab06e48 | note | Inspection / Test Method - Inspection
025458ea-eac9-5326-89e1-87f198f669a3 | note | Verification Records - Photos
b7380092-55aa-5605-b03f-2ba3fde63ebf | note | Signatory - Site Engineer
c99da230-e9a1-4165-b921-79fb3b5da7ac | checkpoint | Link in at intersection of Wilton Street andTerrace Street (2)
37aaeb7c-29a3-5726-be90-8ff132e8381f | note | ACTION (W, M, H) - W
45a3643e-0e20-55dc-853e-d35b500be892 | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x1)
97b49562-044c-5755-abdb-4f71610a51d1 | note | Detail - As per detail F in sheet 16 and typical details as per sheet 18
7dca37f3-192a-5d93-bfe2-f8c8199d4f6a | note | Frequency - Before backfilling
f8a3032a-cba7-51a0-bc4e-4f8a3fec10a1 | note | Inspection / Test Method - Inspection
b68a8a82-4c50-5799-8389-dbaff371536c | note | Verification Records - Photos
22fff634-3c31-54ff-9e95-339fc3a20918 | note | Signatory - Site Engineer
a0011df6-2c6f-464e-82c9-d85b58f7135d | checkpoint | Removal of existing tees (2) and reinstated with straight through pipe and associated bends/thrust protection at SW corner of Wilton Street and High Street
e1061695-a363-54ce-97f8-8d1bb1801f0b | note | ACTION (W, M, H) - W
0818ab4f-f7f4-5b3d-aac7-d65268c39265 | note | Conformance Criteria (What's Required) - Pipe reinstated through old line and thrust protected
8663496a-d6b5-5af2-900f-7b4c0adaf8b8 | note | Detail - As per detail L in sheet 16 and typical details sheet 18
70a96bff-0875-5dd6-b59f-766ad277ee70 | note | Frequency - per connection
702639d0-b545-57ed-a633-d4f8860b039a | note | Inspection / Test Method - Inspection
29fa7776-40d0-5303-b70b-0cf61ed048ba | note | Verification Records - Photos
6f024f17-836e-5c56-9352-1ea5e2f51072 | note | Standard - AS/NZS 4130
8abca253-a8b5-57e7-819c-799ef16e1b87 | note | Signatory - Site Engineer
c50810b3-cb65-4319-9e2b-d35b6bbd4f82 | checkpoint | D5.4.2 - Isolation Valve WILTON-TERRACE CH235 (1)
64e15f5b-71c1-5234-aee3-7da5e4205275 | note | ACTION (W, M, H) - W
b7b2a368-b38c-5a84-b68e-7bb20d550a28 | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
870cf3c7-86c5-5bec-a75a-917f19d59855 | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
b2aeec26-2038-562d-8adf-d0f9c9457ba0 | note | Frequency - Per each valve
c2029903-d6da-5c32-bd61-9f611dfe1341 | note | Inspection / Test Method - Inspection
1638900d-9dd0-520e-a04e-115e9fb668ee | note | Verification Records - Photos
f9bc41e3-7aa0-503c-a192-db91301c1ca0 | note | Signatory - Site Engineer
ae4c7472-8909-4d53-bb15-30844977ebb2 | checkpoint | D5.4.2 - Isolation Valve WILTON-TERRACE CH235 (2)
d4b5a6f3-fe58-50ba-b926-290a24147013 | note | ACTION (W, M, H) - W
d6701206-1d1b-5494-975c-b2ec57495f4a | note | Conformance Criteria (What's Required) - Thrust wall installed
5dbb666c-4135-5a61-8909-e874675484ec | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
46c4b7f6-9742-5f0c-9ddf-4dc7a69a8baa | note | Frequency - Per each valve
0ed194fb-21d1-53e6-8786-351166d17bde | note | Inspection / Test Method - Inspection
06215b1f-0240-58e9-b658-664a7edb260f | note | Verification Records - Photos
8d8fbef0-8051-548d-8faf-94cefe2cd550 | note | Signatory - Site Engineer
bc0e1d89-f8da-4219-a383-739e33b9cae3 | checkpoint | D5.4.2 - Isolation Valve WILTON-TERRACE CH235 (3)
3121ebe3-51ea-5db1-9be5-21116934e03a | note | ACTION (W, M, H) - W
fe28562a-8dc1-521a-bb1e-1fdb9b7d26f3 | note | Conformance Criteria (What's Required) - Surface box finish
41ed8b0a-9975-5750-8f6f-f2158d3bd86b | note | Detail - cast iron valve box to be flush with the finished surface level.
f73d8cb0-40e9-5efb-a9e9-c6683c70e004 | note | Frequency - Per each valve
fe340e19-0626-5208-a2ed-ecc096832ed0 | note | Inspection / Test Method - Inspection
d79839a0-605b-551e-aefa-2b0cedd792ba | note | Verification Records - Photos
3c121c0f-2a27-5b67-b125-5a35c67e0e05 | note | Signatory - Site Engineer
cf258c09-e28e-4517-8d23-8ee5f70bbc4e | checkpoint | D8.3, D8.4 - Lateral connection to house no#159 Wilton Street
bbfbf17a-291a-5523-afb9-0fa5a7039fc2 | note | ACTION (W, M, H) - W
fd644122-3c41-53d4-97d3-46df73a352c0 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
a4c120bb-5521-5f13-96fd-21a8dc15e2d5 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
5bf9fbfd-9929-5fe9-a07b-494aede6b2d3 | note | Frequency - Per each connection
ee5e0f2f-4558-5035-8b76-e84cf0f3d5e7 | note | Inspection / Test Method - Inspection
9d4b1f28-826d-5b13-b94b-4749f15d0dce | note | Verification Records - Photos
427dacf5-afd0-571b-b42b-8423eef623d4 | note | Standard - AS/NZS 4129
9df0d0c1-93f9-534b-b463-24e3f406bd6c | note | Signatory - Site Engineer
4c7822a3-67b9-454b-96e6-3cb3a36c419c | checkpoint | D8.3, D8.4 - Lateral connection to house no#162 Wilton Street
66db62e8-e57a-5314-8f04-f6fbe3d972bf | note | ACTION (W, M, H) - W
45fe0544-61e2-541f-9726-ef3be42402fc | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
993dbe60-3c92-5343-b2ec-db68105b4d51 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
96b645dd-4f1f-586a-b2f1-5b1dddfe2f68 | note | Frequency - Per each connection
9d1fe641-8ace-523a-be08-b05fadcc62f0 | note | Inspection / Test Method - Inspection
b3b3dc05-2888-577a-9dde-91309ff7d96d | note | Verification Records - Photos
c1a60a68-c57f-59a4-ab49-9eb8d5673286 | note | Standard - AS/NZS 4129
1f9f7fc9-ce4c-514b-ae86-1f49851184f2 | note | Signatory - Site Engineer
2b62e516-2c23-41db-8d7f-939a007ab4ba | checkpoint | D8.3, D8.4 - Lateral connection to house no#166 Wilton Street
2d90c7ac-63fb-5fc8-80b9-c16d4f5f4372 | note | ACTION (W, M, H) - W
130aa534-65a4-5698-9c43-b1e6dea93f7a | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
2f249314-164d-5645-a7bd-f684c98118f7 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
df62196b-66e2-5f4f-84b9-14ff04a4c8d3 | note | Frequency - Per each connection
27d2a71e-8846-5761-beb3-6248ef686dbf | note | Inspection / Test Method - Inspection
c04b2e24-cbc8-5914-b590-faa5664c00bb | note | Verification Records - Photos
15e80f1c-f93a-5d06-be67-b590b31b86e6 | note | Standard - AS/NZS 4129
6dca7a81-87f7-58f0-862a-f5e816c4854c | note | Signatory - Site Engineer
36b2b3c9-ebc7-403a-9f80-66b92b256017 | checkpoint | D8.3, D8.4 - Lateral connection to house no#165 Wilton Street
75bb83cf-e8f8-52f6-a0d0-4f541375f79d | note | ACTION (W, M, H) - W
4722d70e-df6e-5d86-817c-93c5d042f3e6 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
40284275-99f2-54e1-a7f9-b960c32443b4 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
724279c9-d77c-57c3-802c-5a3f710675e4 | note | Frequency - Per each connection
40bcfe99-f1fa-5521-8e0f-52315a32fe71 | note | Inspection / Test Method - Inspection
8dcca77c-32dc-57b5-bd22-2c27b59bb260 | note | Verification Records - Photos
b5350d84-dc44-51d5-b018-bc6fb251c136 | note | Standard - AS/NZS 4129
cac489d3-d575-5a7c-ab28-6683291c03ec | note | Signatory - Site Engineer
ae6d1efa-ce6f-4382-ab05-ba62d0107e80 | checkpoint | D5.5 - Fire Hydrant WILTON FH03 at CH294 (1)
a44e8563-9837-5181-98f2-d250dd6833ad | note | ACTION (W, M, H) - W
709e54f7-5d63-5a33-acde-f8806c7914aa | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
cfbbb557-afeb-554d-bce0-16be546a1d51 | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
91448953-209e-555b-b4f6-6b9685fb2215 | note | Frequency - Per each hydrant
04f337bb-f9cf-5b76-b719-39e0c92a9b0f | note | Inspection / Test Method - Inspection
2ed90a7a-86c5-5700-985b-bd70bbb06e5c | note | Verification Records - Photos
207df5ad-07db-5b29-9c2a-5c89a584fd41 | note | Standard - NZS 4522
14d5232d-f497-50f1-813e-d785d145e06f | note | Signatory - Site Engineer
0289c0d3-ea29-4f7e-b919-459eab1e31b3 | checkpoint | D5.5 - Fire Hydrant WILTON FH03 at CH294 (2)
548eeffa-7956-54e1-9915-2d002dddf665 | note | ACTION (W, M, H) - W
30882fc7-c84f-5364-85fe-3c3c3f76b492 | note | Conformance Criteria (What's Required) - Surface box finish
3959af35-4d5f-5393-8498-6961a42b323e | note | Detail - cast iron valve box to be flush with the finished surface level.
6fd8f676-ce72-52f8-8c05-aa90d9af68ed | note | Frequency - Per each hydrant
4c93b392-897e-56e4-9af9-022cca77ca6e | note | Inspection / Test Method - Inspection
267afd04-70d6-5707-a676-b9b78a47542d | note | Verification Records - Photos
ae4c6349-0577-5460-a69b-8f37bc0a89c0 | note | Standard - NZS 4522
0083c265-b4bd-5dc4-9688-9d1ab1ff177e | note | Signatory - Site Engineer
f0bc2184-05e7-49a5-a76d-bde6b2ae8e91 | checkpoint | D5.5 - Fire Hydrant WILTON FH03 at CH294 (3)
bccd84b1-c3e0-5f4e-b2e9-c223c3a46b25 | note | ACTION (W, M, H) - W
2dc2a60f-b518-5151-b75a-56c3e9db8a0e | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
4476bc79-84b0-54a0-9732-fc875d03c101 | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
94b02ccf-532b-5ddc-aecb-ac9bbf9702ea | note | Frequency - Per each hydrant
fa1a132c-2717-5c1b-9ea8-f8a820edd18f | note | Inspection / Test Method - Inspection
c9a6137d-9d28-5a87-81e2-8671f9f51729 | note | Verification Records - Photos
e77721ca-b1fd-590d-b41b-a902c0448f3e | note | Standard - NZS 4522
2bc6f1c0-e948-5709-a78a-0d75d12b5415 | note | Signatory - Site Engineer
f622b8f2-eb5b-41e3-8590-ec8cecdef034 | checkpoint | D8.3, D8.4 - Lateral connection to house no#167 Wilton Street
3e70159b-0df3-566d-9874-9214e0f9dd68 | note | ACTION (W, M, H) - W
c3575635-1271-52f8-b34e-b64402fece06 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
ed853605-0895-584b-988d-b05540d05814 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
d62ef22e-fc97-5d1c-ada0-04a13aae7dc1 | note | Frequency - Per each connection
7f1555b3-a38e-5221-8599-91a3e63b960d | note | Inspection / Test Method - Inspection
1e5fc8fd-a4ac-59cd-99dd-0a49f0b2b0c4 | note | Verification Records - Photos
128e3838-1229-5581-bd03-5b5a0004bdd0 | note | Standard - AS/NZS 4129
2768d53d-a5cf-5be0-a1a4-d536736f2f34 | note | Signatory - Site Engineer
4408cd36-cfbb-4e68-bdd2-97d3d550a17b | checkpoint | D8.3, D8.4 - Lateral connection to house no#170 Wilton Street
d5e98dec-822e-535e-8faa-49ceea557d89 | note | ACTION (W, M, H) - W
0f075d01-c1c2-5db7-9887-4973d01f690d | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
a5a670be-783f-5b1d-8027-e5971cc35043 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
926902d3-0408-5239-b9c0-d21c6a876e09 | note | Frequency - Per each connection
ec635984-b081-5f13-9b38-02dbf19a0bd1 | note | Inspection / Test Method - Inspection
20cce658-4969-5d0b-9d47-5c3ce43833e5 | note | Verification Records - Photos
8e3bb8d0-a62e-5964-ad5e-bf7e10fb9ac7 | note | Standard - AS/NZS 4129
09c02502-35db-5e72-968b-8e39cb894a56 | note | Signatory - Site Engineer
b7164b4a-1c33-4608-9c49-cd3ce941b8ac | checkpoint | D8.3, D8.4 - Lateral connection to house no#175 Wilton Street
0f04034d-e623-578e-b137-5ad814d4bdc0 | note | ACTION (W, M, H) - W
6e150d32-922a-52eb-8f63-ec7e7d63f349 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
5393f078-7449-59b7-9838-9ad4ec46444e | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
cc0c7bb3-bbc1-56ff-8a95-b05c924b4988 | note | Frequency - Per each connection
d0e7d3e6-edad-5dd3-802b-42a86e353ed4 | note | Inspection / Test Method - Inspection
bff9091e-b8df-5a5a-8a96-ccf409d8da41 | note | Verification Records - Photos
73546c3d-b96a-5d9a-908f-00c53dd01a46 | note | Standard - AS/NZS 4129
f05f09e8-dc6b-591f-8f0a-899abcfb5f07 | note | Signatory - Site Engineer
79f50c1a-abe8-4673-8aa8-0d22a881ee46 | checkpoint | Link in at intersection of Wilton Street and Lamond Street West (1)
9ae80080-5037-53a4-90f2-ce43aea85f7f | note | ACTION (W, M, H) - W
9545d8d2-65ed-5ab8-b069-3ddcb93e828c | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
81d88624-a9ab-5c36-bcc6-d8fa59aed49c | note | Detail - PE to DI connection to be done as per the detail G in sheet 16 of the drawing
6e05f09f-53eb-5104-bd7e-f6125a59bfc8 | note | Frequency - Before backfilling
515ae915-9879-5b5d-899d-55d024bd8268 | note | Inspection / Test Method - Inspection
bbbc9f2a-a0ef-5dba-9b86-f901a161236b | note | Verification Records - Photos
b1c6898e-c442-5980-a086-4d4aa77f9611 | note | Signatory - Site Engineer
6546cf63-d0e8-4b44-be77-2fe5dd105f40 | checkpoint | Link in at intersection of Wilton Street and Lamond Street West (2)
4032085b-aee8-55f5-8bd5-3b267eea86ac | note | ACTION (W, M, H) - W
b5e44318-2271-513e-aff4-7be2d6300d69 | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
7d8f4685-5095-5739-aff2-967757d647c9 | note | Detail - As per detail G in sheet 16 and typical details as per sheet 18
85a9b49f-8a6a-5963-954c-d9a30ffd3bd2 | note | Frequency - Before backfilling
0e244931-6a79-5b23-b829-bf1976ebfb48 | note | Inspection / Test Method - Inspection
a06d02c9-e059-59b6-8c67-4450b45f4043 | note | Verification Records - Photos
d0c82dc6-58b6-5298-831e-29547ed17f3d | note | Signatory - Site Engineer
8142a4b4-e85e-4948-8f01-61adc025b8cb | checkpoint | D5.4.2 - Isolation Valve LAMOND-WILTON (1)
a382dc25-14f0-59d8-975e-705fc1894a84 | note | ACTION (W, M, H) - W
8f68ed58-d2b8-50b9-afab-9635b21c7c05 | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
42185d2d-91be-5ab6-bede-aacb63a1fcd2 | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
737a1e2c-f0c7-55d0-8583-d4be78d40a47 | note | Frequency - Per each valve
5ea3ab4b-7a1d-5a26-a87d-66564e3c2d3d | note | Inspection / Test Method - Inspection
40af59a9-c373-547c-b9df-f535b7813c3b | note | Verification Records - Photos
2373eeba-9f75-5b50-8dfc-a3ba9b24280c | note | Signatory - Site Engineer
f3814a58-60f1-4cf1-a7dc-0f9fdb2ca12a | checkpoint | D5.4.2 - Isolation Valve LAMOND-WILTON (2)
53992e20-e792-5f96-88c3-2539759fba1a | note | ACTION (W, M, H) - W
f993625b-461d-5dba-9539-c291aad8a2c5 | note | Conformance Criteria (What's Required) - Thrust wall installed
fb252d29-6c38-5d50-ad82-b55e0cfb7c3d | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
d568892c-6641-5643-acce-3f61ba2e4180 | note | Frequency - Per each valve
7d9870d1-f9e2-5fd9-a34f-2ac231c0ded8 | note | Inspection / Test Method - Inspection
4e9ed2c4-937a-5e56-9629-4993b091af7f | note | Verification Records - Photos
09059da0-3b37-521b-91f3-a4cb2a74f983 | note | Signatory - Site Engineer
a656588a-a4e6-44ff-9f61-c726c37cd4ce | checkpoint | D5.4.2 - Isolation Valve LAMOND-WILTON (3)
d9fe1527-e11d-5b7b-a621-fa0300d9543f | note | ACTION (W, M, H) - W
307379c0-54c5-5f4e-878e-5a8a67c9a033 | note | Conformance Criteria (What's Required) - Surface box finish
f56d35bf-d356-574b-ac2c-9198551f2d10 | note | Detail - cast iron valve box to be flush with the finished surface level.
0e078a26-d096-58c7-be51-23a32f6c0d81 | note | Frequency - Per each valve
6212865a-899a-542d-b354-0cf62cb0ab2b | note | Inspection / Test Method - Inspection
11cae210-9b5b-591f-aa6f-e986d6d421e2 | note | Verification Records - Photos
064550fe-e075-5a63-b1a6-291b007083fb | note | Signatory - Site Engineer
383f3d53-6b16-4579-b8f8-5d370b967738 | checkpoint | D8.3, D8.4 - Lateral connection to house no#177 Wilton Street
07739855-2818-552d-b04d-d146e358201a | note | ACTION (W, M, H) - W
c6e9e677-d240-5ffa-8e72-4a11799d51f8 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
1520ff82-cf82-5b00-9461-2b355f9014de | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
383ad9b7-e8e5-5466-9ed3-6c937a71a115 | note | Frequency - Per each connection
f6ada87e-f7cd-52d0-97a5-89017159d709 | note | Inspection / Test Method - Inspection
25a15448-0829-557b-bdfe-d85c3d2fc5a9 | note | Verification Records - Photos
f219a708-9da2-5e1a-91b7-0c612802c112 | note | Standard - AS/NZS 4129
a2b1e3b9-cba1-5684-898a-b58bd8605178 | note | Signatory - Site Engineer
fcc2f84c-7c3e-4e7e-a5ef-101f0aa58568 | checkpoint | D5.4.2 - Isolation Valve WILTON-LAMOND CH347 (1)
07c47061-45b3-5d46-a058-8d6e70b76208 | note | ACTION (W, M, H) - W
ffdaa9bd-68d8-5ca9-8fff-89b54e90e55e | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
4dcfabec-113f-5474-a067-42fc70144ae6 | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
7a6dbf70-828b-5396-88bd-2c49bc069b96 | note | Frequency - Per each valve
e9dda532-2700-548d-bb19-90a32c2a6a43 | note | Inspection / Test Method - Inspection
6b264677-69f1-5090-b47f-722bc3bcf021 | note | Verification Records - Photos
38fb7f74-a0c1-50b7-a6b4-b9686b1719e6 | note | Signatory - Site Engineer
0fe10a73-e4e2-4a66-9419-ce4b0b25976e | checkpoint | D5.4.2 - Isolation Valve WILTON-LAMOND CH347 (2)
cf2dc6f9-45cc-54e8-8651-50ff8bc87566 | note | ACTION (W, M, H) - W
97e853fa-bb6c-5038-955f-4b183c00b0be | note | Conformance Criteria (What's Required) - Thrust wall installed
9718d1a5-d7ca-56ed-9155-7c18a8a85a56 | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
13937348-dd9a-50cd-9aea-a034038a6798 | note | Frequency - Per each valve
a644f72f-2ba4-5e7d-a7fa-0705d8ae1348 | note | Inspection / Test Method - Inspection
9c246c7f-86af-5f48-b4b3-2b316358a872 | note | Verification Records - Photos
708ee691-8700-5b3b-ba5c-cc5b028c41f3 | note | Signatory - Site Engineer
33c1e093-5c9c-49d9-a414-c50f0efab933 | checkpoint | D5.4.2 - Isolation Valve WILTON-LAMOND CH347 (3)
91973091-755e-5179-a774-6c5d09238a49 | note | ACTION (W, M, H) - W
d93f8182-66a8-5146-bf10-ab50814c56dd | note | Conformance Criteria (What's Required) - Surface box finish
7e862104-86a0-5562-8e62-d20f298b47a1 | note | Detail - cast iron valve box to be flush with the finished surface level.
60e27486-ded9-527c-8116-25fddbc32071 | note | Frequency - Per each valve
1052e177-f002-5468-b9e1-40cdc67bfe1c | note | Inspection / Test Method - Inspection
f8660da0-0d0d-5375-9259-bca908e5cd4b | note | Verification Records - Photos
8d757b7c-2adf-55df-a9d3-09b32eeb195e | note | Signatory - Site Engineer
077f7445-1ee4-49b6-90e2-bf044c45b80d | checkpoint | D8.3, D8.4 - Lateral connection to house no#180 Wilton Street
1940b44c-73e0-58de-b24b-72d707a5daea | note | ACTION (W, M, H) - W
72277005-ea31-5eed-bc1a-40098ea77a61 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
d515a518-3d1c-5b54-86f7-bbefc346c01d | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
9d04c2e2-5adb-57c6-8f93-edf70a94a29f | note | Frequency - Per each connection
65dc91c3-9968-5d1e-8e34-647ce2872e78 | note | Inspection / Test Method - Inspection
60c58137-594e-5c0c-a5ce-97ae8675e1d5 | note | Verification Records - Photos
ba6eb388-dbbb-5b64-a265-977e6d0d712d | note | Standard - AS/NZS 4129
8045076d-a738-59a9-8d03-ff971f580256 | note | Signatory - Site Engineer
5d77c708-4670-42c0-acf9-298bd5e45510 | checkpoint | D8.3, D8.4 - Lateral connection to house no#181 Wilton Street
480cbefa-f746-5180-9b8f-0cfc66e51eb8 | note | ACTION (W, M, H) - W
5162ffc9-6307-5bb0-b204-140dca8ac845 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
35d12261-665c-56d5-8389-4eab4e27796f | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
12b2c96d-28ab-543b-a2b1-ff0b12a01df2 | note | Frequency - Per each connection
2606e48b-fef1-5899-b217-cb1cd0184607 | note | Inspection / Test Method - Inspection
5342d23d-8145-5b7d-b88c-1a60740d50b9 | note | Verification Records - Photos
8edbd15c-5f70-5960-a88f-8303a14cb00d | note | Standard - AS/NZS 4129
d1f87ee3-9537-5689-a8ad-578e30e37d97 | note | Signatory - Site Engineer
f4183bc4-fd71-4286-9255-dfd32361700f | checkpoint | D8.3, D8.4 - Lateral connection to house no#184 Wilton Street
66ca808f-5a24-56d3-ad7d-860bc85a04ca | note | ACTION (W, M, H) - W
e258250d-f332-50e1-91dd-42a8ee043693 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
664f806a-3041-55f0-bd7f-d9716847dbc6 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
8f06909e-ab78-5b8f-af6d-742383049e59 | note | Frequency - Per each connection
44a8cb2b-11cb-590f-931b-1bec26b2b80b | note | Inspection / Test Method - Inspection
7671069c-c78b-5bd0-891f-ae4e06e22f48 | note | Verification Records - Photos
7201f9c3-4de5-5182-971c-a568de5ff784 | note | Standard - AS/NZS 4129
34f18774-dfbf-58a4-94e5-b0a053861ee2 | note | Signatory - Site Engineer
b54e7fda-b5b8-489f-9dfa-cc6219d9b03d | checkpoint | D5.5 - Fire Hydrant WILTON FH04 at CH387 (1)
dbf4cb7c-3052-59c3-a834-61b7306efde3 | note | ACTION (W, M, H) - W
179c1d16-4976-5634-9f2e-05db1ff5714c | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
97a80fd2-a213-5be3-8eaa-a2d7e6f48985 | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
cad73214-6598-57f9-a9c9-f424690d59fb | note | Frequency - Per each hydrant
4a057c88-e593-5b86-b5c5-4ed59a490e6a | note | Inspection / Test Method - Inspection
5e796ec7-94ed-5faf-9729-032cc24ee1f1 | note | Verification Records - Photos
cca51e05-91c6-5563-b695-c56a0c9e5a71 | note | Standard - NZS 4522
2372e7b9-d22c-5fac-b1ce-3ad2053bf442 | note | Signatory - Site Engineer
cb32e838-4bd4-44ec-93f8-61ca78879d17 | checkpoint | D5.5 - Fire Hydrant WILTON FH04 at CH387 (2)
c3eaae88-fed3-5cac-8dd4-3d04e14b6e95 | note | ACTION (W, M, H) - W
8fd72c59-d1b2-5452-bdf3-716d9ae0d29c | note | Conformance Criteria (What's Required) - Surface box finish
9d85e098-4088-5c1c-bc6a-d49fcc6dfe20 | note | Detail - cast iron valve box to be flush with the finished surface level.
2d66de29-48fb-57e5-a3ad-d30b63b5efd8 | note | Frequency - Per each hydrant
7adcb454-1d90-5829-9aa7-54f480bcc520 | note | Inspection / Test Method - Inspection
00b2b325-a3b7-5d2f-98a3-784574297801 | note | Verification Records - Photos
e5b4371f-c1a5-59d5-9777-9dbfdb704c39 | note | Standard - NZS 4522
d1e43fea-29d3-51bf-bad7-6ce2fc5ea886 | note | Signatory - Site Engineer
d5235de7-3d86-4876-a2f9-26b0f279f796 | checkpoint | D5.5 - Fire Hydrant WILTON FH04 at CH387 (3)
a0cd7b18-28ca-50f8-bd6b-b3c6b2093c39 | note | ACTION (W, M, H) - W
0a49c882-3ea9-5ce8-a07e-a5946e0f77d6 | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
4658935b-8875-5c0b-90eb-58e1a8bfb70c | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
0f8ff73d-09d0-5e71-ad6a-f4b3d46a0aca | note | Frequency - Per each hydrant
d038b333-8c34-531a-bbc0-153271d330bf | note | Inspection / Test Method - Inspection
0bc2d160-2aa2-563f-a3d5-5b94f9795314 | note | Verification Records - Photos
3e16e298-9104-55f2-b463-97ede60755cd | note | Standard - NZS 4522
28fb6bbe-9aed-5f2b-a9f6-67944aea55c6 | note | Signatory - Site Engineer
b07beacd-83f1-4009-bea2-8784472149fd | checkpoint | D8.3, D8.4 - Lateral connection to house no#185 Wilton Street
27e1af27-63fc-5f67-a780-230765be0bef | note | ACTION (W, M, H) - W
55238fbe-f081-575d-94ac-bd7448e349e8 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
519cb310-c5bf-5e1b-9abe-c07704c831e8 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
0c695225-f2d3-52be-b2b2-ee94d9ff16b2 | note | Frequency - Per each connection
2b7a4115-47c8-5d4a-a384-1e5272b482a1 | note | Inspection / Test Method - Inspection
c08b1c52-73be-5623-ac74-3ce9a14befbe | note | Verification Records - Photos
c2371bfc-aba5-575f-8ad9-fdfa47add232 | note | Standard - AS/NZS 4129
f9ce6424-612b-5cbd-a9e3-3339658594d5 | note | Signatory - Site Engineer
1b518844-0904-4f19-8759-93b812dd87ee | checkpoint | D8.3, D8.4 - Lateral connection to house no#188 Wilton Street
654bdcdf-4319-508d-86cd-cfd85a92cea8 | note | ACTION (W, M, H) - W
af90ff5a-b81e-58d2-8cdb-5608d3aa3794 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
47bef714-4492-5ba4-8a85-f0c74fec15fb | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
7eeff17b-721d-5d22-a67b-122588de719e | note | Frequency - Per each connection
3a022de0-5cab-5e85-bbf2-597f5a3be527 | note | Inspection / Test Method - Inspection
2375a04c-da6e-556c-9232-50e3e9d7f3c1 | note | Verification Records - Photos
b44fbc0d-1a85-556f-9b9d-8e2338a98544 | note | Standard - AS/NZS 4129
26e60fe1-738f-57b4-aa34-1715b20aa671 | note | Signatory - Site Engineer
f32215a8-65c7-43ae-bc6a-4cf1eb9dcee9 | checkpoint | D8.3, D8.4 - Lateral connection to house no#189 Wilton Street
15a7346b-531d-549a-b1e0-27456c207872 | note | ACTION (W, M, H) - W
61034514-cd31-5c66-9c9d-5b9ecd695680 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
9f783922-04f1-59d3-9042-1fe1a09511ea | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
be61023b-c7bb-5e03-8720-3b5ec63355ef | note | Frequency - Per each connection
d73b8e0c-9630-5b84-871c-a27bd15a725a | note | Inspection / Test Method - Inspection
2b369770-c7d3-573e-acb7-cecd254b9244 | note | Verification Records - Photos
f92dd839-ece1-591b-8feb-f1a85c7fb971 | note | Standard - AS/NZS 4129
c132a016-1e12-526b-a29e-2a5a5de5b55e | note | Signatory - Site Engineer
fe183009-304e-449b-85ed-d9e0a2615f2e | checkpoint | D8.3, D8.4 - Lateral connection to house no#133 Moana Street
2f9bd977-72bd-54bd-ab5e-728b168117bd | note | ACTION (W, M, H) - W
cc55f893-355f-5f3f-9074-06f57dba4f28 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
ae9101fe-c167-5f2e-b618-d8f42d94e510 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
656baab9-708e-5122-aaba-2f21de0fec3a | note | Frequency - Per each connection
acd347c5-400b-552b-9ad4-fb686f3afbd3 | note | Inspection / Test Method - Inspection
b48cff71-65af-563f-8f56-d25f564b22df | note | Verification Records - Photos
09a7813e-cef5-5845-9e37-b5e362be4101 | note | Standard - AS/NZS 4129
36062463-7fae-5f5a-accc-8709e74ca973 | note | Signatory - Site Engineer
4fc93a69-13c3-41de-8390-c2cda62fdfe0 | checkpoint | D2.7 - Trenching and excavation
cfa0c750-11e7-52bb-ab7c-3755b9d8bc24 | note | ACTION (W, M, H) - M
f7ba4e52-d4f4-563d-b4a8-9de9750480d9 | note | Conformance Criteria (What's Required) - In accordance with NZS 4407
0aa58100-ea6c-5eaf-996c-da6d1b6b5672 | note | Detail - AP65 Subbase particle size and sand equivalent
2cc4fdf8-cd3f-5754-80b1-c10c78be6b27 | note | Frequency - Daily
d38b48c1-d8e1-5cd7-ba98-deb7ccd739e2 | note | Inspection / Test Method - Inspection
86b9df5d-f2ca-5f8d-b2cf-9f63dd9b4820 | note | Verification Records - RCP and digging checklist
f8d12c8f-71f3-5f5a-92bb-5bae3a1050ad | note | Standard - NZS 4407
2e0c9802-a8d0-5d52-8f10-192a9e397844 | note | Signatory - Site Engineer
2ae294e5-94ac-4ee6-8088-2cdce3128900 | checkpoint | D2.9.1 - Pressure testing & disinfection (1)
d50864a5-c9aa-558a-850d-1d86cde92030 | note | ACTION (W, M, H) - H
5465cb1b-d4f5-566a-8ae3-862c63bdeadb | note | Conformance Criteria (What's Required) - AS/NZS 2566:2 Section 6.3
9a3dbfa1-70c0-5cd6-bc6b-fac079547906 | note | Detail - pressure testing of the new PE main
f8fa8729-be33-556a-aea8-5da4e5d7e55a | note | Frequency - Prior to link in
4a92b5c7-8933-5848-b0ed-07a466395d7b | note | Inspection / Test Method - Testing
87552fab-3859-5d35-9ed3-bdba687e391d | note | Verification Records - Test records
5fca0973-68bc-5b2d-aeea-ccd9bdcbb7a4 | note | Standard - AS/NZS 2566:2 Section 6.3
17acf663-53f0-5e80-91b6-7bcece4bd6fa | note | Signatory - Engineers Representative
8f92d7c5-dd19-4f3d-aaa5-a6b233a7925f | signoff | HOLD POINT
6dd3ef6f-3fe9-432c-9e46-9884d31437e5 | checkpoint | D2.9.1 - Pressure testing & disinfection (2)
49ef2b16-3496-5a60-bcb9-f3e61fd22f61 | note | ACTION (W, M, H) - H
ce83a492-536c-5a08-9e8d-9c298f3d95c5 | note | Conformance Criteria (What's Required) - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
7368b357-268c-5eda-a169-37fe135842b4 | note | Detail - Disinfection of the new PE main
407dc106-2113-50e9-8323-2b5a9ff3cc3f | note | Frequency - Prior to link in
5dbcd850-bf50-5d77-a2fa-e070f8e8ed0f | note | Inspection / Test Method - Testing
f55c2efd-8b52-5923-96ad-613d0ef29b70 | note | Verification Records - Test records
aeea6367-a865-5dd4-b914-7795774016cf | note | Standard - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
0af7d080-a0a1-552d-95ab-35a0036d849d | note | Signatory - Engineers Representative
57a7d28a-0f5f-45fe-9741-cde5c15351f9 | signoff | HOLD POINT
5a9721bb-dc94-4ebf-b671-f7176fed1063 | checkpoint | D1.3.3 - Engineer's inspections
ae2ad479-23ed-5e6b-b51f-ead67d673eae | note | ACTION (W, M, H) - H
3550b755-41cb-5f02-ae76-a452d9f48e44 | note | Conformance Criteria (What's Required) - Inspection report
fce868b7-d7c8-5188-873e-c358335a4e5b | note | Detail - Enginer's inspection for pipe, concrete pre pour, pre sealing
f386359d-4036-581e-aad4-6684dc5cb31a | note | Frequency - As required
c443bcd7-7380-5990-ade0-41137d5cdb97 | note | Inspection / Test Method - Inspection
3c7876ec-78f1-57ec-90a3-f89c5107675b | note | Verification Records - Email
9ef82c31-361b-5ba6-9b47-b9e971ecbfbe | note | Signatory - Engineers Representative
1b54fb0a-efaf-4dd6-b072-b9047fe82584 | signoff | HOLD POINT
6182eda6-f985-4b87-890b-4350863c318e | checkpoint | C1.18 - Surface Reinstatement (1)
2d29dab5-b355-5543-9b52-aa1a2626a7fa | note | ACTION (W, M, H) - H
749f4c12-a2dd-5d85-8f09-76ff4c90c61a | note | Conformance Criteria (What's Required) - Engineer's Approval
3a9fb5cf-4a00-59ac-954f-5ac806de72fd | note | Detail - Mark out the trench including overcuts
eef1c09b-42cf-51ad-9d06-6a28022a87f6 | note | Frequency - Prior to surfacing
e677a204-7f71-580f-bacf-d20567d72cb0 | note | Inspection / Test Method - Inspection
79d1969c-2c07-5909-a403-e10d550f2be8 | note | Verification Records - Email
bb4e1c12-0aeb-57b8-85ff-f8175e012166 | note | Signatory - Engineers Representative
b0895a81-c503-491e-a83a-6b7f76135cb5 | signoff | HOLD POINT
c5cae17a-7897-4e31-8394-eec9ae947599 | checkpoint | C1.18 - Surface Reinstatement (2)
1fa458c2-33e0-5d81-8509-11f52647e9a0 | note | ACTION (W, M, H) - H
2ffb82ca-14d6-5df9-93ce-7cfe222a988a | note | Conformance Criteria (What's Required) - NDM testing
fd081dcf-4aa1-5afc-9c3c-74fbe3a62783 | note | Detail - Provide NDM test results for AP65 and AP40 layers
f5a11f07-09b9-561b-b4fd-eafb0c5ea375 | note | Frequency - Prior to surfacing
6a91ed1b-d694-529d-9a3a-11af5f9250fb | note | Inspection / Test Method - Testing
0a96f30c-75c6-527c-83fe-5e608284b664 | note | Verification Records - Test records
fe45aec6-de41-5425-b766-b4b112e30fb9 | note | Signatory - Engineers Representative
bd54192e-2da9-4b00-8932-13b4a7358292 | signoff | HOLD POINT
afc1c5f4-c4ae-4a54-b203-392b3a4d49a0 | checklist | ITP - Salford, Moana, Wilton, Waihopai Streets - 6.0 Waihopai Street - Layard Street to Moana Street (DN180mm) | itp | 6.0 Waihopai Street - Layard Street to Moana Street (DN180mm)
983349cd-1b81-4b82-8058-e8e9146f0e9d | section | 6.0 Waihopai Street - Layard Street to Moana Street (DN180mm)
00c712bd-0b9a-4b36-8052-bfc48eb764fd | checkpoint | Link in at intersection of Layard and Waihopai Street (1)
06805c56-f5a1-56aa-bf52-9f37961cfd16 | note | ACTION (W, M, H) - W
ee906a70-8d32-5cda-8f9e-352c9c21698b | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
24a5c083-7b02-5972-b673-b0ada14e07b8 | note | Detail - PE to DI connection to be done as per the detail H in sheet 16 of the drawing
93424442-3829-5f44-8926-f4e7808783aa | note | Frequency - Before backfilling
c0d89773-9f9c-5bd1-9f6c-4d31731344fb | note | Inspection / Test Method - Inspection
aaeb56d3-c2fe-5060-9028-4d58ae453d44 | note | Verification Records - Photos
a4e7260d-c485-555e-8178-baa5b6fc9fd7 | note | Signatory - Site Engineer
1e4f7ebc-4cb8-4026-8d7f-3eef53366eaf | checkpoint | Link in at intersection of Layard and Waihopai Street (2)
25741e19-f35c-5607-a674-78c6b6accca8 | note | ACTION (W, M, H) - W
41b8900c-73eb-56d0-afb9-4a732b135c3b | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
d01d0bde-4510-5f9a-8f74-dd0c1579efee | note | Detail - As per detail H in sheet 16 and typical details as per sheet 18
fd03402d-a7b8-5628-9bf1-1ef8ed9fd241 | note | Frequency - Before backfilling
30e84a56-1209-53b3-9e29-1fa154d003d0 | note | Inspection / Test Method - Inspection
1b276b7a-32a8-5224-81f6-db69c14fd0fc | note | Verification Records - Photos
af50b818-b986-5657-b468-c4d1bae8e555 | note | Signatory - Site Engineer
69bb6f1a-ac20-404f-b489-723b2595bbb5 | checkpoint | Removal of existing teeand bends and reinstated with straight through pipe and associated bends/thrust protection at intersection of Layard and Waihopai Streets
13f170d3-91a5-562e-a855-4dd53dc81ef7 | note | ACTION (W, M, H) - W
becdfe04-491a-5d65-8516-ca09a57b2d3d | note | Conformance Criteria (What's Required) - Pipe reinstated through old line and thrust protected
8d6fcf32-78af-57cf-97aa-db5f795e295f | note | Detail - As per detail L in sheet 16 and typical details sheet 18
daf4f44a-3c50-5134-81c6-a5c15469ed89 | note | Frequency - per connection
dde56bb1-cacb-5966-9ea2-4b40df5024ad | note | Inspection / Test Method - Inspection
9e9b4c6f-c49b-5e76-b93f-589b2e6a09d6 | note | Verification Records - Photos
02c0db00-9eb0-5a26-9ae7-78585f78b792 | note | Standard - AS/NZS 4130
a7b8b3a6-2c51-53ef-9826-443dbaa4b5ba | note | Signatory - Site Engineer
ebb51bb8-f868-4d35-970a-3b9a7ff93d25 | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-LAYARD CH15 (1)
4fe96eb1-a2bb-593c-884c-be849d9e45b2 | note | ACTION (W, M, H) - W
9e3c38b4-d5ff-5318-9b18-aa1fa77051e9 | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
b0d3e335-b094-51ed-96e1-3eb5d70fd611 | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
36966d49-b96d-556c-a200-3285f921e0a1 | note | Frequency - Per each valve
6e990f72-adb3-583b-a32e-80b372295584 | note | Inspection / Test Method - Inspection
79cb1ad8-d6b4-574a-bc23-c1c6971c702d | note | Verification Records - Photos
8831ada7-0b42-51b9-a509-52fa7b965b84 | note | Signatory - Site Engineer
5495029f-379a-4112-8a02-2ed9b59e970d | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-LAYARD CH15 (2)
e598b0a7-6381-5c2a-bd58-1615e34fa3a2 | note | ACTION (W, M, H) - W
bb4d5b4f-485e-5017-92e1-d5e2f056ec89 | note | Conformance Criteria (What's Required) - Thrust wall installed
a8b65e6c-0559-5750-b297-85bbd4a3034b | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
e4580041-a649-5483-814d-a6943234c0f7 | note | Frequency - Per each valve
67d02b06-5a4e-5adb-a229-b576ceba286e | note | Inspection / Test Method - Inspection
0a1862c3-4431-5da8-b23e-5b68519f221d | note | Verification Records - Photos
d8ab6809-8f89-5181-be34-5f3f0f53d306 | note | Signatory - Site Engineer
08798466-7ed2-4195-9b44-378736ccd2ec | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-LAYARD CH15 (3)
178d12b0-14ed-539a-9fab-95ad58a28051 | note | ACTION (W, M, H) - W
4eb30ed7-af66-51e1-bf86-5d1e62fda072 | note | Conformance Criteria (What's Required) - Surface box finish
4fae0f7b-f53c-596f-9fca-4909311d4ce3 | note | Detail - cast iron valve box to be flush with the finished surface level.
29c92887-6e08-5d60-b54a-a3ee109a1972 | note | Frequency - Per each valve
99d702c5-4e7a-5b05-b67b-9ed52fae5571 | note | Inspection / Test Method - Inspection
eab647ce-e8ab-5321-ad43-e0b67ffe8ed7 | note | Verification Records - Photos
32bd6dcf-f093-55dd-a0dd-7f93fac5bdbb | note | Signatory - Site Engineer
49041042-fcc9-4160-8c8c-716feaab5d02 | checkpoint | D8.3, D8.4 - Lateral connection to house no#90 Layard Street
acc5ea12-75b3-5982-8651-5dddcea0fa62 | note | ACTION (W, M, H) - W
3fe40295-3655-522e-a496-c4bbfe63ac98 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
b0bd9d57-5ac2-5217-b50b-6992f8cf8e53 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
d3ab17c5-b92a-575e-88a9-7accdff26c98 | note | Frequency - Per each connection
5e5b3026-9200-5e5c-93a3-13c0989702e7 | note | Inspection / Test Method - Inspection
de09628b-624d-578d-836a-0be36dcafd5e | note | Verification Records - Photos
c24e3ab6-ac7e-59de-ad1f-a3796b08c79a | note | Standard - AS/NZS 4129
6dcc0a8a-1a2d-5b74-b728-c7a133915fca | note | Signatory - Site Engineer
f055c9be-3c08-46c0-9560-44b16fe36781 | checkpoint | D8.3, D8.4 - Lateral connection to house no#92 Layard Street
c0618748-f3e4-5a32-8905-241a33091bb4 | note | ACTION (W, M, H) - W
5d0e4973-2657-512d-878f-c82f98aabd2c | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
bf1d35a8-8794-5da5-86a0-a1f7a2faa59a | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
4e9e6ec3-4c1a-5a1a-970a-d06aa44b0a93 | note | Frequency - Per each connection
9c531070-c68f-57c6-a2cd-be4d5f2a6012 | note | Inspection / Test Method - Inspection
82716efa-fbb9-5aeb-bc3e-1583afb245ca | note | Verification Records - Photos
52a8a445-8aea-5b68-8dd3-f47f38aafa1c | note | Standard - AS/NZS 4129
1000a0c1-856c-581b-97af-c1036d4e218d | note | Signatory - Site Engineer
1df607db-fee9-4915-9134-7f3e5d4ae8b1 | checkpoint | D8.3, D8.4 - Lateral connection to house no#4 Waihopai Street
06691af6-21dd-59ab-ba71-6c6c80f54a44 | note | ACTION (W, M, H) - W
dbb37247-d7b2-5d3b-93f7-2e7895781054 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
2c4d43ff-45e3-54e8-866e-70a7b81d83f9 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
13fa8ce7-e138-5d49-815e-969bd62db041 | note | Frequency - Per each connection
be77a8d7-6fd3-581f-abee-145b01d52112 | note | Inspection / Test Method - Inspection
ccf1c79b-a709-5d89-8179-105311cdbc8c | note | Verification Records - Photos
e23210aa-26fc-5c3b-aff7-32ef457e1a42 | note | Standard - AS/NZS 4129
bfa056c9-38c5-5ee6-82bc-f9abad1025c6 | note | Signatory - Site Engineer
ab0cbf37-9a39-48d5-91ea-08e6cea585bb | checkpoint | D8.3, D8.4 - Lateral connection to house no#7 Waihopai Street
fbc5d059-b888-51aa-a1d8-1b765516521a | note | ACTION (W, M, H) - W
c8bf7fe1-e0f5-5541-acaa-5f8f2ec40f61 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
b4b2b76e-e7d8-52a4-878d-949b84a86867 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
299ab374-efb1-5b5b-8dc6-ea8048fa85d6 | note | Frequency - Per each connection
866c9f98-21b3-5627-9579-ea2a3232f703 | note | Inspection / Test Method - Inspection
6337ba3e-2590-595b-b3be-74b508e45eff | note | Verification Records - Photos
35bb9555-e6f0-5f16-bb5e-9929347d2e69 | note | Standard - AS/NZS 4129
d60c5102-b3df-5e0d-be9b-46f117f2a6dc | note | Signatory - Site Engineer
a28b7e98-41d1-41b5-9671-3f72e5e59a4b | checkpoint | D8.3, D8.4 - Lateral connection to house no#8 Waihopai Street
3859a30b-e757-5a0f-bf5c-55df97cb0e8e | note | ACTION (W, M, H) - W
d8c02b6a-374a-56c2-b56f-28e2f7282fce | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
905d7f30-60fe-50dd-80ef-4db45238b6a1 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
bf87d11d-b4e6-5773-b84e-64ab014cd1d7 | note | Frequency - Per each connection
41f3e0e8-3a51-5a6f-92f9-821e6745efd5 | note | Inspection / Test Method - Inspection
e4057a06-7223-5c65-984c-1fb62bd6759b | note | Verification Records - Photos
7bc7d6f1-f21e-5b2b-b493-0a7d2f826efd | note | Standard - AS/NZS 4129
c86028b2-fbe2-5463-bf44-0f6437efc2e9 | note | Signatory - Site Engineer
132893c4-dc93-4e87-98eb-0f4b3ee0ae1b | checkpoint | D8.3, D8.4 - Lateral connection to house no#18 Waihopai Street
ecb600d1-f76b-5aa6-bb6d-38e488857a03 | note | ACTION (W, M, H) - W
affb2eec-5b96-5c2c-90f1-574110e93ce6 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
9ab1bc07-a112-5592-93df-c7152d02e672 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
1c037020-cca5-5156-b65f-bca70fccab20 | note | Frequency - Per each connection
9622f55b-aacf-5261-89b0-08b6d8e105c2 | note | Inspection / Test Method - Inspection
a83dd206-e072-58ed-88b5-6f40e4986e2c | note | Verification Records - Photos
fc8f5184-922c-5446-ad88-dfc411c89dea | note | Standard - AS/NZS 4129
bb5bef04-7302-50bb-8cf0-f7f4dd1262b3 | note | Signatory - Site Engineer
a1415911-7c5a-4ee0-a3fe-4b03e5b960b5 | checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH01 at CH90 (1)
83c67814-4dd5-5eb4-9f95-8784a8b2e0f6 | note | ACTION (W, M, H) - W
34981308-b35a-52b9-91a4-e6846562d123 | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
77f5a2b4-01b3-5790-9de0-04b32e96439b | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
88e639d5-d35d-5d03-b52a-8963d960f3f9 | note | Frequency - Per each hydrant
a786bfd2-2738-54f0-b123-411e336d7924 | note | Inspection / Test Method - Inspection
a50cfca8-19eb-51d5-95eb-8a446d54cfa6 | note | Verification Records - Photos
c40d7953-5735-543f-9f86-e34b41bd9f8d | note | Standard - NZS 4522
5957181f-b17c-5470-ae70-de933e97cb2c | note | Signatory - Site Engineer
2f8c1dfd-b2ca-4056-8936-1ea6cca2eb37 | checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH01 at CH90 (2)
47bdc911-4254-50e8-8fcf-abeb97f2476e | note | ACTION (W, M, H) - W
a437876a-7fa4-5b2d-8c19-4a60279ffe50 | note | Conformance Criteria (What's Required) - Surface box finish
33252426-f80b-53d0-a0e9-edb76c19eeed | note | Detail - cast iron valve box to be flush with the finished surface level.
93dffe3f-21f9-5660-ac74-80f026663b1b | note | Frequency - Per each hydrant
9a85ac5a-42aa-5edd-8a77-7cc25a7d0275 | note | Inspection / Test Method - Inspection
99d2d681-bd3b-5629-b284-5c356389fe2a | note | Verification Records - Photos
d4b336ea-0d55-5bef-88bb-5e0d1630c735 | note | Standard - NZS 4522
e2de0da3-eab0-5770-8510-976167bd35e2 | note | Signatory - Site Engineer
7c14aac0-6132-439d-926c-b7972cd46fd0 | checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH01 at CH90 (3)
da891c43-ab48-554d-b31b-37b59a0e6288 | note | ACTION (W, M, H) - W
6cfd552d-75e3-530b-a875-1f9b2f26ec33 | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
61623fb9-67da-57f0-abd4-fefa098455a6 | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
cc3b8c77-8b5c-534b-9ed4-0a6b5b893d3f | note | Frequency - Per each hydrant
accd666b-602a-53d6-acf6-4187cfda8d84 | note | Inspection / Test Method - Inspection
83a964d1-d34c-5b65-8209-86d30a1f8b5a | note | Verification Records - Photos
d169c9b5-6322-5dbf-844c-2981ecd2809e | note | Standard - NZS 4522
dfac6931-923e-5143-9e3f-a291153c001f | note | Signatory - Site Engineer
56bd45cf-c210-4ce5-be9a-0fd69994e3fb | checkpoint | Link in at intersection of Waihopai Street and High Street (1)
b68d37ee-3ff3-5f78-a1e6-867e1dc56084 | note | ACTION (W, M, H) - W
1f7ee08c-7f50-507c-97b3-ed6e76e37a51 | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
81ff55b7-4268-5e52-bed2-b7f58a7d2b15 | note | Detail - PE to DI connection to be done as per the detail I in sheet 16 of the drawing
ad1492be-9b68-5663-819a-e3becef6cfc7 | note | Frequency - Before backfilling
db50b6b0-ffb7-55ce-9cef-3a406b52611c | note | Inspection / Test Method - Inspection
ca8acf19-6959-5593-be1d-cd313302ca7d | note | Verification Records - Photos
96e5c031-6dcc-5919-9b70-46f7ef6a7f26 | note | Signatory - Site Engineer
7b9c6085-7f7f-4a19-bdc3-35c71e0a0ab0 | checkpoint | Link in at intersection of Waihopai Street and High Street (2)
10958ba3-3ede-575e-82fe-6b2ddea37b17 | note | ACTION (W, M, H) - W
0001552b-18ff-55f9-bb84-74ba316aba4e | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
723af175-2776-5a86-a154-4718dcdcec3c | note | Detail - As per detail I in sheet 16 and typical details as per sheet 18
e3758ae0-e42f-55c7-8740-c57f0c012cdf | note | Frequency - Before backfilling
44424548-c8ed-5f05-a2f5-2a13c29607b8 | note | Inspection / Test Method - Inspection
ee0527d5-2262-5597-9b04-6b3ea36b244a | note | Verification Records - Photos
324dde35-f972-5097-9ccb-fc9ff897c972 | note | Signatory - Site Engineer
ce59c3a8-9bcb-4277-a57c-ead0d4bc7111 | checkpoint | D8.3, D8.4 - Lateral connection to house no#11 Waihopai Street needs confirmation
f1ebf8c7-95e9-5222-b5fe-86f438eb7881 | note | ACTION (W, M, H) - W
4cf1cc92-9a32-5967-8324-d52d54f8b5ff | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
d357d1f3-0331-51cc-9025-c97b1447d897 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
d582fe5e-e7ac-556e-8390-2a739a663854 | note | Frequency - Per each connection
3c34c1d6-25b4-5ce9-a152-c06bf1eedbe5 | note | Inspection / Test Method - Inspection
60aee4a1-380c-542a-9626-84138fcdb2bf | note | Verification Records - Photos
21060c8d-5252-5a4a-84bc-ba429425a2ab | note | Standard - AS/NZS 4129
09ae97e0-a4fd-5a3b-9fe0-25e4cf7bc0f6 | note | Signatory - Engineers Representative
5b2ec315-bacd-494d-983b-33f701d4e077 | checkpoint | D8.3, D8.4 - Lateral connection to house no#22 Waihopai Street
5e4aa02f-cb0a-5273-ae81-86c0cc7c7f11 | note | ACTION (W, M, H) - W
3efe3474-5687-5557-834d-8575d9fd1d37 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
ded84027-c5c3-504a-a10b-c1605f2cb276 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
7b079092-f1c8-557b-b615-62719730d174 | note | Frequency - Per each connection
5b790eeb-c25c-522c-874c-2de1f6e37cdd | note | Inspection / Test Method - Inspection
bd0e8aa3-b2c8-5a15-91e3-8dbfcb0f5c63 | note | Verification Records - Photos
d66f8500-431f-5bac-a3b5-7db1b427e939 | note | Standard - AS/NZS 4129
8f49ca8f-764b-5177-b0b8-1bb59c001b24 | note | Signatory - Site Engineer
1eb16a5e-bf3c-4deb-8b49-ff8aeb2275a1 | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-HIGH CH126 (1)
78e2128f-a923-5726-9669-f5ea2aa7c0d4 | note | ACTION (W, M, H) - W
9a04c01a-c9cb-5547-809c-a2a95d5aea81 | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
b0427fc2-ecb2-56ae-b630-65d288968bbb | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
29b2e533-635e-5af4-abdd-5c134ff2ad25 | note | Frequency - Per each valve
4b354af2-03a4-5df4-b041-450f9f9ca9da | note | Inspection / Test Method - Inspection
c7459ba4-7d9f-5dc2-b0e7-d70626a29bd8 | note | Verification Records - Photos
012b6e79-e13b-5918-8fd0-5de891820be6 | note | Signatory - Site Engineer
c6961f3a-452c-47ad-8163-f9f212ee75fc | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-HIGH CH126 (2)
7ce6f569-0587-5232-b9d7-d9d5a9eb76a3 | note | ACTION (W, M, H) - W
01cb089d-5484-54ec-90db-0466931a4c97 | note | Conformance Criteria (What's Required) - Thrust wall installed
ffb64683-c476-5d43-85f8-a0978245b837 | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
ecc72877-4da4-5743-bb0f-a39c4544b904 | note | Frequency - Per each valve
bf395902-6eaf-5269-a145-c7bf2fc88834 | note | Inspection / Test Method - Inspection
e5c8927b-dcbe-59ca-b86c-8f39bfafe698 | note | Verification Records - Photos
357aedc1-ff0d-51dd-a0f6-f5951f78bf49 | note | Signatory - Site Engineer
3ea426aa-3c4e-47b2-8db9-b9ae45c5b1c0 | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-HIGH CH126 (3)
2ed2d526-d3f5-53d0-9a47-83dd0a9b03c5 | note | ACTION (W, M, H) - W
a527f03b-bd9d-5d92-995f-b1c43967ae29 | note | Conformance Criteria (What's Required) - Surface box finish
ffc19527-8828-5ed6-a671-0c83210e64d2 | note | Detail - cast iron valve box to be flush with the finished surface level.
cf86d4b3-1840-5a32-93c0-c7ee72116e1a | note | Frequency - Per each valve
f5a5c9d1-1fdf-502e-b42a-4f14d47c1fce | note | Inspection / Test Method - Inspection
70318fc3-5357-5b5d-a7d5-011920975731 | note | Verification Records - Photos
1dffc6b9-611b-5d2f-a605-33e43d944edb | note | Signatory - Site Engineer
a9655cb9-bcf1-46d7-911d-8ccd15e1f195 | checkpoint | D8.3, D8.4 - Lateral connection to house no#26 Waihopai Street
f3a2a397-c2c6-5af2-95e4-3ac39630e5de | note | ACTION (W, M, H) - W
31de2529-a50d-5c01-9580-e729b58fe6ba | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
0d8738a1-21d6-5b65-865a-8fe1ca67fddb | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
bcf398d0-d011-50fd-a601-7060d8193f79 | note | Frequency - Per each connection
6313a9c9-b8fa-5ed0-b694-508890454cb5 | note | Inspection / Test Method - Inspection
98fd69be-771b-557d-ab2b-730b7b2396bb | note | Verification Records - Photos
341a70cd-0de3-57db-8732-4195e1653c1d | note | Standard - AS/NZS 4129
36cb92eb-961b-539c-b206-547f76b94e1e | note | Signatory - Site Engineer
e8b69c6a-2953-43cc-8c53-f977fca6e968 | checkpoint | D8.3, D8.4 - Lateral connection to house no#25 Waihopai Street
b3792225-c533-57c5-8959-8a80c3a3cd2d | note | ACTION (W, M, H) - W
515d81b6-40eb-598f-851f-d674dc74e0c5 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
785ef309-33d8-58cb-9724-263a5dd953f4 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
1323228b-7d92-50cb-9cad-f50b299c69ed | note | Frequency - Per each connection
75ea1ca9-f1de-5133-9b04-4b88c5f042fa | note | Inspection / Test Method - Inspection
59ec1fc7-cb8a-5bdf-a81b-bd2e087d4ac6 | note | Verification Records - Photos
8f73510a-ae45-5253-a972-5398db6ca1fe | note | Standard - AS/NZS 4129
01e3c0f1-414f-5e6b-9e80-8aa4f2aac322 | note | Signatory - Site Engineer
efe7c148-006d-46db-a79e-6cfeb7e514e2 | checkpoint | D8.3, D8.4 - Lateral connection to house no#29 Waihopai Street
f20b1238-22cb-5af8-9bb7-bf8167cc1671 | note | ACTION (W, M, H) - W
f3a0df75-e4c4-51d5-8ba9-7f6950faadf8 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
99a07feb-6300-5475-8199-0049f8f06b15 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
b8968a0e-69c0-5d0d-97fb-a89ccaca7086 | note | Frequency - Per each connection
c8834f29-07f4-5f19-b283-1138a7525e21 | note | Inspection / Test Method - Inspection
6d8446fb-820c-5099-966d-d7ae168450aa | note | Verification Records - Photos
3f73b41c-3297-5154-bc13-98a6e7aa150b | note | Standard - AS/NZS 4129
7b4817cb-e2c1-5db3-a616-50a7ad270e3d | note | Signatory - Site Engineer
d60e48d1-718e-41d2-b873-6c32e7bda138 | checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH02 at CH178 (1)
4d7c9089-36a0-548c-ba19-778e77dc6cdf | note | ACTION (W, M, H) - W
6c7cd6d4-a22f-5805-ae3c-7acb4a3faa07 | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
3aa7c478-ccdf-5393-ba7c-8190367aa191 | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
a74f474a-ca84-53a6-838c-506d5f42bca8 | note | Frequency - Per each hydrant
ae54f2eb-ead1-509b-85cb-3dc980c6c5d2 | note | Inspection / Test Method - Inspection
486e5e91-30b2-52e9-80fd-230cb8ebf169 | note | Verification Records - Photos
85269e5d-f879-5816-b08c-7b1064d83795 | note | Standard - NZS 4522
fa9e6488-c4d5-511f-8984-ceeb03c43cec | note | Signatory - Site Engineer
98a4325c-6c56-4cc1-b429-1fa1e33b3c48 | checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH02 at CH178 (2)
36cbd609-c203-5248-8612-b8ba4a8419a7 | note | ACTION (W, M, H) - W
84329799-dc23-5d98-bd63-02c622b03ca8 | note | Conformance Criteria (What's Required) - Surface box finish
58f587b8-a0b7-571d-bd7e-26ef53051b31 | note | Detail - cast iron valve box to be flush with the finished surface level.
a55614e4-5c53-5e1c-9a9c-836f542cf0b2 | note | Frequency - Per each hydrant
80176ffb-35a3-5875-9315-f3e00bfd03fb | note | Inspection / Test Method - Inspection
bea8d16a-07e8-54e0-bb68-394ecc6f8026 | note | Verification Records - Photos
376e0310-2765-55a3-8aac-814c66248844 | note | Standard - NZS 4522
0a3d726a-624a-5975-9ff2-36ab26335e3b | note | Signatory - Site Engineer
3ea733a8-762a-477c-bc35-96646c673905 | checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH02 at CH178 (3)
36f950d1-b676-5a0a-ad88-d263edd76752 | note | ACTION (W, M, H) - W
cbc15f56-4131-53d6-9c8d-e59d383f1b5c | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
d5a2aac7-6713-547d-998d-f2833f582d3d | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
276e982c-1076-5795-bead-95d0f7c6e922 | note | Frequency - Per each hydrant
f8057279-c9d1-5e81-8995-6d334bf19d01 | note | Inspection / Test Method - Inspection
23632205-c7dd-57a2-9a53-3c1a89ddc8dc | note | Verification Records - Photos
adc685f8-98a5-5a81-a7d9-8d7a9c5ee340 | note | Standard - NZS 4522
a7a28772-8213-5104-8497-37f7dca09616 | note | Signatory - Site Engineer
77d760b5-2df6-4a97-99f4-9fea5bd14d6c | checkpoint | D8.3, D8.4 - Lateral connection to house no#30 Waihopai Street
7c7637e1-cd25-50c5-8f27-e6424016a215 | note | ACTION (W, M, H) - W
b18a2a65-0f83-58c7-bf50-d911d9844c79 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
2350f674-5faf-52c5-b697-90f99ab6324f | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
52cc5fa5-f9e2-59e8-a123-dec91ddcf1d8 | note | Frequency - Per each connection
e01565f5-1280-5b3d-8683-2c5d307eb74d | note | Inspection / Test Method - Inspection
e1367720-bc4b-58d4-a640-d1370cb06c59 | note | Verification Records - Photos
33c26945-8f35-5a0e-8b9e-9c590e60bc77 | note | Standard - AS/NZS 4129
fe7762ec-d526-57a6-b1a4-6d2c5f27b065 | note | Signatory - Site Engineer
1701ba11-e103-4721-bf3e-99d3934f5ac0 | checkpoint | D8.3, D8.4 - Lateral connection to house no#38 Waihopai Street
cb9cf2b4-602f-57e9-b752-fab39bcae80a | note | ACTION (W, M, H) - W
3446bb0d-2c64-53a0-bd20-03eeec2d0a31 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
361cfd34-4644-513b-aec5-1dabe2b8f0f6 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
581c9b26-424d-57f7-bc3a-b02bbbfa9f1b | note | Frequency - Per each connection
5553922b-0d80-577c-b96a-c88603a420a9 | note | Inspection / Test Method - Inspection
55b687ce-9d7d-5737-bed1-bc0bfe0ecc6d | note | Verification Records - Photos
1c01870e-7ec9-55cd-940a-8cc999015624 | note | Standard - AS/NZS 4129
26c9beaa-0a0a-54d4-93bf-993659c8d54d | note | Signatory - Site Engineer
8fe0606d-8065-407d-826e-e48c3594d89b | checkpoint | D8.3, D8.4 - Lateral connection to house no#33 Waihopai Street
4c1185de-ce9a-5e41-a415-f240bee6a5be | note | ACTION (W, M, H) - W
c540ef36-354b-5464-babe-984905e23253 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
b62982bd-b05e-5296-8a53-532bb9b5ab51 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
2728a689-35de-52e7-aa3d-cb0bef97ff06 | note | Frequency - Per each connection
462ee495-023f-5a98-b3cf-e4d7d2683824 | note | Inspection / Test Method - Inspection
d439d86d-1f1a-541f-9afc-731c811ede01 | note | Verification Records - Photos
97645fab-59f7-50d1-9939-0d20a199276b | note | Standard - AS/NZS 4129
5d8ac216-5804-5c87-8546-8bd53b0147b3 | note | Signatory - Site Engineer
9d1f1363-7187-4b0f-a517-e28d8f8b973b | checkpoint | Link in at intersection of Waihopai and Terrace Streets (1)
df76474a-6f68-57c5-8091-6cde9c5c31c6 | note | ACTION (W, M, H) - W
233d5107-fbde-5571-9487-05a2882819e0 | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
f05a5ee9-c5e4-5c7f-a6a4-4763b3564dd3 | note | Detail - PE to DI connection to be done as per the detail J in sheet 16 of the drawing
05d304a1-c8f6-54db-b02a-84f31a4f645d | note | Frequency - Before backfilling
a68f1298-7826-5e86-af68-9ba5fdc1bd6c | note | Inspection / Test Method - Inspection
72acae33-5490-548f-b56f-7a474d3a9b36 | note | Verification Records - Photos
7785bcad-f85d-5123-8cfa-f7d48b9db4da | note | Signatory - Site Engineer
8d1085ed-f946-4b69-a1ed-10c05432dca8 | checkpoint | Link in at intersection of Waihopai and Terrace Streets (2)
9192babd-7b0b-58f6-aa8c-5f6dfec9c5b3 | note | ACTION (W, M, H) - W
81fe397c-de2e-5509-9b3b-edfd68344a20 | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
cab9f549-fd48-5f09-8052-021c152d606a | note | Detail - As per detail J in sheet 16 and typical details as per sheet 18
0bc960ba-d4da-5792-a1a4-408b184bdb46 | note | Frequency - Before backfilling
4acd22e1-ae27-5828-85fc-79455e48c3f6 | note | Inspection / Test Method - Inspection
8e3159d4-4b44-5170-b923-2c1a40dd2845 | note | Verification Records - Photos
32aa4761-3f19-5646-b147-b1652e0f2eaa | note | Signatory - Site Engineer
bbdfd285-8912-422e-aead-ac323e7e4e15 | checkpoint | Capping of existing tees to blank abandoned ends. Intersection of Waihopai and Terrace Streets
ef7e379d-23ff-5f86-afe2-f559075fae18 | note | ACTION (W, M, H) - W
4d8d1ce1-8d69-5637-9ce7-cbab8fb348b4 | note | Conformance Criteria (What's Required) - Tee ends blanked and thrust protected
cfde1a11-a763-53b2-98bb-0759e75b36ab | note | Detail - As per typical details in sheet 18
5d249e6f-598d-5420-9f4e-8115ef93c90e | note | Frequency - per connection
82e15227-5012-5783-9d89-be817fb4643b | note | Inspection / Test Method - Inspection
e208046e-2bb9-52ee-91c2-d1a8f4a14b63 | note | Verification Records - Photos
f0d526e7-8097-53f4-89c5-ab9a9b320f63 | note | Standard - AS/NZS 4130
f4c1ef28-37f6-5b3b-8640-6028685adc88 | note | Signatory - Site Engineer
acfdaa50-e818-47c8-bc1d-8ad6a7180788 | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-TERRACE CH238 (1)
0a8538f0-fda9-5f41-93ce-9f53b0931464 | note | ACTION (W, M, H) - W
680c729f-fd5e-5068-b962-9c6d586b2616 | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
a3cf89ea-c86e-5fb8-921e-080121dcabae | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
f272b70c-6ebd-5098-a305-c92941c61223 | note | Frequency - Per each valve
b5a88012-84e2-53bd-be25-fad8d716f1ac | note | Inspection / Test Method - Inspection
1b3e9bb1-05f2-5117-b26d-3df0c68a4242 | note | Verification Records - Photos
59acedc3-34f4-56b0-b2a1-c3688536dc28 | note | Signatory - Site Engineer
98ece131-ebab-4375-970f-b3b2b0d46266 | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-TERRACE CH238 (2)
cb50e4f7-060f-59e0-b979-d66b74f497e5 | note | ACTION (W, M, H) - W
50f436cd-5cb8-5dd0-bbc7-0f4bfba2122f | note | Conformance Criteria (What's Required) - Thrust wall installed
9ba61e06-3454-5fa8-ae8c-a7d0acad5cdb | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
718c98e8-970a-5f51-9dd0-02a2e64904c9 | note | Frequency - Per each valve
275c5770-960e-5cc8-a8f3-a132e6beaf49 | note | Inspection / Test Method - Inspection
8f97cf23-da94-5a74-8fb1-5f077e19e80a | note | Verification Records - Photos
72250cd0-12c1-5604-b8f1-f51447169d2c | note | Signatory - Site Engineer
c950b71b-98f4-430b-9e63-98e4680ff3fe | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-TERRACE CH238 (3)
829f60ea-4a64-5c17-bd60-55d75cd271d3 | note | ACTION (W, M, H) - W
742c3fb1-621d-56a0-a178-f9ee18ee6e2e | note | Conformance Criteria (What's Required) - Surface box finish
621ea096-0d6a-5c12-a436-042624ee90db | note | Detail - cast iron valve box to be flush with the finished surface level.
ac0b554a-8fee-5278-a98a-b537f1b27396 | note | Frequency - Per each valve
80288904-d84b-5c6c-9793-0b7994f2b3d8 | note | Inspection / Test Method - Inspection
63eaaa32-28f0-5135-a94b-14ab4a5bfb6f | note | Verification Records - Photos
c46f822c-f977-5c02-a382-d2aba11f2ae2 | note | Signatory - Site Engineer
8af34df5-8f97-4876-b7f6-2bdd494c1d18 | checkpoint | D8.3, D8.4 - Lateral connection to house no#42 Waihopai Street
1488140a-d709-557b-825e-b9cda421bcc4 | note | ACTION (W, M, H) - W
6c4b2894-63c1-5106-93c8-3d7524ab5736 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
40f709f9-248b-57d7-91c8-bc3e40d255b0 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
8677c9f9-8a0c-535c-af01-080b53ff7bb3 | note | Frequency - Per each connection
498bf88b-4223-5463-82ee-b5769bb50b86 | note | Inspection / Test Method - Inspection
af17dd39-fe54-54b5-ba2c-84fed1d53553 | note | Verification Records - Photos
b1fc3c2e-12d6-5db6-b48d-23c00a9783af | note | Standard - AS/NZS 4129
c200eac9-81d8-5c94-962d-de764c071a54 | note | Signatory - Site Engineer
cb62b660-21a1-4e31-b339-f0066f2c59ac | checkpoint | D8.3, D8.4 - Lateral connection to house no#46 Waihopai Street
c1122ad3-9f77-54a2-95b5-04f4f3ff6bd6 | note | ACTION (W, M, H) - W
fa2f8d93-3b0b-5645-a174-e27d60a7c803 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
32b67622-86b3-5cf9-a35d-d5a08a5e5afd | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
8a1a0c74-6ff7-5210-a178-ff934cd061f8 | note | Frequency - Per each connection
4f73f0b0-5d38-51a4-a0bf-292ab8f4a4b0 | note | Inspection / Test Method - Inspection
e7f9427b-dc4c-5737-bb5c-1d871d4a5b5d | note | Verification Records - Photos
a2acffcf-1af0-59f3-b6aa-6c0247da3d80 | note | Standard - AS/NZS 4129
c94ce2e6-a17b-56d9-8792-7f2255f90464 | note | Signatory - Site Engineer
75cc25a2-cb08-4d8a-86d0-2bb81fc9f92b | checkpoint | D8.3, D8.4 - Lateral connection to house no#52 Waihopai Street
9c26f9d3-f9ba-5270-9cf6-7aeeb7779c5a | note | ACTION (W, M, H) - W
00fc0b21-5269-513e-b670-42573bd61349 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
873895c6-a62f-5fb0-bcf4-b2835e6dedb2 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
7124b26b-6081-5293-ba66-c00bfd34ca3a | note | Frequency - Per each connection
75232bd5-e1f6-5621-95e0-02caa7ec86ec | note | Inspection / Test Method - Inspection
4602e725-1661-54ce-b94f-6a14719382c0 | note | Verification Records - Photos
a074912f-3acf-58dd-9af4-6294dbca5dd1 | note | Standard - AS/NZS 4129
f85c6012-2fdb-529b-ad29-d07f55373c03 | note | Signatory - Site Engineer
9cdc99ff-0283-4ae6-a798-45cf7f8ce303 | checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH03 at CH285 (1)
391ab149-70e5-529f-b542-3c6ed644a856 | note | ACTION (W, M, H) - W
d1e258e5-386a-5415-90e3-14c4c1b03959 | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
72ded3c5-8771-5904-a971-141f5f504ebb | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
378509b5-8ed3-5d10-adb9-ac763a145da0 | note | Frequency - Per each hydrant
037ad6cb-aab8-53b0-943d-b18561f6389e | note | Inspection / Test Method - Inspection
cdd3a806-7536-55c2-bb82-3f1c6465d52d | note | Verification Records - Photos
f29f0efd-603a-5e31-8805-f7a47204e9b2 | note | Standard - NZS 4522
2ad08fec-1bfd-5409-8f12-c75243e9dcd3 | note | Signatory - Site Engineer
3258ea63-1118-4bf9-a302-daa61ac3682c | checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH03 at CH285 (2)
9490f7c3-154a-5c14-a0ea-062a035f52f8 | note | ACTION (W, M, H) - W
e979ef87-2dc6-5b47-b36a-29ae1d2f9290 | note | Conformance Criteria (What's Required) - Surface box finish
5f82028b-4cd6-516c-b115-892152cf6034 | note | Detail - cast iron valve box to be flush with the finished surface level.
d6fe9277-b866-5b8f-b09e-f30b9b5f3438 | note | Frequency - Per each hydrant
1f4cb496-da22-5c95-a40f-15b32f3b53ff | note | Inspection / Test Method - Inspection
d46d80c5-30b5-5d87-b5de-7c5bf13ce0e4 | note | Verification Records - Photos
7b5e119b-d8a3-565f-98bb-51e7165a1c4f | note | Standard - NZS 4522
d6866b94-bb9e-5508-a16f-f8f4e0fd6e8f | note | Signatory - Site Engineer
289bfeaf-0602-4b7e-a69c-94e914b6364b | checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH03 at CH285 (3)
03a884b4-3987-5a53-9624-985c363b4279 | note | ACTION (W, M, H) - W
46b8a188-c3bb-5c3c-9ee7-c25d485155cf | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
25405e16-7aa8-5ea1-9346-b000733f4969 | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
266a1116-5068-5c6f-8df8-626f8bf05a62 | note | Frequency - Per each hydrant
c1da0be6-99ab-5c17-b63e-355c57003f84 | note | Inspection / Test Method - Inspection
9d97ae02-840e-595b-9876-f739589a38cf | note | Verification Records - Photos
9b33953d-6811-50c1-a091-1c6d19f71858 | note | Standard - NZS 4522
6f174a56-b902-5c98-93d5-6c4d6ca15b6f | note | Signatory - Site Engineer
c8f488dd-f083-47d7-8aca-4c202022e2d7 | checkpoint | D8.3, D8.4 - Lateral connection to house no#53 Waihopai Street
5c20a391-479b-5c80-9ee7-64c3d41550fc | note | ACTION (W, M, H) - W
b459f1b2-1dd8-5cf1-b6d5-40e6a2c244be | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
7a0197e0-16db-5f55-9148-c9cb9b8bb363 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
17c76ed7-4233-59ec-a285-4cdf5117cdf5 | note | Frequency - Per each connection
da868aa9-4f0d-5900-98d6-df3df5520401 | note | Inspection / Test Method - Inspection
046f329f-a9d3-5aaa-9a4f-27490bb015a6 | note | Verification Records - Photos
3620d8bc-2270-593c-a2fb-e84a0112d8f1 | note | Standard - AS/NZS 4129
33cf9ac6-cb24-53bb-8ac3-826024ba962a | note | Signatory - Site Engineer
a437ba44-0d17-4e8e-8e67-70fa6a91e5d0 | checkpoint | D8.3, D8.4 - Lateral connection to house no#54 Waihopai Street
26102698-c419-5748-b7fe-3c83cf052a7f | note | ACTION (W, M, H) - W
dc77bd78-dc08-516c-9a2e-e9855f439d5e | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
8f2a6723-1fd8-5f4f-a3ab-44bfdc0854c0 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
3f8fdd4c-085c-5825-b9ee-bd49b732f99e | note | Frequency - Per each connection
979424fc-6d6d-5e30-b27e-9ae26c50bee1 | note | Inspection / Test Method - Inspection
39e85946-2c36-51f8-b2c5-d1b46309dd75 | note | Verification Records - Photos
a2eb95c7-2fc7-5b97-81a4-6e9083594177 | note | Standard - AS/NZS 4129
0b790782-08ce-551a-839f-8a72df960aac | note | Signatory - Site Engineer
8162065a-ada2-43cf-8c51-aff52f256b2e | checkpoint | D8.3, D8.4 - Lateral connection to house no#58 Waihopai Street
a1892654-f925-5bc8-990a-3f98a7b80f1d | note | ACTION (W, M, H) - W
0c652567-84ee-5081-bc80-def875cb3e2e | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
f490e7fe-97f7-5f88-9fad-a6efbba958ca | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
ab95907b-bb6c-5670-8e60-9d7ae3b88e14 | note | Frequency - Per each connection
8522b5e4-c0ac-527d-bc78-2f96adf4163c | note | Inspection / Test Method - Inspection
9128d7ad-3862-5ad0-86b5-b5fd8ffda480 | note | Verification Records - Photos
4f1fa114-3383-5ce0-8ccd-d5914e8c86fd | note | Standard - AS/NZS 4129
41abb6ff-7b10-57a8-ba13-fb54c9caa4f7 | note | Signatory - Site Engineer
22f3cf83-ce53-4a71-8b0b-f74ac03667d3 | checkpoint | Link in at intersection of Waihopai Street and Lamond Street West (1)
74dfeda4-084d-5efe-b5fb-1c0afcfcf390 | note | ACTION (W, M, H) - W
f0577736-5162-500b-89aa-1126ca89b7c6 | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
3e1994f9-cb18-56c3-a76c-8c4caa0b887b | note | Detail - PE to DI connection to be done as per the detail I in sheet 16 of the drawing
78c14d77-2a02-5655-b4d0-031e82845b47 | note | Frequency - Before backfilling
3bf865fd-2691-5883-a6d2-8326535758d0 | note | Inspection / Test Method - Inspection
c808e403-797a-50e9-900d-437c4b28104c | note | Verification Records - Photos
ade657d6-b882-5f56-9f0a-f12078ba3ee8 | note | Signatory - Site Engineer
fe60db98-466b-4e13-88dd-cec07546bd14 | checkpoint | Link in at intersection of Waihopai Street and Lamond Street West (2)
0286996e-0c40-5557-bd2b-4ff1b80113e3 | note | ACTION (W, M, H) - W
6d9a7830-75d1-5de4-8970-b55bbea6ec2f | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
b084d302-7413-5a5c-a77a-2c55906cc70d | note | Detail - As per detail I in sheet 16 and typical details as per sheet 18
54481076-0bec-5b59-9919-bfe729cb7175 | note | Frequency - Before backfilling
39f056a8-f8be-5c0e-9d78-3d43363493e1 | note | Inspection / Test Method - Inspection
b0957cf9-7ad8-53d2-9a07-c6e383ce1ba3 | note | Verification Records - Photos
a3e57c4c-1795-52d0-b70a-e13c127e492c | note | Signatory - Site Engineer
6314e7c2-854f-435b-9586-b09224bda6a0 | checkpoint | D8.3, D8.4 - Lateral connection to house no#60 Waihopai Street
1af3ec56-fd48-52d8-932c-96ad73c24b50 | note | ACTION (W, M, H) - W
67710da2-177e-5056-b5df-c4b5733c6360 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
91827ea0-bec9-51c0-bb6d-d654c30b6d81 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
e9a20a3d-6698-5cde-879d-a834d93259be | note | Frequency - Per each connection
c7ccdda8-dd83-52fb-a5ab-54d27b772b91 | note | Inspection / Test Method - Inspection
90950ca0-5b2d-5c6b-8d16-88414bf2a71c | note | Verification Records - Photos
b345ae7f-6bf2-5e7d-8a48-a1c291ad1094 | note | Standard - AS/NZS 4129
afd1628c-2f59-5412-a122-2c97955a837e | note | Signatory - Site Engineer
f12dcd36-ab72-4253-8bc5-4fd3a45de7ff | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-LAMOND CH347 (1)
38fb1e0a-a96f-57ea-8bd7-04172572d80e | note | ACTION (W, M, H) - W
7df1a6e2-6719-5d7c-a5fd-93ddd8efe5d0 | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
36d28b35-2101-50c1-bb3e-883ba0dab52d | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
9a2b07b0-ffd5-5d68-99e5-a3977739d806 | note | Frequency - Per each valve
b028d74a-bb03-5ce2-aabd-366a48edcafb | note | Inspection / Test Method - Inspection
a97254bb-573b-5118-af8e-b4d2b139cb7e | note | Verification Records - Photos
fe3bfd64-2001-5df6-9ed1-32a8008d2dc8 | note | Signatory - Site Engineer
994e26a4-6bc8-4903-ad3f-a50569bcd371 | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-LAMOND CH347 (2)
37b59939-57ba-54a5-b558-ad718919abf9 | note | ACTION (W, M, H) - W
4569d3be-1802-5d58-8728-8debd0f6bb23 | note | Conformance Criteria (What's Required) - Thrust wall installed
4e1c17fb-964e-51a4-8375-1ab455b1b6bc | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
b673f092-5a75-526b-9631-0af0188062e4 | note | Frequency - Per each valve
f90c2cef-d2be-5932-ab42-3b9262815078 | note | Inspection / Test Method - Inspection
26387fb5-b09a-53f2-9772-ba8cde23449d | note | Verification Records - Photos
b5682a1e-55db-5ff2-95d7-46cb56bfc848 | note | Signatory - Site Engineer
07230a58-7fbb-4ca6-88ac-e07e7855f9e1 | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-LAMOND CH347 (3)
11d25116-3f7c-56da-84c2-dea7907531b6 | note | ACTION (W, M, H) - W
899b5bf6-0e02-536b-801d-497186e4183f | note | Conformance Criteria (What's Required) - Surface box finish
a3097743-021f-526f-be32-612e6ff5db26 | note | Detail - cast iron valve box to be flush with the finished surface level.
975e2328-7d30-5f36-a753-ab43905d19e4 | note | Frequency - Per each valve
85b04002-3401-5d96-8d65-aba178e7fa07 | note | Inspection / Test Method - Inspection
dcc4d59c-2f79-5295-88dd-25357927ce26 | note | Verification Records - Photos
704bcb6c-689a-5a71-a7cd-02ccc3e66772 | note | Signatory - Site Engineer
47e7ac5b-8a84-4b70-a55c-7fdf4f6d910d | checkpoint | D8.3, D8.4 - Lateral connection to house no#62 Waihopai Street
3bc1ac34-00a7-5c7a-9792-272095ce628f | note | ACTION (W, M, H) - W
e68d03a1-9ff8-5336-9e03-497956a78b0e | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
3100c193-9538-5350-8706-a1c3d14a7828 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
899746d8-469e-5a5d-93e8-0420327cd392 | note | Frequency - Per each connection
f917e267-03fe-5fe5-ae61-90a2c36f050f | note | Inspection / Test Method - Inspection
6013769e-a066-5430-9761-ef27175e1a35 | note | Verification Records - Photos
5bac7082-80fa-57d6-94b8-24901387b1ee | note | Standard - AS/NZS 4129
479fa5db-3942-5143-bd75-7086f04e802b | note | Signatory - Site Engineer
dae357a5-c628-47b5-96e0-7876f46d4bb4 | checkpoint | D8.3, D8.4 - Lateral connection to house no#64 Waihopai Street
70a730d4-26a1-594b-8150-f27bec98afb7 | note | ACTION (W, M, H) - W
88e09e14-743f-5386-8a73-a964cd386ca7 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
3c226911-8e87-552d-b0ce-40a3e209f320 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
a16703ce-9069-5259-a218-6221752fac86 | note | Frequency - Per each connection
9415e0fa-929d-52cc-90a9-4eff87b95822 | note | Inspection / Test Method - Inspection
3ec8452f-e903-5781-822c-ac78111d2678 | note | Verification Records - Photos
914db11a-f419-56e1-b7d6-da4c6cf6ed10 | note | Standard - AS/NZS 4129
5e05d006-3043-58a7-a1a6-37a79aec24d7 | note | Signatory - Site Engineer
0108437d-df03-49bf-a615-a6c2f42e23cd | checkpoint | D8.3, D8.4 - Lateral connection to house no#71 Waihopai Street
54b920dc-1c5f-553a-88ae-fa3db1134d5d | note | ACTION (W, M, H) - W
4f3c70c1-e71d-57d3-8e9f-62b1bd8f28b1 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
a5180aa0-e643-58f1-9a8e-4b99ed9fdbbf | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
c3481ea9-c659-531b-a997-b3d49d75934f | note | Frequency - Per each connection
4a5b957f-bfa7-50f6-85b2-34eaeaff01ee | note | Inspection / Test Method - Inspection
c78c361c-898d-56a9-a278-dcb3135c3959 | note | Verification Records - Photos
9ab0bfe9-3c22-5508-abb2-5d910c663f84 | note | Standard - AS/NZS 4129
e553b6a8-9458-553c-984a-eda7326edf0e | note | Signatory - Site Engineer
1a881fb7-3613-4b01-829c-55021f238cc1 | checkpoint | D8.3, D8.4 - Lateral connection to house no#66 Waihopai Street
2266170e-b30a-50e1-bdee-8264963a21d6 | note | ACTION (W, M, H) - W
06cf00bc-52b0-5f3d-bca1-5df2688ba360 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
239af3f5-18d1-5fea-95c9-29fe7828c121 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
f28f4b28-822e-59c4-9c75-7e72caf014c4 | note | Frequency - Per each connection
a46389c9-1c9b-5954-8d0e-dfa8644b0425 | note | Inspection / Test Method - Inspection
6aa692ee-e2f6-5b62-ba03-7408a51d1e1e | note | Verification Records - Photos
533eb6b6-8193-5a96-a542-1ba76ab7a83a | note | Standard - AS/NZS 4129
1cffb3bf-9a1c-5a8d-a893-d6a0daff3f78 | note | Signatory - Site Engineer
29ae0c3f-a997-4af2-ad86-55a7b6b82028 | checkpoint | D8.3, D8.4 - Lateral connection to house no#70 Waihopai Street
a81a2e1c-5445-5f29-8486-5b8ee2af9e95 | note | ACTION (W, M, H) - W
fffa5f50-a2c0-53d2-90fb-170b41a66086 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
dc3086e5-d718-5a65-8d01-ef9f42e1c59a | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
b3f5d741-b8b8-514c-a35e-d88c03dc5e9f | note | Frequency - Per each connection
47de1831-057f-54bd-b4a5-059be8f58466 | note | Inspection / Test Method - Inspection
e191ad36-4070-5b6c-8ba2-8e6060532280 | note | Verification Records - Photos
632a2a88-1ee0-50af-8428-f31feadb747e | note | Standard - AS/NZS 4129
b60f9043-85a6-5b63-b9cb-df7f73915456 | note | Signatory - Site Engineer
bb311d18-99a3-4c26-adfa-e666726324a7 | checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH04 at CH393 (1)
69462f23-aa98-5a51-a675-f12d7a385232 | note | ACTION (W, M, H) - W
26024246-3ddd-50d7-804d-b02fa9698408 | note | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
9b68ce66-24b0-5804-9c4d-ff498c90003c | note | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
9d3d348c-12ab-584b-9367-c4abb9171f26 | note | Frequency - Per each hydrant
b1089c5e-eb5d-5116-9ad3-a3d84e9145cd | note | Inspection / Test Method - Inspection
d49c760d-5246-57c7-a608-5b71f581520a | note | Verification Records - Photos
e6a04e12-020e-5440-93fe-c61189b904a6 | note | Standard - NZS 4522
7ad2aed1-d9c6-515c-8ebf-8aa3b89c4743 | note | Signatory - Site Engineer
0e8e03ef-a413-4304-b29e-415afebe8b14 | checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH04 at CH393 (2)
e65fa501-8d01-5c9b-b59c-3729ef139e92 | note | ACTION (W, M, H) - W
b85fa1a2-0243-5425-a24b-2bd157b1992c | note | Conformance Criteria (What's Required) - Surface box finish
026a582f-d0b8-5af7-9047-5139ffa26d23 | note | Detail - cast iron valve box to be flush with the finished surface level.
9712d249-4ac4-5b73-b39a-db3a909b8fd6 | note | Frequency - Per each hydrant
35ebcc7f-178f-5fb7-8142-7e49ff83cba8 | note | Inspection / Test Method - Inspection
200fd567-d70c-5fd2-aa32-e1f185284b34 | note | Verification Records - Photos
00e21959-547a-55fe-9e07-e376c9df6d6f | note | Standard - NZS 4522
66a372fd-6938-5f33-a5d3-0eb7ba692257 | note | Signatory - Site Engineer
751082ab-53af-4c94-b2ca-21520e4ff19b | checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH04 at CH393 (3)
a776f5e8-fb3c-51e0-be89-8310a6d8483a | note | ACTION (W, M, H) - W
fab3dbc5-59a6-535b-843e-f6eb5bc3b1e6 | note | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
5bfeb58f-22d0-50d2-8052-119c66aa1b99 | note | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
fa148c17-65cc-5de6-af28-47d97259b66b | note | Frequency - Per each hydrant
4051a801-54ce-5576-bcbf-f5b7827662bb | note | Inspection / Test Method - Inspection
0de2b6d3-9eb4-59d7-a142-66957fa202d5 | note | Verification Records - Photos
c62f59bc-b343-5a41-96b1-8aa1442068ae | note | Standard - NZS 4522
c42447aa-53a8-579c-83dd-b394469f117c | note | Signatory - Site Engineer
bb408c7f-d27a-496a-b594-26bb50f16daf | checkpoint | D8.3, D8.4 - Lateral connection to house no#75 Waihopai Street
51ff30ac-817b-5dd8-80dd-d4721228bee6 | note | ACTION (W, M, H) - W
35f4f407-cd05-5df7-ba4e-386961fc68eb | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
6af35755-1ba4-58a2-a053-54eee5311356 | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
fd66cfd8-4c60-5bc9-8502-fe22ad6713ac | note | Frequency - Per each connection
c1a97cea-178e-5f90-8583-78961f3fe5a7 | note | Inspection / Test Method - Inspection
e3fb44cf-9660-52b0-9f12-8806821656a2 | note | Verification Records - Photos
ef86848f-bb06-5aa6-ab51-301f3765053e | note | Standard - AS/NZS 4129
412ea535-033c-5680-ad1d-c0416448fcb6 | note | Signatory - Site Engineer
1f6c9031-b093-44ee-9562-cca0b2ee93d7 | checkpoint | D8.3, D8.4 - Lateral connection to house no#74 Waihopai Street
53cb6b83-f9a5-5c7d-975f-b722cf92a768 | note | ACTION (W, M, H) - W
794fc132-8698-5329-afe1-32e2f87a7422 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
a9b9944e-43cf-5893-99de-58a030c1ddad | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
820f0558-34cd-570f-aaaa-dd4d6e0b8379 | note | Frequency - Per each connection
39640d2f-9fa9-50ba-8390-a56a37a5ff80 | note | Inspection / Test Method - Inspection
0600ce39-11d2-537b-a8f2-42ccf8cf14b2 | note | Verification Records - Photos
47d697ff-c45e-5b56-8c52-92faf686960b | note | Standard - AS/NZS 4129
4d616f4d-d6f9-5fdc-bab3-4c9a37f861b1 | note | Signatory - Site Engineer
40721a94-4562-4e9a-a5f5-37f0fe259c7e | checkpoint | D8.3, D8.4 - Lateral connection to house no#78 Waihopai Street
e6724f95-d668-593b-b1ad-121d684432dc | note | ACTION (W, M, H) - W
ff06805f-b5df-5b25-8f36-6e16b9709b91 | note | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
0a546ccd-5ec4-57ec-a942-c3651840340d | note | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
7e6b00eb-b92f-50ea-b627-f368784ac7a4 | note | Frequency - Per each connection
851bad62-064c-59e0-9c6d-58cd6c068de0 | note | Inspection / Test Method - Inspection
efe72aec-ef54-53b9-800f-3285edcfb4d3 | note | Verification Records - Photos
4814e44e-1093-55d3-a35e-100df09339cf | note | Standard - AS/NZS 4129
6f02033d-517b-5ead-8ec8-87494fec0b15 | note | Signatory - Site Engineer
1dfc0a7f-f64c-4ccd-9f92-b56f8b2b98c1 | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-MOANA CH438 (1)
8ac89aaf-4da0-520f-9596-46219137990b | note | ACTION (W, M, H) - W
14ba7d96-4e67-52c5-9a26-db47db96c0f9 | note | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
5cc6b28b-ce93-581f-ace6-9e80a101a957 | note | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
a1348368-9365-5f21-862f-293664cfe409 | note | Frequency - Per each valve
8f7417cc-7417-5ea0-98cd-8c318fe84d4a | note | Inspection / Test Method - Inspection
65be72fd-b4d6-5eec-9006-cf3bccff9761 | note | Verification Records - Photos
8c808018-9daf-515a-8372-0b733f73e478 | note | Signatory - Site Engineer
afc86178-eef7-4f67-926b-1fdf0a832d59 | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-MOANA CH438 (2)
0d63c06f-2e44-52b1-9307-110ced699926 | note | ACTION (W, M, H) - W
9c3ef278-6663-5aa6-b600-ddfb56e1d411 | note | Conformance Criteria (What's Required) - Thrust wall installed
d7dd583c-be9c-5efc-9c0c-9ca95e4d7453 | note | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
cb93cb29-571a-5000-a3a2-7b5b7db1664f | note | Frequency - Per each valve
8a81c09a-b68c-5513-b25d-12671300b35a | note | Inspection / Test Method - Inspection
6583f53d-0452-5504-adc2-dd68c96fa1f6 | note | Verification Records - Photos
64f0311e-07b7-5fa7-9d9e-e9027f4baa96 | note | Signatory - Site Engineer
4f678fbf-16a7-4fb1-9b87-76107753564c | checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-MOANA CH438 (3)
abf6d924-e786-5663-9cfa-d1e63e65b000 | note | ACTION (W, M, H) - W
b323f3dd-282b-5fd6-98a0-95e2ae221c92 | note | Conformance Criteria (What's Required) - Surface box finish
0e19316e-1981-5c29-8497-309e09bbd347 | note | Detail - cast iron valve box to be flush with the finished surface level.
0364c4bd-336a-55de-ad1c-81c378c6dc4f | note | Frequency - Per each valve
2d5f8960-947d-5828-a024-1c4ba91a21f2 | note | Inspection / Test Method - Inspection
5126a498-267a-5417-835d-d62a9fa54a92 | note | Verification Records - Photos
29eab3c0-d642-56c8-9c60-02165caeff7b | note | Signatory - Site Engineer
1236f7cf-dda6-41b7-93d7-5514f178ef48 | checkpoint | Link in at intersection of Waihopai Street and Moana Street (1)
7377c8d3-8736-57fc-8fce-a0ab1d27f45e | note | ACTION (W, M, H) - W
c9e92bab-5ce8-5a0d-8cad-243a44da9f24 | note | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
5ebe4a71-86c4-5c16-aaa4-1fea3df4c397 | note | Detail - PE to DI connection to be done as per the detail K in sheet 16 of the drawing
89e85444-e808-5608-801f-506f0f69bd75 | note | Frequency - Before backfilling
d2638359-79a0-5654-b8ff-36024d17c3b9 | note | Inspection / Test Method - Inspection
3bbb6e2a-dcf7-5812-b397-0b77133d3d29 | note | Verification Records - Photos
4e152a93-a1b5-541e-a496-11bebbc73030 | note | Signatory - Site Engineer
79288bb6-7a28-454d-8615-bd9b728a3eeb | checkpoint | Link in at intersection of Waihopai Street and Moana Street (2)
65246bd5-a04e-536f-ad2b-d628b7081826 | note | ACTION (W, M, H) - W
1247ea66-5051-5428-9f27-d6b82eaedb0a | note | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
0c241517-abaa-5f9b-ae22-d4ed56255df9 | note | Detail - As per detail K in sheet 16 and typical details as per sheet 18
0ffd5958-669f-592d-b680-3b934e306090 | note | Frequency - Before backfilling
eeefe222-cbfa-57be-b970-a652560615a3 | note | Inspection / Test Method - Inspection
dd29d0f5-ef8e-5d03-9613-c68de09c789c | note | Verification Records - Photos
f90239e9-bb8f-5f49-9904-e4dd371c25bb | note | Signatory - Site Engineer
dc5ec73f-cf5f-4bfa-9d9e-620647488434 | checkpoint | Removal of existing tee and bends and reinstated with straight through pipe and associated bends/thrust protection at intersection of Waihopai Street and Moana Street
6c15d06d-ce64-540e-90ac-bbbce7f70045 | note | ACTION (W, M, H) - W
642068cc-99fa-5c42-aef9-0a61574b78d0 | note | Conformance Criteria (What's Required) - Pipe reinstated through old line and thrust protected
6d5b1869-1d53-5b6b-b32a-3c6b19199379 | note | Detail - As per detail L in sheet 16 and typical details sheet 18
1161c461-2d75-5542-8d0e-8d3667e1db70 | note | Frequency - per connection
8405d281-6fe8-5207-915d-20702a69b1b1 | note | Inspection / Test Method - Inspection
60c1529b-cb7f-5b4a-9715-322fe29ccc50 | note | Verification Records - Photos
c83c031c-9534-5801-b3de-4462aee1dac0 | note | Standard - AS/NZS 4130
95de31cc-f3a5-51d5-90fd-1d7105459b3b | note | Signatory - Site Engineer
28bf8af0-51be-4c03-83b9-b63cdf41954c | checkpoint | D2.7 - Trenching and excavation
1f9849d4-5b65-5664-8a3c-204a364ba081 | note | ACTION (W, M, H) - M
d2d821d0-dd19-5960-96d0-d33f042c2d41 | note | Conformance Criteria (What's Required) - In accordance with NZS 4407
560ebf44-5f68-5366-a65d-716ffd42489c | note | Detail - AP65 Subbase particle size and sand equivalent
5051fdca-875b-5a19-b789-6512331ed01a | note | Frequency - Daily
ad4ce273-023d-55ef-b4d7-e95f29de9934 | note | Inspection / Test Method - Inspection
33e332bb-efc7-5786-9e54-2f96f70568ac | note | Verification Records - RCP and digging checklist
60f616cb-80cd-5680-b615-177617b5215f | note | Standard - NZS 4407
db82983d-2f4f-52ae-a468-0471d8c4c642 | note | Signatory - Site Engineer
1124172b-fbbc-477f-b8bd-bfee34c4c935 | checkpoint | D2.9.1 - Pressure testing & disinfection (1)
e7ae8481-5a38-5c25-8a9b-1294f2b190f9 | note | ACTION (W, M, H) - H
a784a435-ffb0-5c02-a04a-049078fafcc5 | note | Conformance Criteria (What's Required) - AS/NZS 2566:2 Section 6.3
5292d590-8f16-5595-864a-9e12f0d7173c | note | Detail - pressure testing of the new PE main
9b637776-a650-5f56-a8f8-7fa3e05d2da2 | note | Frequency - Prior to link in
a2164bb8-5b75-5816-9875-45277524e1df | note | Inspection / Test Method - Testing
edabd17a-6ea3-5468-a553-74d7b1043034 | note | Verification Records - Test records
75e10754-bec8-5393-a944-5a2b7ba8d81f | note | Standard - AS/NZS 2566:2 Section 6.3
5572c361-857e-5e56-b7bb-46031e9f6b25 | note | Signatory - Engineers Representative
9bc27f90-1cbb-416a-914d-f930ced738a0 | signoff | HOLD POINT
ebaad79b-7caa-4fb8-8ce9-a311c26dfb53 | checkpoint | D2.9.1 - Pressure testing & disinfection (2)
fb99b837-e409-51d4-bb16-7fa602352730 | note | ACTION (W, M, H) - H
5a6bdf21-c59f-58c2-91ba-822d8b861b36 | note | Conformance Criteria (What's Required) - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
8af557c3-8560-57d0-aeda-9e836028ff0f | note | Detail - Disinfection of the new PE main
ac45fed7-37b3-5ce9-bb96-0acaedd424e7 | note | Frequency - Prior to link in
5f8de81d-4f48-507b-ad20-47dff8551a5d | note | Inspection / Test Method - Testing
78d09030-2979-53f3-9350-f60b89a67310 | note | Verification Records - Test records
4e448f6a-99fe-5095-967e-1ea9a361705f | note | Standard - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
2a14928e-e4d0-578d-be56-c23c1c9d448f | note | Signatory - Engineers Representative
5bed91dd-1397-4821-8894-643c57ef9bca | signoff | HOLD POINT
ce2b89cc-eca9-41c5-826a-c96e822502d4 | checkpoint | D1.3.3 - Engineer's inspections
d37b7c45-bb3a-5ff8-8401-e9ae10db97e2 | note | ACTION (W, M, H) - H
19dae8b5-3c62-5b6e-95f4-7e75a5002ba3 | note | Conformance Criteria (What's Required) - Inspection report
b07c4d42-dfb5-5aef-8c23-5f0e94a96f94 | note | Detail - Enginer's inspection for pipe, concrete pre pour, pre sealing
6adbc9a6-fa0f-5be9-8bc6-1d3cdc9bdb59 | note | Frequency - As required
81bda805-faa8-579d-a4da-83fc7a7149a0 | note | Inspection / Test Method - Inspection
41ed8a56-aca7-5424-8e61-238b95b49381 | note | Verification Records - Email
12eef62c-7685-522c-b733-0d8e906928af | note | Signatory - Engineers Representative
f1710d1f-ffc7-41db-b501-e0ad2321479b | signoff | HOLD POINT
64997fd5-4977-4d83-b6d3-9ab28338e40e | checkpoint | C1.18 - Surface Reinstatement (1)
e4d48bf4-508e-55fb-ace0-ec8b3bc61605 | note | ACTION (W, M, H) - H
7d359fb5-2d3f-5751-becc-2a9423bd9abe | note | Conformance Criteria (What's Required) - Engineer's Approval
61fef3d4-c11e-5d56-b705-fd92729baf75 | note | Detail - Mark out the trench including overcuts
070ed550-ec09-5da8-9058-2b63545a17ae | note | Frequency - Prior to surfacing
d837fa63-20b9-5faa-aa59-7d81db912a05 | note | Inspection / Test Method - Inspection
4afa4e64-f37b-5945-b050-958baa66dd0c | note | Verification Records - Email
1629c6c8-027c-5daf-8b68-183a7e6b6b45 | note | Signatory - Engineers Representative
63edbee2-5d4f-408a-b226-aeaeb49b7668 | signoff | HOLD POINT
a2d9773e-b633-49bc-bfd7-814f7faf31b8 | checkpoint | C1.18 - Surface Reinstatement (2)
4a90f6d8-cebb-5446-9a5d-f2c9c5a1b5d5 | note | ACTION (W, M, H) - H
31037377-e1b7-5b72-a1cc-af690e4eb845 | note | Conformance Criteria (What's Required) - NDM testing
05fb3d33-8d02-5278-b95e-30747e51aed7 | note | Detail - Provide NDM test results for AP65 and AP40 layers
8b7fe834-dc0f-5e64-ac51-6fef8762f793 | note | Frequency - Prior to surfacing
863410bd-9bf5-57ef-b05e-b9b74108c81c | note | Inspection / Test Method - Testing
ef8ad692-e429-55a6-8b17-50692d103af1 | note | Verification Records - Test records
a7eb20ca-6022-5cc7-8cbd-7f3b4e22d514 | note | Signatory - Engineers Representative
29060417-8ea9-4bfc-8b0c-fadae79b086f | signoff | HOLD POINT
584af932-70fd-4ba0-a7bb-0b2e2554177b | checklist | ITP - Salford, Moana, Wilton, Waihopai Streets - 7.0 Close out documentation | itp | 7.0 Close out documentation
617a1427-7392-42ac-be31-f88c083ed3d7 | section | 7.0 Close out documentation
f6cac46c-e9a5-4073-b1cc-c9fec9df56a2 | checkpoint | C1.13 - As-built
aea6b24b-f3c1-594b-8ead-14894ed1cd36 | note | ACTION (W, M, H) - H
41c6654b-a26d-56ad-803f-fe38ec9b12b0 | note | Conformance Criteria (What's Required) - Ensure as-built data recorded and submitted
0f6acc00-efbe-5a9b-9492-b32378619e91 | note | Detail - Red pen markup drawing
c5ea45c0-a911-51d4-90cb-feb8e19226f3 | note | Frequency - Prior to PCC application
e689e3b3-e440-5be1-8900-350321fd349f | note | Inspection / Test Method - Submission
a0ce884d-2f93-5ea2-8396-57c0096a9d1b | note | Verification Records - Asbuilt plans
05780da2-5684-5143-a27e-15256b6082cd | note | Signatory - Engineers Representative
8419b15c-bdfe-4685-97b5-cc38b2b35493 | signoff | HOLD POINT
a87e10e5-2e48-4962-817c-c2a1f4d36016 | checkpoint | PS3 submission
015891b8-6d23-570a-84bc-e4cd1a3e9574 | note | ACTION (W, M, H) - H
954666cf-65a8-5129-8cd8-81a227c4c1b8 | note | Conformance Criteria (What's Required) - Producer statement for construction to be supplied to client
7f173c5d-27f1-5c2e-b8b8-ecbe2190b507 | note | Detail - As per schedule 6 3910:2013
d6f1e8bc-c555-59fe-bcb8-049031a57be6 | note | Frequency - Prior to PCC application
953f7cbc-b009-57c3-92b9-8fc95da8bb24 | note | Inspection / Test Method - Submission
d6a4c72e-e241-5f31-8f03-e900152f2e86 | note | Verification Records - Email of notice
a951910d-7c97-513a-a050-2d62bfa08c50 | note | Signatory - Engineers Representative
7965134a-db4a-4140-a754-9f9c2b51b26d | signoff | HOLD POINT
6a03559e-4061-48f3-bf7c-03989718195d | checkpoint | WCN and CAR close out
5f48bc45-e27b-58ab-b840-c96305ebf9ee | note | ACTION (W, M, H) - H
4aad57c2-fa78-577b-852c-8d2ff535bb3f | note | Conformance Criteria (What's Required) - To be submitted at completion of works
25949392-658d-5d40-88c8-c85488649380 | note | Detail - Submission to ICC of completion of works in road corridor and close out of CAR
bba2ef79-8163-5af5-b32d-af42070abc94 | note | Frequency - Prior to PCC application
691f81ae-d240-5f49-af18-3520e260c1db | note | Inspection / Test Method - Submission
ecddc479-d3e4-587f-b041-fbc64edfbbd2 | note | Verification Records - PS3 document
3a2f482e-9ad5-56ef-983a-56aac3963657 | note | Signatory - Engineers Representative
0aebe89f-c7a1-4a14-8cd8-7388f866046f | signoff | HOLD POINT
d93833c4-98e9-45a4-8050-bd153917ae90 | checkpoint | QA documents submitted
85359090-f94a-5f8a-abe9-427a47a47aa8 | note | ACTION (W, M, H) - H
a972cc01-9e26-5d90-89cf-72c232fe4c31 | note | Conformance Criteria (What's Required) - All required documents submitted throughout and at conclusion of project
8de02c73-b869-53bf-a272-ea3bd6082b1f | note | Detail - All connection sheets, weld logs, NDM results, destructive testing weld reports, encountered services sheets, construction photographs, any outstanding H&S or non conformance reporting
90975df9-5d0d-5c1f-8aae-ac9274cf34f1 | note | Frequency - Prior to PCC application
7a9c669f-5b2e-585a-9c1c-fc90774ef35c | note | Inspection / Test Method - Submission
8c4b21d6-7aef-5f55-9a11-7457ed2a9186 | note | Verification Records - Various
26673b63-a900-508e-a55d-7b350e7e97dd | note | Signatory - Engineers Representative
736344ec-8b54-4ab6-ace8-51e4e63fb177 | signoff | HOLD POINT