## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | 8.0 Moana Street - Wilton Street to Waihopai Street (DN180mm) | itp |  |  |  |  | ITP - Salford, Moana, Wilton, Waihopai Streets - 8.0 Moana Street - Wilton Street to Waihopai Street (DN180mm)
section | 8.0 Moana Street - Wilton Street to Waihopai Street (DN180mm)
checkpoint | D5.4.2 - Isolation Valve MOANA-WILTON-2 CH769 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 23 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve MOANA-WILTON-2 CH769 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 23 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve MOANA-WILTON-2 CH769 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANA FH 03-2 at CH773 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 23 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANA FH 03-2 at CH773 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANA FH 03-2 at CH773 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#123 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#121 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#120 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#117 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#116 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#113 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#109 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#108 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#105 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANA FH 04 at CH890 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 23 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANA FH 04 at CH890 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANA FH 04 at CH890 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#104 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#100 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#101 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#99 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#96 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#92 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#79 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve MOANA-WAIHOPAI-2 CH962 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 23 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve MOANA-WAIHOPAI-2 CH962 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 23 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve MOANA-WAIHOPAI-2 CH962 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Waihopai Street and Moana Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail K in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Waihopai Street and Moana Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
label | Detail - As per detail K in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Removal of existing tee and bends and reinstated with straight through pipe and associated bends/thrust protection at intersection of Waihopai Street and Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Pipe reinstated through old line and thrust protected
label | Detail - As per detail L in sheet 16 and typical details sheet 18
label | Frequency - per connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4130
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#88 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D2.7 - Trenching and excavation
label | ACTION (W, M, H) - M
label | Conformance Criteria (What's Required) - In accordance with NZS 4407
label | Detail - AP65 Subbase particle size and sand equivalent
label | Frequency - Daily
label | Inspection / Test Method - Inspection
label | Verification Records - RCP and digging checklist
label | Standard - NZS 4407
label | Signatory - Site Engineer
checkpoint | D2.9.1 - Pressure testing & disinfection (1)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - AS/NZS 2566:2 Section 6.3
label | Detail - pressure testing of the new PE main
label | Frequency - Prior to link in
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Standard - AS/NZS 2566:2 Section 6.3
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D2.9.1 - Pressure testing & disinfection (2)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
label | Detail - Disinfection of the new PE main
label | Frequency - Prior to link in
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Standard - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.3.3 - Engineer's inspections
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Inspection report
label | Detail - Enginer's inspection for pipe, concrete pre pour, pre sealing
label | Frequency - As required
label | Inspection / Test Method - Inspection
label | Verification Records - Email
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.18 - Surface Reinstatement (1)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Engineer's Approval
label | Detail - Mark out the trench including overcuts
label | Frequency - Prior to surfacing
label | Inspection / Test Method - Inspection
label | Verification Records - Email
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.18 - Surface Reinstatement (2)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - NDM testing
label | Detail - Provide NDM test results for AP65 and AP40 layers
label | Frequency - Prior to surfacing
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checklist | 9.0 Cruickshank Crescent (DN125mm) | itp |  |  |  |  | ITP - Salford, Moana, Wilton, Waihopai Streets - 9.0 Cruickshank Crescent (DN125mm)
section | 9.0 Cruickshank Crescent (DN125mm)
checkpoint | D8.3, D8.4 - Lateral connection to house no#38 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#23 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#36 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#21 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#34 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#19 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#17 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant CRUICKSHANK FH 03 at CH40 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 23 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant CRUICKSHANK FH 03 at CH40 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant CRUICKSHANK FH 03 at CH40 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#15 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#32 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#30 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#28 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#26 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#24 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant CRUICKSHANK FH 02 at CH177 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 23 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant CRUICKSHANK FH 02 at CH177 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant CRUICKSHANK FH 02 at CH177 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#22 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#20 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#18 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#18A Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#16 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#14 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#12 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#10 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#8 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant CRUICKSHANK FH 01 at CH58 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 23 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant CRUICKSHANK FH 01 at CH58 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant CRUICKSHANK FH 01 at CH58 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#5 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#6 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#4 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#3 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#1 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve CRUIKSHANK-TERRACE CH12 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 23 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve CRUIKSHANK-TERRACE CH12 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 23 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve CRUIKSHANK-TERRACE CH12 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Cruickshank Crescent and Terrace Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail N in sheet 22 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Cruickshank Crescent and Terrace Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed
label | Detail - As per detail N in sheet 22 and typical details as per sheet 24
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#13 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#11 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#9 Cruickshank Crescent
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 23 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D2.7 - Trenching and excavation
label | ACTION (W, M, H) - M
label | Conformance Criteria (What's Required) - In accordance with NZS 4407
label | Detail - AP65 Subbase particle size and sand equivalent
label | Frequency - Daily
label | Inspection / Test Method - Inspection
label | Verification Records - RCP and digging checklist
label | Standard - NZS 4407
label | Signatory - Site Engineer
checkpoint | D2.9.1 - Pressure testing & disinfection (1)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - AS/NZS 2566:2 Section 6.3
label | Detail - pressure testing of the new PE main
label | Frequency - Prior to link in
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Standard - AS/NZS 2566:2 Section 6.3
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D2.9.1 - Pressure testing & disinfection (2)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
label | Detail - Disinfection of the new PE main
label | Frequency - Prior to link in
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Standard - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.3.3 - Engineer's inspections
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Inspection report
label | Detail - Enginer's inspection for pipe, concrete pre pour, pre sealing
label | Frequency - As required
label | Inspection / Test Method - Inspection
label | Verification Records - Email
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.18 - Surface Reinstatement (1)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Engineer's Approval
label | Detail - Mark out the trench including overcuts
label | Frequency - Prior to surfacing
label | Inspection / Test Method - Inspection
label | Verification Records - Email
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.18 - Surface Reinstatement (2)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - NDM testing
label | Detail - Provide NDM test results for AP65 and AP40 layers
label | Frequency - Prior to surfacing
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Signatory - Engineers Representative
holdpoint | HOLD POINT