## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Site Establishment and Safety Checklist
section | Details
checkpoint | Delivery and goods lift location
checkpoint | Delivery requirements i.e. booking process
checkpoint | On site storage / office location
checkpoint | Site specific restrictions i.e. noise / starting times
checklist | Ductwork Checklist
section | Details
checkpoint | Rectangular duct installed as per latest drawing
checkpoint | Duct flanges firmly bolted and sealed where required
checkpoint | Cleats installed as required
checkpoint | Correct hanger spacing / supports installed
checkpoint | DW insulated where required and damage free
checkpoint | Ductwork restrained for wind/seismic where required
checkpoint | Any required ductwork leakage testing
checkpoint | Spiral installed as per latest drawing
checkpoint | Spiral joins sealed correctly
checkpoint | Correct hanger spacing / supports installed for spiral
checkpoint | Spiral insulated where required and damage free
checkpoint | Additional taping/sealing to medium/high pressure spiral
checkpoint | Pops & flex installed as per latest drawing
checkpoint | Correct hanger spacing / supports installed for flex
checkpoint | Free from support off other services
checkpoint | Flexible duct connections completed correctly
checkpoint | Blade dampers installed as documented and left in the open position
checkpoint | BD pop access panel coordinated and marked
checkpoint | Cushion boxes installed as per latest drawing
checkpoint | Balancing dampers installed as documented and left in the open position
checkpoint | Location of register coordinted with other services and marked on plan or floor
checkpoint | Volume Control Dampers installed as per latest drawing
checkpoint | Motorised dampers installed as per latest drawing / actuator fit off
checkpoint | Smoke dampers installed as per latest drawing / actuator fit off
checkpoint | Fire dampers installed as per latest drawing / access panel in DW where required
checkpoint | Damper access panels coordinated and marked
checkpoint | Photos of ductwork correctly sealed through smoke wall & smoke damper
checklist | Indoor Equipment
section | Details
checkpoint | Indoor Unit (IDU) correctly supported as per project engineering requirements
checkpoint | Correct IDU installed as per latest drawing
checkpoint | Flexible connections installed and sealed
checkpoint | Access to filter bank / filters installed
checkpoint | Access to all relevant controls and isolators
checkpoint | IDU access panel coordinated and marked
checkpoint | Ventilation fan correctly supported as per project engineering requirements
checkpoint | Correct fan installed as per latest drawing
checkpoint | Fan connections secured and sealed
checkpoint | Access to fan and isolator
checkpoint | Ventilation fan access panel coordinated and marked
checkpoint | Correct VAV installed as per latest drawing
checkpoint | Access to VAV and controls
checkpoint | VAV access panel coordinated and marked
checklist | Grille Fit-Off Checklist
section | Details
checkpoint | Grilles installed in correct location as per latest duct layout / RCP
checkpoint | Correct grille type installed
checkpoint | Grille installed flush and square
checkpoint | Are all grilles installed correctly? Air leaks, vibration or failure
checkpoint | Grille color as per schedule
checkpoint | Grille left clean of fingerprints and caps installed where required
checkpoint | Grille fit-Off completed to drawings/specification & Area left clean/tidy (Any Issues comment below)
checklist | All Subbie Rough-in Progression Checklist
section | Details
checkpoint | All work in zone completed and appear compliant
label | Pass once all work complete
checklist | All Subbie Fit off & Testing Progression Checklist
section | Details
checkpoint | All work in zone completed and appear compliant
label | Pass once all work complete
checklist | As Builts Checklist
section | Details
checkpoint | Update As-Built's of any known changes
checklist | Pipework Checklist
section | Details
checkpoint | Pipework installed as per latest drawings
checkpoint | Pipework installed level and free of damage
checkpoint | All joins welded / crimped as per manufacturer's instructions
checkpoint | Air bleeds installed in pipework where required
checkpoint | Riser or area branch valve access panel coordinated and marked
checkpoint | Correct hanger spacing / supports installed for pipe runs
checkpoint | No other services suspended from pipework
checkpoint | Correct coil valves installed as per schedule
checkpoint | Test points, drains and bleeders installed where required
checkpoint | Coil valves accessible and not blocking any service points
checkpoint | Coil valveset access panel coordinated and marked
checkpoint | Correct coil valves installed as per schedule
checkpoint | Test points, drains and bleeders installed where required
checkpoint | Coil valves accessible and not blocking any service points
checkpoint | Coil valveset access panel coordinated and marked
checkpoint | HHW Pressure Test – ITR attached
checkpoint | HHW Flushed - plan, photos of flow readings and water quality attached
checkpoint | Drain trapped where required
checkpoint | Correct hanger spacing / fall
checkpoint | Drain tested
checkpoint | Drain pump installed level and tested
checkpoint | Drain terminates at a tundish
checkpoint | Drains, pump and tundish access for maintenance.
checklist | Pipework Testing
section | Details
checkpoint | Pipe tested and recorded as per Pipe Testing ITP
checkpoint | Initial pipe pressure test (attach photo)
checkpoint | 24hr pipe pressure test (attach photo)
checkpoint | Piping cleaned and flushed
checklist | Drains
section | Details
checkpoint | Drain trapped where required
checkpoint | Drain pump installed on a gradient/ level
checkpoint | Drain terminates at a tundish
checkpoint | Drain pipe insulated where required
checkpoint | Drains, pump and tundish access for maintenance
checkpoint | Drain pipe is labelled clearly
checklist | VAV Checklist
section | Details
checkpoint | Unit installed as per latest drawing
checkpoint | Inspect the unit casing is not damaged. Record and report for any issues
checkpoint | Unit is labelled clearly
checkpoint | Unit correctly supported as per documented
checkpoint | Confirm test points, sensors and pressure points have been provided and installed as documented
checkpoint | Confirm electrical connection to unit
checkpoint | Confirm ductwork connections to the unit are correct
checkpoint | Unit complete with acoustic wrapping as per documented
checkpoint | Adequate maintenance clearance maintained
checkpoint | Installed as per manufacturer's requirements. Refer to specific equipment schedule for detail