## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | ITP-007A - Lighting Control DALI & CBUS Rough In |  |  |  |  | Yes | ITP-007A - Lighting Control DALI & CBUS Rough In | 35755d57-53d7-489b-994a-59a095d474b1
checkpoint-status |  |  | checkpoint | Cbus Rough In Complete
checkpoint-status |  |  | checkpoint | DALI Rough In Complete
checklist-flat |  |  | checklist | ITP-003B - Sub-Mains - Fit Off, Commissioning & Verification |  |  |  |  | Yes | ITP-003B - Sub-Mains - Fit Off, Commissioning & Verification | 3acbaa83-091e-45e6-999d-86fef2437174
checkpoint-status |  |  | checkpoint | Fit-Off Complete
label | 318381d0-e350-58f9-881d-637c582bf236 |  | note | Connections Tight
label | 6a5d3aa1-9339-5b17-afb6-ae970f753e0e |  | note | Glands Tight
checkpoint-status |  |  | checkpoint | Commissioning Complete
label | dc2c6af4-eb4f-5d97-871a-1788724b2cdf |  | note | Cable is Labelled
label | 20bca091-6d35-5acb-8364-0aa3fdc62df5 |  | note | Test results passed and attached below
checklist-sectioned |  |  | checklist | ITP-005 - Switchboards Installation & Commissioning (V.031121) |  |  |  |  | Yes | ITP-005 - Switchboards Installation & Commissioning (V.031121) | 3c9db1f1-5dd1-4ad1-b8e1-e9228512b65c
checkpoint-group |  |  | section | Identification
checkpoint-status |  |  | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 492c2e6a-d6df-5507-aca5-8cd84a52d984 |  | textbox | Drawing & revision number(s)
label | 686c961f-5ceb-5e43-9145-ce27663ce261 |  | note | All inspections are to be completed in accordance with the specification and AS/NZS3000:2018
checkpoint-status |  |  | checkpoint | Switchboard Type - Pass once entered
select | d4f93f05-bba1-59ca-98b5-29aaa4a1765e |  | dropdown | Type | Main Switchboard,Distribution Board,Controls Panel,Meter Panel,Other (Specify Below)
text | cfd34249-c352-554d-bfab-48a8062f494c |  | textbox | If other selected above, please specify
text | d77e0ed3-0a94-514e-89ca-1423f32c143a |  | textbox | Switchboard Name
text | 257dd958-dfdd-5a8b-adf6-7b7a815c0901 |  | textbox | Isolation Device
text | dd04ea8a-5048-57ee-bc4d-24f03288bee8 |  | textbox | Board Location
button | aa1e722a-fcf0-520c-b7c0-713794e40fe5 |  | button | Generator Back-up Verified | Yes,No,N/A
text | 043fb32f-a15b-5777-b935-1882f0e04275 |  | textbox | MEN Location
select | 7cd6d5d8-69ff-556f-9d60-4ffdcc648679 |  | dropdown | Earth size | 1mm,1.5mm,2.5mm,4mm,6mm,10mm,16mm,25mm,35mm,50mm,70mm,95mm,120mm,150mm,185mm,240mm,300mm,400mm,500mm,630mm
checkpoint-status |  |  | checkpoint | Cable details - Pass once entered
text | 00ca1a09-7d4b-5dfe-8308-62ca3213cf05 |  | textbox | Cable No.
select | f0394837-99ec-5f0a-8f04-b18f9b599928 |  | dropdown | Protection Device Type | HRC Fuse,MCB,ACB,N/A,Other (Specify Below
text | a49af466-ad69-514b-a52f-96c9fe550993 |  | textbox | If other selected above, please specify
select | 112479e3-f390-51ff-bcc0-33299564a6a1 |  | dropdown | Protective device rating | 6 amps,10 amps,16 amps,20 amps,25 amps,32 amps,40 amps,50 amps,63 amps,80 amps,100 amps,125 amps,150 amps,160 amps,200 amps,250 amps,315 amps,400 amps,500 amps,630 amps,800 amps,1000 amps,1600 amps,2000 amps,2500 amps,3000 amps,3200 amps
text | 7b041c6e-6bae-56d7-bb22-6b5a7ab19b53 |  | textbox | Cable Origin
text | 418f4224-8bb3-539c-b36e-7e546ecac4fc |  | textbox | Cable Destination
select | 00e5c17e-1e4d-5c50-aaec-e14ca792b1a0 |  | dropdown | No. of conductors per phase | N/A,1,2,3,4,5,6,7,8,9,10
button | 3e9bb438-13d3-595d-80aa-72ef166df9db |  | button | Multicore or SDI (Select One) | Multicore,SDI
button | 6b2971b1-eca9-5a4b-bc69-5f60ec77b167 |  | button | PVC, XLPE, Fire Rated (Select One) | PVC,XLPE,Fire Rated
button | b11987d5-ee6e-5d78-8331-b8cfc7184b0d |  | button | Copper (CU) or Aluminium (AL) | CU,AL
select | cd6b67a9-232f-595e-a305-071f2bbd4e84 |  | dropdown | Size of active conductors | 1mm,1.5mm,2.5mm,4mm,6mm,10mm,16mm,25mm,35mm,50mm,70mm,95mm,120mm,150mm,185mm,240mm,300mm,400mm,500mm,630mm,Busduct
select | 0cb9b5c4-1b74-5e59-adb3-89bf2b1f9bae |  | dropdown | Earth size | 1mm,1.5mm,2.5mm,4mm,6mm,10mm,16mm,25mm,35mm,50mm,70mm,95mm,120mm,150mm,185mm,240mm,300mm,400mm,500mm,630mm
checkpoint-group |  |  | section | Completed items checks
checkpoint-status |  |  | checkpoint | Switchboard fixed into place
label | f1904545-df79-59e0-b9fe-9ee7d67c65db |  | note | Attach photos below as applicable
checkpoint-status |  |  | checkpoint | Supply cable terminated & checked
checkpoint-status |  |  | checkpoint | Supply Earth cables terminated & checked
checkpoint-status |  |  | checkpoint | All Labels Installed
button | 9af2aabc-8f13-5c3d-a69b-abd433682a6b |  | button | Switchboard Vacuumed and cleaned | Yes,No,N/A
button | b6b92c29-d06c-579b-a9f3-ad967264cc83 |  | button | Circuit schedules in place | Yes,No,N/A
checkpoint-status |  |  | checkpoint | BMS Interfaces connected
checkpoint-status |  |  | checkpoint | Controls cables connected
checkpoint-status |  |  | checkpoint | Insulation Resistance checks completed. Refer ITPs
label | be157dfc-b787-539f-a6e9-9e268e263dab |  | note | Attach evidence below as applicable
checkpoint-status |  |  | checkpoint | Earth Continuaity Tests completed. Refer ITPs
label | 31727804-f869-5a74-a3c5-53072532a79f |  | note | Attach evidence below as applicable
checkpoint-status |  |  | checkpoint | Polarity and connection checks. Refer ITPs
label | 8c65dfac-a007-5c26-88b1-4d3cf32ba30f |  | note | Attach evidence below as applicable
checkpoint-group |  |  | section | Verification
checkpoint-status |  |  | checkpoint | Ready for Energisation
checkpoint-status |  |  | checkpoint | Post Energisation checks completed
label | 94ad0c14-117c-5b10-a4c3-034bf6d68b1b |  | note | Attach photos/comments below as applicable
checkpoint-status |  |  | checkpoint | Surge Divertors on after energisation
checkpoint-status |  |  | checkpoint | Installation & Commissioning completed to specifications
label | 5d962ce7-e03a-573f-9cdf-a154b3662c52 |  | note | Any issues comment/photo below
text | c447c03c-852a-500e-be11-1e98657430f9 |  | textbox | Name of Person Completing checks
text | 8704ebdf-8e04-56cb-8d72-4091d0f61006 |  | textbox | License No.
text | 5c7d9dbc-c9f7-5fc1-908a-321a2ef18fd2 |  | textbox | Energisation Date
checklist-sectioned |  |  | checklist | ITP-006 - Communications Cabling Installation Installation (V.100321) |  |  |  |  | Yes | ITP-006 - Communications Cabling Installation Installation (V.100321) | 40c2ea59-d842-4e8d-8bd5-ce3cff7e6f29
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 67cb66e3-08e0-5fc4-bb76-7fa520f209de |  | textbox | Drawing & revision number(s)
label | 21f9e6dc-e67a-507b-b84b-e1d1f6f60581 |  | note | All inspections are to be completed in accordance with the specification and AS/NZS3000:2018
checkpoint-status |  |  | checkpoint | Cabling Details - Pass once entered
text | 888ef0be-2e79-5265-b436-83f4025e8d57 |  | textbox | Cable No.
text | 1b838ec6-27df-5b94-b414-8b9f8f5568fb |  | textbox | Description of cable installation, Destination and origin etc
select | 16b65d0b-a05e-5643-9599-f6dfd7ad47e3 |  | dropdown | Cable Type, Copper / Fibre, TV | MMOF,SMOF,CAT 6 UTP,CAT 6A UTP,RG6 QS,RG10 QS,CAT 3
select | 24d8c9bb-9974-5d27-a918-fb9b267f7cf2 |  | dropdown | No. of cables | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24
select | c2b9057a-a08e-5938-ac05-a1631afed230 |  | dropdown | No. of Cores or pairs | 2 Core,4 Core,6 Core,12 Core,24 Core,36 Core,1 Pair,2 Pair,4 Pair,10 Pair,15 Pair,20 Pair,25 Pair,50 Pair,100 Pair,N/A
checkpoint-group |  |  | section | Installation checks
checkpoint-status |  |  | checkpoint | Details of checks - Pass once read & below completed
label | 7ecd3609-f3a7-51e3-b941-1f052bc1b1b1 |  | note | Select - "Y" Completed. "X" not done. "N/A" Not applicable
label | 60c2bbe9-26ea-511a-8c7f-6e5387bc33c3 |  | note | Attach photos/comments below as applicable
button | 546ff797-cc02-5f3a-8a32-96f387af0e3a |  | button | Bend Radius | Yes,No,N/A
button | 046d4f1b-e94b-562e-9fba-4ed1ea472cf9 |  | button | Segregation & separation | Yes,No,N/A
button | 7f932246-041d-5f2b-8cb5-ba8368569e7f |  | button | Correct fixings & supports | Yes,No,N/A
button | 749da506-093f-519c-800d-733501d71ad4 |  | button | Cables labelled at both ends | Yes,No,N/A
button | 6e97172e-926e-5dbb-ae10-ca08cb6669db |  | button | Correct cable grouping | Yes,No,N/A
button | 80dc3d6f-07c0-5691-9431-8d74bf16025e |  | button | Comms Racks correctly installed & size | Yes,No,N/A
button | 7b508b5d-a056-5a6b-bd61-c200c6fe9a82 |  | button | Patch panels or frame labelled | Yes,No,N/A
checkpoint-status |  |  | checkpoint | Test equipment calibrated
checkpoint-status |  |  | checkpoint | Tested to correct standard & passed
checkpoint-status |  |  | checkpoint | Mark Up drawings completed - Attached as applicable
boolean | 6977032f-e2d2-5af1-b953-b77399e694ed |  | tickbox | Area clean & safe
checkpoint-group |  |  | section | Verification
checkpoint-status |  |  | checkpoint | Installation completed to specifications
label | 802c5132-a016-5991-81ab-ef10a0a36915 |  | note | Any issues comment/photo below
text | 4bb2fb15-37b0-5089-9da4-7789d56e847a |  | textbox | Length
text | 42b15c27-3416-5ec5-b117-8af858e4102b |  | textbox | Installers Name
text | f79ce02f-448e-5044-9f10-a331c4e5576c |  | textbox | Date
checklist-flat |  |  | checklist | ITP-001 - Conduit Installation |  |  |  |  | Yes | ITP-001 - Conduit Installation | 4aa2407c-0730-449b-be77-87fd894ee6be
checkpoint-status |  |  | checkpoint | Check existing services, correct location & permit approval
checkpoint-status |  |  | checkpoint | Correct Depth/Cover
checkpoint-status |  |  | checkpoint | Tied and joins glued
checkpoint-status |  |  | checkpoint | Ends sealed
checkpoint-status |  |  | checkpoint | Area clean and safe
checkpoint-status |  |  | checkpoint | Drawings marked up with changes
checkpoint-status |  |  | checkpoint | Ready for wall sheeting, wall closure or column sleeve
text | 4a5dc7d1-9843-5e3f-9c8e-4aa9d0f915b5 |  | textbox | Name of Installer
text | 11c3ac59-1384-59a4-8a7b-ee2b15c2a728 |  | textbox | Date Installed
checklist-flat |  |  | checklist | Details - ITP (V.030921) |  |  |  |  | Yes | Details - ITP (V.030921) | 53e1e092-cb52-4ff4-bd4b-72da572409d1
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 6a38006c-7ac9-5bf5-aae5-e94d08a7c964 |  | textbox | Drawing & revision number(s)
label | 607f9067-09ab-58c7-8de4-be0420f86dee |  | note | All inspections are to be completed in accordance with the specification and AS/NZS3000:2018
button | ea77e5f4-8d51-573d-b1b9-163fa57633e0 | DataPoint is missing 'button' values | button | Confirm area of work is accessible & acceptable to commence (If not comment below)
checklist-flat |  |  | checklist | ITP-008 - Emergency Lighting Test Sheet |  |  |  |  | Yes | ITP-008 - Emergency Lighting Test Sheet | 59d2b59e-e1a5-430f-aafc-ce5ef5367033
checkpoint-status |  |  | checkpoint | Test sheet uploaded below
checklist-flat |  |  | checklist | ITP-007B - Lighting Control DALI & CBUS Fit Off |  |  |  |  | Yes | ITP-007B - Lighting Control DALI & CBUS Fit Off | 5d6b7127-9a85-4a86-90ec-bd782294e3f5
checkpoint-status |  |  | checkpoint | Cbus Fit Off Complete
checkpoint-status |  |  | checkpoint | DALI Fit Off Complete
checklist-flat |  |  | checklist | ITP-007A-Lighting Control (Dali) rough-in (V.171121) |  |  |  |  | Yes | ITP-007A-Lighting Control (Dali) rough-in (V.171121) | 6697fd0b-deb8-41d6-ad19-54bb9c1b1f6a
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | a083958a-ae9e-59fe-816c-b1b729279f3f |  | textbox | DALI No / Relay No
text | 51b711a8-9051-520d-9271-ed10f050caa8 |  | textbox | Circuit Attched
text | 4a27b31e-8f7c-558e-baf6-346bdd5c63a2 |  | textbox | Rough-In feed start location
text | 049a4637-8dc7-5127-9279-d39a42734906 |  | textbox | Loops/Backbone
text | ae09b70c-9599-5219-b586-4a9b2ec1ae3c |  | textbox | Finish Location
select | 07a980a0-2e03-5f68-9644-dcb22cf1a4f9 |  | dropdown | Control Type | Dali,DMX,DSI,Relay,Other (Specify Below)
text | f4326e20-5086-525f-9d8c-1080f6abe823 |  | textbox | Other (Specify Here)
select | 79f9c028-07f3-52eb-944d-92aca84f6588 |  | dropdown | Type of Cable Installed | Twin 1.5,Twin 2.5,CAT5e,CAT6a,Dyna Liite,CBUS,Two Pair Shielded,Other (Specify below)
text | c4d9a917-45d0-56b3-8e5d-fbb52ea87848 |  | textbox | Other (Specify Here)
select | 3f2b2a45-9bfb-51f7-b7a4-e438ffc8a647 |  | dropdown | No. of ights per Universe | 0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41,42,43,44,45,46,47,48,49,50,51,52,53,54,55,56,57,58,59,60,61,62,63,64,65
checklist-flat |  |  | checklist | ITP-009 - Energy Meter Validation Test Sheet |  |  |  |  | Yes | ITP-009 - Energy Meter Validation Test Sheet | 67d2386f-24e3-4e71-958b-fcc30318ad56
checkpoint-status |  |  | checkpoint | Test sheet uploaded below
checklist-flat |  |  | checklist | Single Circuit - ITP-004 - Sub circuit Installation & Commissioning ITP (V.031121) |  |  |  |  | Yes | Single Circuit - ITP-004 - Sub circuit Installation & Commissioning ITP (V.031121) | 77d75821-450a-4add-a4f4-c439641568c3
checkpoint-status |  |  | checkpoint | Circuit details - Pass once entered
text | 35420105-e83c-5e6f-ae9c-e32022017c65 |  | textbox | Circuit Description (Input if known, if not leave till Commissioning)
select | 80a2449e-d628-5d98-aba8-6c648a519df5 |  | dropdown | CB / RCD No. | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41,42,43,44,45,46,47,48,49,50,51,52,53,54,55,56,57,58,59,60,61,62,63,64,64,65,66,67,68,69,70,71,72,73,74,75,76,77,78,79,80,81,82,83,84,85,86,87,88,89,90,91,92,93,94,95,96,97,98,99,100,101,102,103,104,105,106,107,108,109,110,111,112,113,114,115,116,117,118,119,120,121,122,123,124,125,126,127,128,129,130
select | 22474421-b0d5-56b9-a2f0-e9d92932546c |  | dropdown | CB / RCD / Fuse Size in amps | 6 amps, 10 amps, 16 amps, 20 amps, 25 amps, 32 amps, 40 amps, 50 amps, 63 amps, 80 amps, 100 amps, 125 amps, 150 amps, 160 amps, 200 amps, 250 amps, 315 amps, 400 amps, 500 amps, 630 amps, 800 amps, 1000 amps, 1600 amps, 2000 amps, 2500 amps, 3000 amps, 3200 amps
select | 56fc503e-03cd-514a-a28a-5a0a8e2ee096 |  | dropdown | Protective Device type | RCD,RCBO,CB,FUSE
select | 4fda63a1-2f20-537d-bfb7-4f87e9c3d8ec |  | dropdown | RCD Rating | 10mA,30mA,100mA
select | b33eec39-459f-5096-b416-ff7b8f933f60 |  | dropdown | Size of active conductors | 1mm Twin,1.5mm Twin,2.5mm Twin,4mm Twin,6mm Twin,1mm Twin & E,1.5mm Twin & E,2.5mm Twin & E,4mm Twin & E,6mm Twin & E,10mm Twin & E,16mm Twin & E,25mm Twin & E,16mm Twin,25mm Twin,1.5mm 4Core & E,2,5mm 4Core & E,4mm 4Core & E,6mm 4Core & E,10mm 4Core & E,16mm 4Core & E,25mm 4Core & E,35mm 4Core & E,50mm 4Core & E,70mm 4Core & E,95mm 4Core & E,1.5mm SDI,2.5mm SDI,4mm SDI
select | b7d7bd35-035b-5dbe-9ac9-478014414def |  | dropdown | Earth size | 1mm, 1.5mm, 2.5mm, 4mm, 6mm, 10mm, 16mm, 25mm, 35mm, 50mm, 70mm, 95mm, 120mm, 150mm, 185mm, 240mm, 300mm, 400mm, 500mm, 630mm
text | d7455ac0-8ba6-5305-ad3b-9666b75c9cb9 |  | textbox | Circuit Notes
select | 5506557e-6ea6-52ff-92f9-b30d1334500e |  | dropdown | No. of Points | N/A,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40
checkpoint-status |  |  | checkpoint | Rough-In Complete (Feeds)
label | 447cdb78-dec7-55c6-8d17-be0b8b87019a |  | note | Attach photos below as applicable
checkpoint-status |  |  | checkpoint | Second Rough in (Loops)
label | e71fe92a-c1c0-5a1e-af91-bec3bccd3f20 |  | note | Attach photos below as applicable
checkpoint-status |  |  | checkpoint | Fit-Off Complete
label | affd7b9d-41ba-53c5-bdf1-f335fa6b6af9 |  | note | Attach photos below as applicable
checkpoint-status |  |  | checkpoint | Commissioning Results - Pass once entered
select | 3c425df9-7714-5e8f-8a5e-b803353a2a0e |  | dropdown | Earth Resistance test result in ohms | 0.00?,0.01?,0.02?,0.03?,0.04?,0.05?,0.06?,0.07?,0.08?,0.09?,0.10?,0.11?,0.12?,0.13?,0.14?,0.15?,0.16?,0.17?,0.18? 0.19?,0.20?,0.21?,0.22?,0.23?,0.24?,0.25?,0.26?,0.27?,0.28?,0.29?,0.30?,0.31?,0.32?,0.33?,0.34?,0.35?,0.36?,0.37?,0.38?,0.39?,0.40?,0.41?,0.42?,0.43?,0.44?,0.45?,0.46?,0.47?,0.48? 0.49?,0.50?,Fail
label | a78b8736-906b-5230-a4c0-907973af4e38 |  | note | < 0.5m? Clause 8.3.5
button | 0eecca8a-0d0e-5a4f-86cb-e734c15eab7d |  | button | L-L Insulation Resistance test result | >1m?,Fail
label | c50a1560-2f67-5877-8191-e2b431aade86 |  | note | > 1m? Clause 8.3.6
button | 43ba796c-5fa6-53f1-8e78-b9a916a9f3b7 |  | button | L-E Insulation Resistance test result | >1m?,Fail
label | b617652f-d74f-579c-8689-00272d40a989 |  | note | > 1m? Clause 8.3.6
checkpoint-status |  |  | checkpoint | Polarity & Circuit connections
label | 871dee0e-eabb-52d1-8dfe-a8a1a9a3ed5a |  | note | Clause 8.3.7 & 8.3.8
button | b821aa2e-00e2-5c27-8374-38e81d85db13 |  | button | L1 (Red) | Yes,No
button | ead3c522-0d1b-51ab-86ba-897f3fdcf49d |  | button | L2 (White) | Yes,No
button | cf25c4bd-b5cb-5207-9ac0-3ae689600777 |  | button | L3 (Blue) | Yes,No
button | 11fb72e1-fd7c-54f8-8430-9787839d2de6 |  | button | N | Yes,No
button | 098f4a63-b61f-5408-a7eb-1dc6fdb5fc7b |  | button | E | Yes,No
checkpoint-status |  |  | checkpoint | Fault Loop Impedance - Clause 8.3.9 (Not required if RCD protected)
text | 2aa890ed-0e09-5cf4-8880-e2171c4c82e3 |  | textbox | Earth Resistance Re ?
text | 78a6b420-fe26-5be6-a124-39333a4eeb72 |  | textbox | Earth Resistance Rpe ?
checkpoint-status |  |  | checkpoint | RCD Acceptance (30mA times checked and correct)
label | 7388c265-e943-5fd9-9577-6fb01b902447 |  | note | X0.5 Trip Time
text | 18815de2-0998-51b1-8ebc-3d98d0db836f |  | textbox | 0.Deg (ms)
text | 34dc9833-f45d-5120-a447-c9beb88cb520 |  | textbox | 180.Deg (ms)
label | 008ac486-94d6-5fbf-818b-afced90867ba |  | note | .. ..
label | 91b108b8-32ba-50be-aa31-9e55a4ed4afb |  | note | X1 Trip Time
text | 66cda19e-b212-5047-8cab-5457e6ccb870 |  | textbox | 0.Deg (ms)
text | 47146fcc-a600-583a-9e3c-48f599637bf5 |  | textbox | 180.Deg (ms)
label | 24e8f7e8-89d0-5dd3-a682-de234e593445 |  | note | .. ..
label | 551df5d4-c004-59fb-a8a5-b81cc1324444 |  | note | X2 Trip Time
text | 41c29c5e-b2fb-5ae9-868b-98628bdf1927 |  | textbox | 0.Deg (ms)
text | 234f34d2-e89b-5c0f-babd-0a5a9b98e411 |  | textbox | 180.Deg (ms)
label | 713c8c16-964f-55b8-bdc4-2f2105dfaf5b |  | note | .. ..
label | 674a7bd4-3a26-583c-9950-ed04bafa6df2 |  | note | X5 Trip Time
text | bdf87615-1628-565c-b932-482185207990 |  | textbox | 0.Deg (ms)
text | 13c4117b-eb1c-53e7-bba6-6f0d61a5f588 |  | textbox | 180.Deg (ms)
label | c94ac6f1-a078-5e46-823e-c3ca2219afde |  | note | .. ..
label | d4a303c5-26b9-5691-822a-ae53fde1e492 |  | note | ImA
text | e923e4f2-eb7e-5bed-bf86-e769d5affd76 |  | textbox | 0.Deg (ms)
text | 5d7af6b7-d616-5d32-934d-b979703130a5 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 89b9b4b8-a604-519a-80f4-df1711023963 |  | textbox | Action taken
checkpoint-status |  |  | checkpoint | Trip test button
checkpoint-status |  |  | checkpoint | Installation & Commissioning completed to specifications
label | 9c9c8276-8a33-52e0-ac65-7c452f592e4d |  | note | Any issues comment/photo below
text | a61aa8f6-a7f4-596a-a7f3-c93f95c1eac6 |  | textbox | Electrician Name
text | caa5c99c-f097-5776-9498-f08d08adc742 |  | textbox | License No.
checklist-flat |  |  | checklist | ITP-008 - Emergency Lighting Installation & Test Sheet (V.100321) |  |  |  |  | Yes | ITP-008 - Emergency Lighting Installation & Test Sheet (V.100321) | 7e5221e5-acc3-434c-8d8c-97ed70f15857
checkpoint-status |  |  | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
text | 2f22b374-23ff-5f62-bfd6-e366d80cdf18 |  | textbox | Drawing & revision number(s) - If applicable
checkpoint-status |  |  | checkpoint | Test Details - Pass once entered
text | 5db74ebc-413f-5733-8f1d-5fcecab3ce21 |  | textbox | Fitting No.
text | 064a5da8-94dc-54a2-97c3-03dda7e24c37 |  | textbox | Location of Fitting
text | 3b959d53-cc41-55f7-984e-1702eaf06674 |  | textbox | Type of Unit
text | 426d5e6f-6ab6-52e4-bfeb-62e09e0a61a9 |  | textbox | DB Number
text | ed12ab1c-ca3f-5fae-aabe-b2bcc4dc150d |  | textbox | CCT No.
text | df5eaa3b-5ba0-52d5-9b97-47f2e59622d4 |  | textbox | Start Time
text | ecfc0017-673c-5464-9207-e18e04b58ff1 |  | textbox | Finish Time
checkpoint-status |  |  | checkpoint | 6 monthly test Mains Operation
label | 67f504f4-270c-50e7-a3ae-958d26083877 |  | note | Photos/Comments added below as apllicable
text | 391fb609-0821-5367-92ac-bef2aee0683c |  | textbox | Test Date
checkpoint-status |  |  | checkpoint | 6 monthly test Emergency Operation
label | c38eab56-4697-5b50-8afe-bbe77fe11702 |  | note | Photos/Comments added below as apllicable
text | e05e219c-0e4a-5790-a696-3e175a3ed386 |  | textbox | Test Date
checkpoint-status |  |  | checkpoint | Testing completed to specifications
label | 15e35ca6-d8ca-504b-a3fa-64dfe05a0f6e |  | note | Any issues comment/photo below
text | 1174f43e-3871-5594-b908-e1823d7ab1e9 |  | textbox | Name of Person Completing checks
text | 71ec4c55-7e33-5875-9344-79437d498174 |  | textbox | License No.
checklist-flat |  |  | checklist | ITP-002 - Cable Tray Installation |  |  |  |  | Yes | ITP-002 - Cable Tray Installation | 7f4f0473-6870-4479-96ff-591c686f48e0
checkpoint-status |  |  | checkpoint | Cable Tray details entered below
text | b3a3ff64-1235-5951-9088-9468ef0eb66d |  | textbox | Cable Tray Description
text | 528a8584-e55c-509b-a5a2-a82b2950656f |  | textbox | All tray sizes
button | bc2c9e32-5e8d-5029-8b53-2fd16b9180f2 |  | button | Fire Rated Tray | Yes,No,N/A
checkpoint-status |  |  | checkpoint | Supports installed & correct spacing
checkpoint-status |  |  | checkpoint | Trays earthed - Where applicable
checkpoint-status |  |  | checkpoint | Seismic bracing installed & Certified where required
checkpoint-status |  |  | checkpoint | Cables installed - Built representative, Ion foreman and Subcontractor signoffs attached below
holdpoint |  |  | signoff | Request Signoff
checkpoint-status |  |  | checkpoint | Service penetrations fire or smoke sealed where required
checklist-flat |  |  | checklist | ITP-004A - Sub circuit Installation |  |  |  |  | Yes | ITP-004A - Sub circuit Installation | 8b6cadb8-83d4-412e-a844-40acce180eab
checkpoint-status |  |  | checkpoint | Circuit details uploaded below
checkpoint-status |  |  | checkpoint | Rough-In Complete (Feeds)
checkpoint-status |  |  | checkpoint | Second Rough in (Loops)
checklist-sectioned |  |  | checklist | ITP-003 - Sub-Mains Installation & Commissioning (V.031121) |  |  |  |  | Yes | ITP-003 - Sub-Mains Installation & Commissioning (V.031121) | 8e8422d1-4f60-4071-8b16-573af5a8c4c4
checkpoint-group |  |  | section | Circuit Information
checkpoint-status |  |  | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | f458420a-a5bb-5343-93cf-0c815af6e5b4 |  | textbox | Drawing & revision number(s)
label | a6ed3f9c-8192-5956-bf6e-ccddb531d89d |  | note | All inspections are to be completed in accordance with the specification and AS/NZS3000:2018
checkpoint-status |  |  | checkpoint | Cable details - Pass once entered
text | a81b5beb-da46-5c4a-bfd1-a17853153801 |  | textbox | Cable No.
select | 1765e7f8-23bc-5a1a-a2d5-e2d9129c65ed |  | dropdown | Protection Device Type | HRC Fuse,MCB,ACB,N/A,Other (Specify Below
text | 9eabb4a8-3b5c-59ba-a1c5-6cecbf1165da |  | textbox | If other selected above, please specify
select | 4d1712ff-fe5c-59e7-b2dd-358ea4473743 |  | dropdown | Protective device rating | 6 amps,10 amps,16 amps,20 amps,25 amps,32 amps,40 amps,50 amps,63 amps,80 amps,100 amps,125 amps,150 amps,160 amps,200 amps,250 amps,315 amps,400 amps,500 amps,630 amps,800 amps,1000 amps,1600 amps,2000 amps,2500 amps,3000 amps,3200 amps
text | 395bf389-9a47-50e4-bf85-86d9cdbbd017 |  | textbox | Cable Origin
text | e8f24f45-3e50-5295-82f8-eba1e7b16a97 |  | textbox | Cable Destination
select | 733e645b-8f26-57ee-9de7-a7943a360058 |  | dropdown | No. of conductors per phase | N/A,1,2,3,4,5,6,7,8,9,10
button | 34da4ec7-a8fd-521f-88cc-0c3de3ad872a |  | button | Multicore or SDI (Select One) | Multicore,SDI
button | 32e14d56-1790-5b6a-b504-74ee5ba321b2 |  | button | PVC, XLPE, Fire Rated (Select One) | PVC,XLPE,Fire Rated
button | da53063c-3126-5e8a-82ce-4a30c480b8e2 |  | button | Copper (CU) or Aluminium (AL) | CU,AL
select | 866bf03c-d42b-538b-a53a-6a8d5aa39a81 |  | dropdown | Size of active conductors | 1mm,1.5mm,2.5mm,4mm,6mm,10mm,16mm,25mm,35mm,50mm,70mm,95mm,120mm,150mm,185mm,240mm,300mm,400mm,500mm,630mm,Busduct
select | 12584e80-f0f7-5eba-a1c4-a686e5d90674 |  | dropdown | Earth size | 1mm,1.5mm,2.5mm,4mm,6mm,10mm,16mm,25mm,35mm,50mm,70mm,95mm,120mm,150mm,185mm,240mm,300mm,400mm,500mm,630mm
checkpoint-group |  |  | section | Installation Pre-Commissioning checks
checkpoint-status |  |  | checkpoint | Rough-In Complete
label | 978d60e3-e004-5499-8925-2383e31ea700 |  | note | Attach photos below as applicable
checkpoint-status |  |  | checkpoint | Fit-Off Complete
label | 090de9c1-b7a5-5358-b059-392750322293 |  | note | Attach photos below as applicable
checkpoint-status |  |  | checkpoint | Connections Tight
checkpoint-status |  |  | checkpoint | Glands Tight
checkpoint-status |  |  | checkpoint | Cable is Labelled
checkpoint-group |  |  | section | Commissioning Results
checkpoint-status |  |  | checkpoint | Phase rotation correct
button | 5758c88c-499a-5cac-b378-8f8790f65db0 |  | button | Earth Resistance test result in ohms | <0.5m?,>1m?,Fail
label | 70cea066-d150-50ef-97de-2685f956bf06 |  | note | < 0.5m? Clause 8.3.5
checkpoint-status |  |  | checkpoint | Insulation Resistance test result
label | a488d547-c83b-5a83-9e07-ab24feb2d4de |  | note | > 1m? Clause 8.3.6
button | b5ea821f-37e7-5974-a708-a9dc99e84afd |  | button | L1 - L2 | <0.5m?,>1m?,Fail
button | 6a3bddcf-c245-572f-9c45-c8ed80cf481a |  | button | L2 - L3 | <0.5m?,>1m?,Fail
button | a0f1441a-dea8-5429-a205-f2627f7efabe |  | button | L3 - L1 | <0.5m?,>1m?,Fail
button | f77d011a-ea8f-5266-9de1-df3953a2a920 |  | button | N - L1, L2, L3 | <0.5m?,>1m?,Fail
button | 45e4d507-69e1-556f-85a4-8b08843555ef |  | button | E - L1, L2, L3 | <0.5m?,>1m?,Fail
button | 52b248b5-f7cc-5767-86c4-7b30048a991d |  | button | E - N | <0.5m?,>1m?,Fail
checkpoint-status |  |  | checkpoint | Polarity & Circuit connections
label | 085ce3b7-fe62-5b92-8570-a37d08096f2f |  | note | Clause 8.3.7 & 8.3.8
button | f8e58554-e2cf-5a7c-8498-9905c7a7fc6f |  | button | L1 | Yes,No,N/A
button | e391e95c-4193-592e-8f50-50a3623d88cf |  | button | L2 | Yes,No,N/A
button | 015f8f8a-1ae5-541d-b2b9-89cecd3995a4 |  | button | L3 | Yes,No,N/A
button | a4b93c47-45c5-54f8-9d35-41f8d86f8c5f |  | button | N | Yes,No,N/A
button | d044965c-be7d-51c1-9589-01b799d00473 |  | button | E | Yes,No,N/A
checkpoint-group |  |  | section | Verification
checkpoint-status |  |  | checkpoint | Installation completed to specifications
label | 28c3045b-e319-5989-818e-64ab956fa89c |  | note | Any issues comment/photo below
text | cd3f0d24-ff27-585f-b6e4-62de06bcfac9 |  | textbox | Electrician Name
text | 76cf5671-189f-50fc-83c9-0e6d415135a8 |  | textbox | License No.
text | 9f6fbc49-fd7f-576e-aa9a-937f5a40487e |  | textbox | Date Installed
checklist-flat |  |  | checklist | ITP-004C - Sub circuit Testing & Commissioning |  |  |  |  | Yes | ITP-004C - Sub circuit Testing & Commissioning | 92204fd7-f2d9-40e4-9514-63b82363b9f0
checkpoint-status |  |  | checkpoint | Commissioning Results passed & attached below
checklist-sectioned |  |  | checklist | ITP-001 - Conduit Installation (V.100321) |  |  |  |  | Yes | ITP-001 - Conduit Installation (V.100321) | a9d7b662-37b9-4f86-b684-b85802afd671
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | eb9ad091-6bb3-572a-bfd6-0f77d8f7a9bb |  | textbox | Drawing & revision number(s)
label | f23b4da6-3d6a-55d1-aa71-45cf0496536f |  | note | All inspections are to be completed in accordance with the specification and AS/NZS3000:2018
select | d0c35546-a6b7-5ae3-a5f6-f26e68680662 |  | dropdown | Conduit Run type | In Slab Conduit,In Wall Conduit,Underground
text | 93227f44-ee7e-5692-bf9b-ec38ede26853 |  | textbox | Conduit route, size & quantity
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Check existing services, correct location & permit approval
checkpoint-status |  |  | checkpoint | Correct Depth/Cover
checkpoint-status |  |  | checkpoint | Tied and joins glued
checkpoint-status |  |  | checkpoint | Ends sealed
checkpoint-status |  |  | checkpoint | Area clean and safe
checkpoint-status |  |  | checkpoint | Drawings marked up with changes
checkpoint-status |  |  | checkpoint | Ready for wall sheeting, wall closure or column sleeve
checkpoint-group |  |  | section | Installation Verification
checkpoint-status |  |  | checkpoint | Installation completed to specifications
label | 8866f6cf-4929-5a95-968f-7e52478ca792 |  | note | Any issues comment/photo below
text | 6c8a4548-aaba-5fc4-8b7f-bc9a01af601b |  | textbox | Name of Installer
text | ab9f9e94-4620-59dc-a67e-900322808a08 |  | textbox | Date Installed
checklist-flat |  |  | checklist | ITP-004B - Sub circuit Fit Off |  |  |  |  | Yes | ITP-004B - Sub circuit Fit Off | b2ffd02d-238b-4f16-93a4-b993c723d36d
checkpoint-status |  |  | checkpoint | Fit-Off Complete
checklist-flat |  |  | checklist | ITP-009 - Energy Meter Validation Schedule (V.100321) |  |  |  |  | Yes | ITP-009 - Energy Meter Validation Schedule (V.100321) | c5cb3afd-350d-4f60-9fd2-9d15dcac7d19
checkpoint-status |  |  | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
text | 863cfd41-525b-58b9-bff0-605ad431c840 |  | textbox | Drawing & revision number(s) - If applicable
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | b195aab0-86fc-59e0-84c5-1a13a3f0455f |  | textbox | Meter Number
text | f311a926-20c4-5f3f-ab17-f2d320ca9b5c |  | textbox | Energy Meter Reference & Detail
text | d92b8e8e-b641-5439-b92a-eb0d657acd4b |  | textbox | Meter Type
text | c303c523-c05d-5c71-9c15-fa6669691595 |  | textbox | Model Number
text | d7f5e7e5-8c38-56d5-bc7a-6fc0fdce0b79 |  | textbox | Protocol
text | a419d5d6-e328-549b-89b5-5e9918c54a01 |  | textbox | Power Rating
checkpoint-status |  |  | checkpoint | Validation Checks - Pass once entered
label | f175eadd-43c8-5c15-887e-b7168d29ce21 |  | note | Photos/Comments added below as apllicable
select | c311afce-1c6c-5d40-9b0f-43f584f939b8 |  | dropdown | CT Ratio | 50:5,60:5,80:5,100:5,200:5,250:5,300:5,400:5,500:5,600:5,800:5,1000:5,1200:5,1600:5,2000:5,2500:5,3000:5
button | b107f1cb-aa05-5fd8-87aa-776e1d89d618 |  | button | CT Ratio checked & confirmed | Yes,No
button | 9e5e6d41-5a0d-594f-ae5c-cf566d0f764b |  | button | CT's checked and installed correctly | Yes,No
button | dcf3a32e-8899-52cf-a6d0-2e07de437377 |  | button | Wiring checked and confirmed correct | Yes,No
button | 5dc54cbd-728a-5be4-bc92-a0adf66c1b40 |  | button | Energised | Yes,No
button | 5a29a152-1a7b-5120-b66d-912bbc5aea9e |  | button | Meter parameters checked and adjusted | Yes,No
button | d79ff617-e2a3-5646-a12b-c34d3566760c |  | button | Volts checked reading meter to check meter | Yes,No
button | 69421a6e-ce99-5f3c-8f8d-a1ea305bf934 |  | button | Amps reading red phase energy meter | Yes,No
button | a10fcc13-fde4-5a3d-a0d2-3b79bc88cb7c |  | button | Amps reading red phase check meter | Yes,No
text | 7bb104f9-a87b-5ac9-93c7-0f963b3011f3 |  | textbox | Meter Serial Number
checkpoint-status |  |  | checkpoint | Validation completed to specifications
label | 43dd9bca-fdd6-5209-aece-2229191aaf91 |  | note | Any issues comment/photo below
text | 36a0407d-2621-57f5-88ab-922bed7cafd0 |  | textbox | Name of Person Completing checks
text | 735b6b26-9ad8-5bca-bac4-9aacc865521f |  | textbox | License No.
text | 17a64ebf-80ef-5d6d-be25-bae1ca379325 |  | textbox | Date
checklist-sectioned |  |  | checklist | ITP-007 - Lighting Control Installation and Commisioning (V.171121) |  |  |  |  | Yes | ITP-007 - Lighting Control Installation and Commisioning (V.171121) | cb1b5b4e-1c17-4c62-9e09-58e193868a35
checkpoint-group |  |  | section | Identification
checkpoint-status |  |  | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | f409d8ee-fa73-5031-b293-119dc6e0f51d |  | textbox | Drawing & revision number(s)
label | 9329e7b8-0c18-50e7-b6a9-cf28e26e6b47 |  | note | All inspections are to be completed in accordance with the specification and AS/NZS3000:2018
text | a94d8283-5c59-5e45-a52e-6086aca0d205 |  | textbox | DALI No / Relay No
text | 232a88f9-2a37-5e85-ae29-0257d6e187d4 |  | textbox | Circuit Attched
text | d6568e41-59a0-5670-9d64-37b381611f69 |  | textbox | Rough-In feed start location
text | ffb45029-8214-5c64-930a-72ae2c023192 |  | textbox | Loops/Backbone
text | 3cec7bc1-39c4-5889-a670-51d6692e11f7 |  | textbox | Finish Location
select | eca4c18f-d1be-5c46-9604-f84454a06945 |  | dropdown | Control Type | Dali,DMX,DSI,Relay,Other (Specify Below)
text | 2d9a386e-0e2c-5bca-9513-f14d01fc3287 |  | textbox | Other (Specify Here)
select | 4909755b-9da3-57c3-88bf-00d80bf94cab |  | dropdown | Type of Cable Installed | Twin 1.5,Twin 2.5,CAT5e,CAT6a,Dyna Liite,CBUS,Two Pair Shielded,Other (Specify below)
text | accb3078-b5a6-5ece-abf7-b2e9b6f5aeb6 |  | textbox | Other (Specify Here)
select | d23c5e6b-936e-5f42-aef4-1a9385bb7be5 |  | dropdown | No. of ights per Universe | 0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41,42,43,44,45,46,47,48,49,50,51,52,53,54,55,56,57,58,59,60,61,62,63,64,65
checkpoint-group |  |  | section | Pre-Commissioning checks
checkpoint-status |  |  | checkpoint | Commissioning checks - Pass once below are completed
label | 43c06acd-3f37-5d2b-b2e9-4ff4dab78397 |  | note | Attach photos/comments below as applicable
select | b830a3d5-b2a2-50e3-8f38-631922bc00b5 |  | dropdown | CB No. | 0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41,42,43,44,45,46,47,48,49,50,51,52,53,54,55,56,57,58,59,60
select | f91a45e6-894b-53c4-987a-61f929b3c944 |  | dropdown | No. of Light Fittings | 0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41,42,43,44,45,46,47,48,49,50,51,52,53,54,55,56,57,58,59,60
select | 6ed0a042-b9d8-5608-9a9e-c40c6cef8705 |  | dropdown | Controller ID number type | 0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41,42,43,44,45,46,47,48,49,50,51,52,53,54,55,56,57,58,59,60
button | c77085f2-1c97-5cdd-80b5-04a77abd3e9d |  | button | Is scheduling applicable | Yes,No,N/A
button | a6c62f34-34cf-56ed-8796-b60bfde3c43b |  | button | DALI, DSI, DMX addressing completed | Yes,No,N/A
button | 713d6e6c-bf05-5b07-924b-03dd5221c308 |  | button | LCP / Touch Screen programmed | Yes,No,N/A
button | 2eb6bf13-11d8-5668-ba7d-5b7ab0a37305 |  | button | Motion Sensor in place and programmed | Yes,No,N/A
checkpoint-group |  |  | section | Commissioning checks
checkpoint-status |  |  | checkpoint | Switching function as per Functional Description
checkpoint-status |  |  | checkpoint | Dimming function as per Functional Description
checkpoint-status |  |  | checkpoint | Schedule function as per Functional Description
checkpoint-status |  |  | checkpoint | Head end in place and programmed
checkpoint-group |  |  | section | Verification
checkpoint-status |  |  | checkpoint | Installation completed to specifications
label | 1cc81638-3519-5a22-905d-2e17541b2ff4 |  | note | Any issues comment/photo below
text | 6c946ec1-1014-522c-a9fa-9b7e86b8adea |  | textbox | ION Electrician Completing Checks
text | 840b073e-a4d6-5790-a7a2-9b14ccfce0f7 |  | textbox | System Programmer Company and name
text | d5854e8d-0667-5b35-a67a-88257da9b0f8 |  | textbox | Date
checklist-flat |  |  | checklist | ITP-005B - Switchboards Commissioning & Verification |  |  |  |  | Yes | ITP-005B - Switchboards Commissioning & Verification | cd62cddd-6542-4127-b82f-47e9eea442ca
checkpoint-status |  |  | checkpoint | BMS Interfaces connected
checkpoint-status |  |  | checkpoint | Controls cables connected
checkpoint-status |  |  | checkpoint | Insulation Resistance checks completed
checkpoint-status |  |  | checkpoint | Earth Continuity Tests completed
checkpoint-status |  |  | checkpoint | Polarity and connection checks
checkpoint-status |  |  | checkpoint | Ready for Energisation
text | ce3cfdb8-414f-57be-8202-4d39e885ddec |  | textbox | Energisation Date
holdpoint |  |  | signoff | Request Energisation Authorisation
checkpoint-status |  |  | checkpoint | Post Energisation checks completed
checkpoint-status |  |  | checkpoint | Surge Divertors on after energisation
checklist-flat |  |  | checklist | ITP-003A - Sub-Mains Rough In |  |  |  |  | Yes | ITP-003A - Sub-Mains Rough In | d06e22e6-32d3-4103-be4d-7c7eccb1dfe8
checkpoint-status |  |  | checkpoint | Circuit Information uploaded below
checkpoint-status |  |  | checkpoint | Rough-In Complete
checklist-flat |  |  | checklist | ITP-005A - Switchboards Installation |  |  |  |  | Yes | ITP-005A - Switchboards Installation | e2a3d775-0420-44dc-93a2-1be2ceba9e89
checkpoint-status |  |  | checkpoint | Switchboard details entered below
select | ae592b4e-3e5e-5549-af72-351034f54679 |  | dropdown | Type | Main Switchboard,Distribution Board,Controls Panel,Meter Panel,TOB,Other (Specify Below)
text | b2261cf5-23f5-5421-9b7b-356a7c5b7b1f |  | textbox | If other selected above, please specify
text | 76ca1f83-ee9b-5e02-88ce-cba995848c10 |  | textbox | Isolation Device
text | 7d4f8937-9930-52cf-ba44-d6ee9f1a8e07 |  | textbox | Board Location
checkpoint-status |  |  | checkpoint | Switchboard fixed into place
checkpoint-status |  |  | checkpoint | Supply cable terminated & checked
checkpoint-status |  |  | checkpoint | Supply Earth cables terminated & checked
checkpoint-status |  |  | checkpoint | All Labels Installed
checkpoint-status |  |  | checkpoint | Switchboard Vacuumed and cleaned
checkpoint-status |  |  | checkpoint | Circuit schedules in place