## zres_siteapp
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | f5b959a8-9496-4502-9f36-3c5ce66f64bc |  | checklist | Low Voltage Cables - Mains/Submains (Pre-Energisation) |  |  |  | 346 | Yes | Testing & Commissioning - Low Voltage Cables - Mains/Submains (Pre-Energisation) | 1a2bf763-f13f-410e-9133-aa91d91ac29e
checkpoint-group | 018edeaf-369d-4f29-b1bf-c91bde4328eb |  | section | Pre-requisite Works
checkpoint-status | 23f86157-f72b-4ffa-a768-98665b79837f |  | checkpoint | Insulation Damage
checkpoint-status | 57bacc0d-557a-45ca-93e7-ece22f64ffd4 |  | checkpoint | Correct Type of Termination
checkpoint-status | 9684c7b9-19a0-48c9-b01a-cccbab0659ff |  | checkpoint | Correct Cable Size and Labelling
checkpoint-group | 57d6eede-c12c-4a00-be4c-750031f4f70e |  | section | Insulation Resistance
checkpoint-status | 0cf19de5-79a4-4ab0-8d41-dc57fd701299 |  | checkpoint | R-W
button | 9a8a942c-c760-54ab-8156-7f923929fb81 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | ce678e18-59f2-501b-974a-b76616a2e263 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | d4ef7fc9-293d-4bb1-a821-0d89ceace40b |  | checkpoint | R-B
button | 1c60b3a6-1e7b-5679-9483-48e4dd4f3da1 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | dd511f61-20d5-518f-81f4-fc71cc02430e |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 88eebd9e-2491-41ab-8bc2-7495c59d63f0 |  | checkpoint | W-B
button | 00092a90-1d66-57c2-9ac1-af0166a8fdba |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | ccd93f11-247b-50bb-8940-faffeea99973 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 0dbda30a-d146-4689-8032-1a754f027c24 |  | checkpoint | R-N
button | c2567637-4493-5346-b1b1-6608d53e6dbe |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | f42ca530-cdd3-5eec-9abc-41f8a9593ad3 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 30776b3e-d58f-4dc9-bb62-41c38d10f98d |  | checkpoint | W-N
button | 9e43d7f4-0af4-5ba6-96d7-5ca6707f7408 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | d3ac676d-4354-5beb-9005-912a85b0d966 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 2970f94b-cb79-43a9-9ea1-b18274f0ac88 |  | checkpoint | B-N
button | 591d006c-3ed7-56f8-8464-c575b772c723 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | 4cc71dfc-b209-54b8-bc83-e89b7f48d10d |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 3d6923be-a1f5-449f-a6e0-8f4ed98390f2 |  | checkpoint | R-E
button | c2fab04d-bf8f-581c-b555-5ed80cce206e |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | 55cce7c7-7810-582e-8a6b-369795d3b0c6 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | c9c38127-6fdd-48a2-9520-4253554c02e0 |  | checkpoint | W-E
button | 06e4a05b-ae5f-5741-8393-5b16751588c6 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | 2282f52b-da13-536e-ac5b-4cba786a817b |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 256e178d-ee3e-4d6a-b835-ea77f714c7d4 |  | checkpoint | B-E
button | 4e9f2bd5-abdc-5f0e-87ca-b8c4ecf750c6 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | 75306665-e77b-5cf6-8ce6-a29309f9b014 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 90b33d64-3d90-45ba-8441-9a370fc4ba0d |  | checkpoint | N-E
button | 7d47d5a8-e5e5-54b1-bf15-f8deabff2b62 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | 71eef9c5-5789-5d90-89ea-0b68c00ea9b5 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-group | 52006caf-6350-4285-8d32-6a0561fdbfed |  | section | Continuity Testing
checkpoint-status | 904dd9ec-4232-4529-a23d-9924bf54ff18 |  | checkpoint | Red Phase
text | cf4db43d-bd8a-5d5d-8efe-a99fe73bd4d0 |  | textbox | Resistance (Ω)
text | bbc273bf-6757-59b2-b065-7b79be06a427 |  | textbox | Target Resistance (Ω)
checkpoint-status | 8a010c34-ad3f-44f6-b612-187c1b52df72 |  | checkpoint | White Phase
text | c53816fc-336b-5f0c-82dc-5a69b57952ab |  | textbox | Resistance (Ω)
text | 96675194-8fbd-56aa-93d5-0408c0aa5faf |  | textbox | Target Resistance (Ω)
checkpoint-status | b3d56b96-05a0-4893-95d7-00bf5811b4fe |  | checkpoint | Blue Phase
text | c1062c2d-c386-55f0-99cd-12016163d1ee |  | textbox | Resistance (Ω)
text | 88f65101-39fd-5748-b7cf-2b25ec17919b |  | textbox | Target Resistance (Ω)
checkpoint-status | b5e9a7d4-309f-452f-b5fb-5b1bdeb93dae |  | checkpoint | Neutral
text | 736f3782-a7c4-588c-acd2-268a4a03e69f |  | textbox | Resistance (Ω)
text | 615464c5-2962-5723-9c3e-de0d1a961057 |  | textbox | Target Resistance (Ω)
checkpoint-status | fbe6cce2-e362-42d8-ac3c-ed5f1e81b0a9 |  | checkpoint | Earth
text | 2ee539aa-933f-56c0-9220-1db1e740fc7b |  | textbox | Resistance (Ω)
text | 17f9b7f0-2c20-5abe-a210-21c0556a83fd |  | textbox | Target Resistance (Ω)
holdpoint | 0963f175-9fe2-4d9e-a431-045b23711916 |  | signoff | Checked By (Heyday):
checklist-sectioned | 50866f89-092f-4410-b11b-5e2c0f371df3 |  | checklist | Main Switchboards (Pre-Energisation) |  |  |  | 23 | Yes | Testing & Commissioning - Main Switchboards (Pre-Energisation) | 7956b573-b3e7-4ec1-a2fa-e5f674399d8f
checkpoint-group | 8fae24b8-93ff-44e4-9f3e-3d4d4fd11b95 |  | section | Physical Checks
checkpoint-status | e709c7be-8e7d-4169-9abe-3cb7607e04ab |  | checkpoint | 1. Confirm boards dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint-status | f12a6ef1-c025-4c3f-8e3c-aabbcbac8a65 |  | checkpoint | 2. Confirm correct MSB Form of Separation, Provide actual Form of Separation in Comments section
checkpoint-status | 4bacf871-43d7-44b1-9ca7-931eb3d5c73e |  | checkpoint | 3. Confirm the Layout of fitted components (ACBs, MCCBs, MEN, ATS) is in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint-status | 5acd8e26-1e16-488f-bf1f-2688b05a237b |  | checkpoint | 4. Confirm that Brand of fitted components is in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint-status | c3e92977-4409-4e3c-b8a0-114bf210be9f |  | checkpoint | 5. Confirm meters location, types and labels are in accordance with approved shop drawings
checkpoint-status | 134840f7-5341-470d-a375-90551e836a99 |  | checkpoint | 6. Confirm the circuit breakers rating is in accordance with discrimination study (provide discrimination study reference in the Comments section)
checkpoint-status | 0763de31-405b-4e72-857d-2ced3f82e9c9 |  | checkpoint | 7. Confirm Trip units and protection relay settings are set in accordance with discrimination study
checkpoint-status | 109d65e8-a0df-42f4-8a18-a6457d59aadf |  | checkpoint | 8. Confirm correct circuit identification and labelling
checkpoint-status | f10e2dcb-9875-47f0-b4d8-958e1fd394ee |  | checkpoint | 9. Confirm easy access to controls termination
checkpoint-status | 9a611db2-39d4-4660-b50b-1fcb1452706a |  | checkpoint | 10. Confirm correct location, access and sufficient support for incoming cables
checkpoint-status | 8083287d-4ea4-4e47-8888-070a7be1c4f8 |  | checkpoint | 11. Confirm correct location, access and sufficient support for outgoing cables
checkpoint-status | dd201025-c906-4ded-af65-32c021351bff |  | checkpoint | 12. Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in a Comment section
checkpoint-status | a596d58c-b005-485b-9c07-51013801b5a8 |  | checkpoint | 13. Confirm correct phase identification of busbars and cables inside the board
checkpoint-status | bc2f44c9-0e12-4027-9ac0-857eef3646d5 |  | checkpoint | 14. Confirm correct size of incoming power cables as per approved cable schedule
checkpoint-status | 5db9f0ed-1af7-439a-be14-ef8d2771c4d1 |  | checkpoint | 15. Confirm correct size of earthing conductors
checkpoint-status | 3039bea8-eb57-44dd-beda-50bce13c367b |  | checkpoint | 16. Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
checkpoint-group | 1e94d923-98c2-4cf3-83f4-8e81fb3f9ed2 |  | section | Mechanical Checks
checkpoint-status | ed460c2b-4e25-45f6-a336-77a8cc25c8ae |  | checkpoint | 1. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
checkpoint-status | 0e70d6de-0d05-46e6-a482-c5df4089c862 |  | checkpoint | 2. Repeat racking of air circuit breaker in and out of chassis for 2 times to verify correct functionality of sliding mechanism
checkpoint-status | 33e985fc-0800-4089-ac92-b78eaf79d6fb |  | checkpoint | 3. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
checkpoint-status | 7606501e-6b84-4d59-bf66-647360d4245e |  | checkpoint | 4. Repeat manual closing and opening of moulded case circuit breakers for 3 times
checkpoint-status | 8365c25d-b9eb-4b26-a107-e3ec28f0ca3f |  | checkpoint | 5. Repeat manual closing and opening of miniature circuit breakers for 3 times
checkpoint-status | cfa73a8c-32bd-498f-92f4-6645a8c83db8 |  | checkpoint | 6. Repeat mounting and dismounting of control fuses 1 time
checkpoint-status | 1bbac3cf-816d-429e-8593-6f95117b09fa |  | checkpoint | 7. Repeat mounting and dismounting of control fuses 1 time
checkpoint-status | 4df04b50-8603-4e17-a06d-09346cb9d6c6 |  | checkpoint | 8. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 1 Breaker and confirm that Source 2 Breaker is mechanically interlocked
checkpoint-status | ba24e470-4526-445c-8da5-7f158e4f0fa9 |  | checkpoint | 9. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 2 Breaker and confirm that Source 1 Breaker is mechanically interlocked
checkpoint-status | a9a85573-39a3-48ad-acb5-79c2bccd745e |  | checkpoint | 10. Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards
checkpoint-group | 722dc086-3965-41eb-8544-d40f6e036103 |  | section | Switch Gear Busbar - Preliminary Checks
checkpoint-status | 7f37c3cd-7b41-49b4-8dd7-d0952e802c69 |  | checkpoint | 1. Confirm all fuses Removed in board’s Control Sections
checkpoint-status | 420447a3-a867-4e5e-b379-dad0ffae8c6d |  | checkpoint | 2. Confirm Main Incomers ACBs/MCCBs are Closed
checkpoint-status | 0cad5f1a-3ffc-4c5c-b91f-9a473d0f7771 |  | checkpoint | 3. Confirm Bus-coupler is Closed (if exist)
checkpoint-status | 216adc9a-95a4-48a8-822a-97fe489b05c1 |  | checkpoint | 4. Confirm Outgoing Feeders is Closed
checkpoint-status | 31e36a40-14f8-4cbe-9a16-a63c06e2e646 |  | checkpoint | 5. Confirm Main Panel Neutral to Earth Link(s) was Removed
checkpoint-status | 3521c02c-fa2e-4164-9e0a-e2a75858c4bd |  | checkpoint | 6. Confirm Neutral link on Transient Voltage Surge Suppressor is Opened
checkpoint-status | f4d3a76f-555b-4d08-b1d6-4d5b74b52e15 |  | checkpoint | 7. Confirm All Long Time rating Plugs From ACB's are Removed (if applicable)
checkpoint-group | b93d32c8-fa8d-49b1-9124-61c88bd8b5a1 |  | section | Switch Gear Busbar - Insulation Resistance (1000V)
checkpoint-status | fce186ff-8fe9-420b-baa6-25a24b2687eb |  | checkpoint | 1. Between L1 Phase and Neutral
button | 5d0fa9d4-3057-5f7b-95f7-ee58f147495d |  | button | >10MΩ | YES,NO
text | 80a0e736-fd6c-580a-9dfe-e4566efffaa5 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | f51eb97c-857c-41ad-8a95-47625b23dfba |  | checkpoint | 2. Between L2 Phase and Neutral
button | 67010062-53c3-58b0-aaf0-1fce18f8b9f5 |  | button | >10MΩ | YES,NO
text | ce4e99d7-d9b1-56ef-8de3-f1adc0c6dea7 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 90fd0fcf-c627-4718-8cc7-77d1c29a1fed |  | checkpoint | 3. Between L3 Phase and Neutral
button | 4411ae80-a470-52a3-8e98-2e78a4fd4846 |  | button | >10MΩ | YES,NO
text | bd565b3f-87dd-59b9-8dbb-46149c449d56 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 13d3855a-a1b4-46e7-8ccc-b27564e8a236 |  | checkpoint | 4. Between Neutral and Earth
button | 91779843-aadc-5e9e-8df5-c8484ba1da16 |  | button | >10MΩ | YES,NO
text | 0d181df8-1b98-5f4c-ba7b-187a701c47b8 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | f95ee146-bbb8-4e2f-a4df-c8e5d3f26450 |  | checkpoint | 5. Between L1 Phase and Earth
button | 4c632dfa-483b-5787-adb5-28360c6c913f |  | button | >10MΩ | YES,NO
text | 39b1bc1e-1c12-50dd-8316-88afe5fca0cf |  | textbox | Actual Reading if <10MΩ
checkpoint-status | d30595f0-a3f8-4402-b31c-336b98e222bb |  | checkpoint | 6. Between L2 Phase and Earth
button | 46836438-d796-5460-aa13-7cae26b1fd97 |  | button | >10MΩ | YES,NO
text | 9e6f285d-66fd-56cf-b709-4c5083cc1e73 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | fe251e3b-f2e0-47da-a196-2c7bede637f4 |  | checkpoint | 7. Between L3 Phase and Earth
button | 6120150e-b479-5ebb-b823-3d0597e4012d |  | button | >10MΩ | YES,NO
text | 371fa103-6b1b-5a1d-a8ff-22b0a9a90fe0 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 6b83d718-c6ab-4eae-9a93-cbf60e348f7f |  | checkpoint | 8. Between L1 Phase and L2 Phase
button | 6c31f4b8-d3b5-5a40-aec8-1cace3e40112 |  | button | >10MΩ | YES,NO
text | e6e64b91-a4fa-503d-a906-c38b723cab43 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 322c5bc1-a6a4-468a-90e9-2fbb787585a4 |  | checkpoint | 9. Between L1 Phase and L3 Phase
button | acae8a88-5a0b-5a84-932f-bd9473732356 |  | button | >10MΩ | YES,NO
text | c3ac8128-d9c4-5287-a16f-68a7a4233fc7 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 5467d427-0bfe-4a76-93c0-dafb6762aab2 |  | checkpoint | 10. Between L2 Phase and L3 Phase
button | c32f53a4-5b47-5025-8e58-dd468a5b1ae8 |  | button | >10MΩ | YES,NO
text | c60a138e-3cbd-5d99-a5d7-e1830a41f33d |  | textbox | Actual Reading if <10MΩ
checkpoint-group | 1101a10d-756f-4e13-8fda-4961a22ab017 |  | section | Current Transformer Checks
checkpoint-status | 6e28df17-fe33-4990-b850-65e3962369b9 |  | checkpoint | Current Transformer Checks
text | 2ca59f02-67a2-5beb-b332-0c51245ac3ca |  | textbox | CT ID | YES,NO
button | a0a82070-b7f4-5def-a4e8-ed1406108b82 |  | button | CT Polarity is Correct | YES,NO
button | a6f07223-c23c-528e-8fc1-033de1f54bd3 |  | button | No crossed phase CT connections | YES,NO
button | ef0bddc3-f045-565f-8180-9f59cbbe3652 |  | button | No phase sequence CT connection errors | YES,NO
holdpoint | 63bf9fa9-ae18-4cdd-93aa-59a4170eb7de |  | signoff | Checked By (Heyday):
checklist-sectioned | ab447333-a299-4292-8db0-7bf6f22c0c5a |  | checklist | Distribution Boards (Pre-Energisation) |  |  |  | 206 | Yes | Testing & Commissioning - Distribution Boards (Pre-Energisation) | 5f890f2e-4399-4f47-92e8-4c162df50d86
checkpoint-group | 8977fb2d-d688-4cf3-ba87-cb3b8fa58f11 |  | section | Physical Checks
checkpoint-status | 53931865-a78a-45ab-97ba-c708723ce19b |  | checkpoint | Confirm board's dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint-status | 406cc207-1337-4249-b626-ad3c99a32f08 |  | checkpoint | Confirm correct circuit identification and labelling
checkpoint-status | 9fe77cb5-17a2-4cbd-986f-6b77e11a3212 |  | checkpoint | Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in the Comment section
checkpoint-status | 803faee4-c37d-40fe-9c85-2e74fc369c5b |  | checkpoint | Confirm correct phase identification of busbars and cables inside the board
checkpoint-status | 47ec17c8-ae92-4b4d-866c-ff0d9ea6aee2 |  | checkpoint | Confirm correct size of earthing conductors
checkpoint-status | 63b54de8-ad3b-41d3-a0f3-fc5241186aa9 |  | checkpoint | Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
checkpoint-group | 64c1c2c8-43ed-4fd4-bb5b-5d012ed1db54 |  | section | Mechanical Checks
checkpoint-status | cf8b9aa7-08fd-4c0e-91c8-cbb9f004a809 |  | checkpoint | Repeat manual closing and opening of moulded case circuit breakers for 3 times
checkpoint-status | 49cfc303-218e-487c-81da-99c451f007b0 |  | checkpoint | Repeat manual closing and opening of miniature circuit breakers for 3 times
checkpoint-status | bcb84516-3183-41b4-96f5-4fce85c25419 |  | checkpoint | Repeat mounting and dismounting of power fuses for 1 time
checkpoint-status | aa08c339-65f9-48dd-bb4c-bcb7bb3ecc17 |  | checkpoint | Repeat mounting and dismounting of control fuses 1 time
checkpoint-status | bc551d4c-f188-4b41-92fa-cc1e5bb9ac39 |  | checkpoint | Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards.
checkpoint-status | 48adfc55-5257-4635-a37d-8aaa1cdb361a |  | checkpoint | Conduct pull test for all cables connected to MCBs and Termination blocks
checkpoint-group | 21404c63-9e24-472c-9e6b-fcff18e7f796 |  | section | Preliminary Checks
checkpoint-status | 28c77213-b2ae-49b2-8713-4e8526be9db4 |  | checkpoint | 1. Confirm all fuses Removed in board’s Control Sections
checkpoint-status | 8dfbd3cf-e1f3-4186-92f7-84d6786be3cd |  | checkpoint | 2. Confirm Main Breaker Closed
checkpoint-status | 19f52456-4a04-4556-af92-67733c2ddd7c |  | checkpoint | 3. Confirm Outgoing Breakers Closed
checkpoint-group | bdf6c1bc-a00d-4ab5-9aff-1bbba6598c13 |  | section | Insulation Resistance (500V)
checkpoint-status | 95780f93-e76b-4d2f-9976-285f8da63ae6 |  | checkpoint | 1. Between L1 Phase and Neutral
button | d13d1e56-7dcb-5e3a-9b5c-a0177a9b705e |  | button | >10MΩ | YES,NO
text | acb50fa4-ec67-553a-ac17-a3c84289aef3 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 97429c4d-a75b-43ac-b3d6-8e93dea59342 |  | checkpoint | 2. Between L2 Phase and Neutral
button | b536bc25-10c9-5f2b-b54e-2d017764b346 |  | button | >10MΩ | YES,NO
text | fbc00ebb-87e0-5b6b-b6ea-a7b87cda5dde |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 56504dc8-adab-47d4-b32b-f0ef6bf26930 |  | checkpoint | 3. Between L3 Phase and Neutral
button | bf84e43c-e7a0-5de6-8d9d-eaaa028eb099 |  | button | >10MΩ | YES,NO
text | 21adcd4d-6cbf-5f5e-b8a8-b96d7ba516f5 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 59e61667-dcdb-4fdf-a339-2e207b35bcbb |  | checkpoint | 4. Between Neutral and Earth
button | a7c183bc-5dac-5983-b295-3010e75cbb96 |  | button | >10MΩ | YES,NO
text | a7e77f7f-29c5-518c-9001-05d65d66e0fa |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 555ad5dc-50ed-4de6-bb8e-e1c1569a6e90 |  | checkpoint | 5. Between L1 Phase and Earth
button | baf66c08-1e2a-5e9b-92bf-4c4497f8506c |  | button | >10MΩ | YES,NO
text | a613c700-5f1c-5268-b5ff-dd5877585430 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 758028f6-f6fa-43eb-906b-ad9ba25d281f |  | checkpoint | 6. Between L2 Phase and Earth
button | 1429255c-7841-56ad-8697-2c6d159d4785 |  | button | >10MΩ | YES,NO
text | 3cb29882-53f7-571c-a986-60f07c038d4a |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 7d0031ee-ffd7-418b-8ad9-32353aca2e22 |  | checkpoint | 7. Between L3 Phase and Earth
button | 6b34d913-698f-543f-acbd-b15ce2393323 |  | button | >10MΩ | YES,NO
text | eca5e2f2-4f96-54a4-bd9c-d773ef32d661 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 95d05598-ce63-4609-bc1e-50944d2c5aac |  | checkpoint | 8. Between L1 Phase and L2 Phase
button | f2d0ded0-11dc-5ed7-b174-7ae1e1f2de7f |  | button | >10MΩ | YES,NO
text | 409049d8-bf8e-5277-b9d3-092b1ed58bf4 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | f5ff6e4a-a62f-4e95-aea1-04b18472b68c |  | checkpoint | 9. Between L1 Phase and L3 Phase
button | 062ccca4-0713-55fd-a25e-95a99c06db87 |  | button | >10MΩ | YES,NO
text | 94d30298-de90-5b38-bbbd-e6d83151d789 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | bb98cdd5-869c-44eb-8f53-98f3bc74dcc8 |  | checkpoint | 10. Between L2 Phase and L3 Phase
button | bb2650ae-08aa-536f-bfd8-7ae3895db90c |  | button | >10MΩ | YES,NO
text | eabaa815-6458-54b1-aa8c-0d477e6c4d97 |  | textbox | Actual Reading if <10MΩ
checkpoint-group | 7ce3d526-d0f2-46a6-919a-831e9e8f6dd5 |  | section | Earth Continuity Test
checkpoint-status | f3e1e57e-5bd1-4798-b4c6-f29e27628b90 |  | checkpoint | Earth Continuity
text | 2a6ea1f6-c5ff-500e-9214-32679eb3c7c6 |  | textbox | Resistance (Ω) - [Target: <0.5Ω]
checklist-sectioned | 13cf0cf9-c3da-4e9c-bb52-18cc0215eece |  | checklist | Low Voltage Busduct (Pre-Energisation) |  |  |  | 918 | Yes | Testing & Commissioning - Low Voltage Busduct (Pre-Energisation) | 98e85fe8-1df5-489b-93b0-be465eb31fa7
checkpoint-group | 2683ac7d-d83d-434f-86db-4bc68ec544c8 |  | section | Pre-requisite Works
checkpoint-status | 6f6e2026-e685-47f6-96eb-26aab5f17835 |  | checkpoint | Insulation Damage
checkpoint-status | fbb93c2b-c852-4a57-b3e1-c9ab11a568fc |  | checkpoint | Correct Type of Termination
checkpoint-status | cfc0e5d9-f976-494b-9421-9032e5ad627c |  | checkpoint | Correct Colour Code
checkpoint-status | 4478576e-9436-47da-943e-dbc0c0770867 |  | checkpoint | Correct Size and Labelling
checkpoint-status | 0af3d548-923b-45c1-9792-4072fb23bf3a |  | checkpoint | Correct Routing
checkpoint-group | 52688ba0-c53b-4ecf-9ceb-ed2c6bea4ef1 |  | section | Continuity Testing
checkpoint-status | 2bbbeb81-d76f-4ab7-9b37-4af81c15d03e |  | checkpoint | Red Phase
text | bccf9913-d1d2-56f3-a607-88c92ed9ccab |  | textbox | Resistance (Ω)
text | f6644a85-f277-584c-b823-e4aabc9fe3fa |  | textbox | Target Resistance (Ω)
checkpoint-status | fb88138b-a601-468d-a400-b241f2a7d8f1 |  | checkpoint | White Phase
text | 0b7948c2-7d82-5100-8f1b-4cea01b30f18 |  | textbox | Resistance (Ω)
text | 66424b14-26aa-5233-a73e-8fa6cc8050f6 |  | textbox | Target Resistance (Ω)
checkpoint-status | 9c311428-b330-40eb-b40c-1dd67b1725aa |  | checkpoint | Blue Phase
text | 52743c86-7a1e-5846-9ed4-16d922e5a47a |  | textbox | Resistance (Ω)
text | 5f38758d-f8b6-51ab-a26e-c74dd36d841b |  | textbox | Target Resistance (Ω)
checkpoint-status | b34c5bdc-1be4-4637-b9d2-444cd99281de |  | checkpoint | Neutral
text | f370275e-68f7-5955-8861-2dcb1588eb3e |  | textbox | Resistance (Ω)
text | 585a13f3-7590-5d8a-bbc8-95d5275da47a |  | textbox | Target Resistance (Ω)
checkpoint-status | 30c50d31-0f05-4055-a918-1ca7a5211171 |  | checkpoint | Earth
text | 3b368092-9571-5aa2-a2a7-e0730ef000fd |  | textbox | Resistance (Ω)
text | b7961f1e-bd19-544e-968b-da79a8efb990 |  | textbox | Target Resistance (Ω)
checkpoint-group | fb07be62-3a2f-4f9c-b77d-500cab4e5db9 |  | section | Insulation Resistance
checkpoint-status | 4b1c9924-2f9e-4a2f-9e95-666cf0fe70da |  | checkpoint | R-W
button | 71e52e0f-a926-568d-a8cd-a92f6c639b94 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 236615dc-9f7f-5d83-b480-8f4a2ee5b083 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 40e123b4-db69-43d8-9785-4b395c22ffc5 |  | checkpoint | R-B
button | 970d468e-6b01-5be9-b3b6-05d5078c0aab |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 33641d8f-e337-533a-a805-87211cbf3a91 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 8d09ae7e-c911-4b43-af36-414ea08fcce7 |  | checkpoint | W-B
button | b3b8d3a8-65a5-5c5d-aeec-ccbf4ea127a9 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | ee127d77-1bf2-5c44-b48e-7269a34edaeb |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 160b2c93-6069-4671-95ba-e72256df6f8b |  | checkpoint | R-N
button | bd4e072d-3fcf-52ff-82b9-294e57745273 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 7ec26620-539d-538d-ba0d-db4f4d700f79 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 2218ed7b-c321-493c-b1f1-41861b0b0a42 |  | checkpoint | W-N
button | f2522ff5-f858-50ac-afa5-d36327eba8b7 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | a8e1d7e2-1f9d-5fae-a962-5a9ff4b7e50e |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | a13a077c-4e34-4816-acfd-d56ca034e416 |  | checkpoint | B-N
button | e6c30564-7894-53de-84e1-27f305aa7aee |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 53ed9870-e3ff-5a45-9d16-70ec0141be7e |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 55c6628d-118f-484b-8659-a501d45e9040 |  | checkpoint | R-E
button | b0dfed67-2b0a-5d94-afbf-b0695936573b |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 1dd8bfc4-1c23-5ce6-8bd8-e776a7524c53 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | b868133f-b4b3-4beb-a629-a4b3ae5e6ccf |  | checkpoint | W-E
button | 8f12b33d-2867-5720-809f-451dd09a8a35 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 11d0aeb0-8c74-5805-8a27-3c9ffc096d80 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 2f1e5474-67ca-4290-a4c0-d0c00ab0fa5f |  | checkpoint | B-E
button | 91374eda-c96c-52e7-8d39-0ea32572ab8c |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 14a493d0-eeb2-5290-9728-f1b86a8b0eba |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | c9a0cae2-b286-4106-845c-1cc0f3a2c670 |  | checkpoint | N-E
button | 5c0881ea-f11e-5a26-9ea2-899b372ad1a0 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 9ec664f6-3127-5687-85f9-817771475f51 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
holdpoint | 475fb419-ba6d-4392-acf5-3dc809c6e54a |  | signoff | Checked By (Heyday):
checklist-sectioned | 8007dcfc-3ab6-4e51-b178-76b596a74764 |  | checklist | Subcircuits (Pre-Energisation) |  |  |  | 2759 | Yes | Testing & Commissioning - Subcircuits (Pre-Energisation) | 7ca2d793-5a69-4e34-a1c4-305de1972fd2
checkpoint-group | 22ad59a6-cf64-407d-8f90-5890e12e2bfe |  | section | Pre-requisite Works
checkpoint-status | b034e671-5464-480c-b898-4c0b89db9eb5 |  | checkpoint | Insulation Damage
checkpoint-status | 13a23277-0fe8-4374-aaef-aa7b3bdea9b0 |  | checkpoint | Correct Type of Termination
checkpoint-status | 7d2acd0a-24f3-41f1-8549-e0698682b9c2 |  | checkpoint | Correct Colour Code
checkpoint-status | 4919545e-b812-4b77-8115-4ff5721c7d27 |  | checkpoint | Correct Outlet Rating and Size
checkpoint-status | 8e34e536-54ec-4939-8934-3f3d3f7f4d4a |  | checkpoint | Earth Continuity
text | e48a685a-85d6-54ef-b8a5-009f1248d667 |  | textbox | Resistance (Ω)
text | c60c77ee-1713-51d3-a35f-5f17b87af27b |  | textbox | Target Resistance (Ω)
checkpoint-status | 25bc796b-0c2c-4d75-b91c-136cda9c846e |  | checkpoint | Polarity Check
button | 6cc45da1-047c-5b14-889c-43bb3bc119b7 |  | button | No Transposition | YES,NO
button | 26306414-0fa5-5acb-b63b-66c528b70448 |  | button | Switch in Active | YES,NO
checkpoint-group | d305aeea-8fea-4098-a7dc-afe9deff4cac |  | section | Insulation Resistance
checkpoint-status | 5ee7f7ee-54b7-45c5-b7e2-fe4ee37eba30 |  | checkpoint | R-W
button | 9a5cb2d1-5579-5a1d-9b00-9e4805b0f7da |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 83ef69cd-1925-58cc-9adc-7a97c9360e5b |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 3dea09e1-3881-45ef-a781-85a5a88bdc6a |  | checkpoint | R-B
button | 2f711467-3548-5a70-a738-dbe6cf167542 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | a9de846a-1cbb-541d-bedc-8a41e4f24ce2 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 2eb786e6-ef15-4e2b-97b7-eecdb2e097a7 |  | checkpoint | W-B
button | d41ed56f-5193-5bba-93eb-44438fc6873d |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 12bdb9a2-bf23-546e-a4ec-6cf6665c5f2e |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 4ea2dc4b-195a-4c12-9876-230d5ac2040c |  | checkpoint | R-N
button | f05704aa-afd2-5e64-9910-56add5f5e59d |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 707778f0-646b-5a67-906a-34920889dd38 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | ec507b52-7f69-4bbc-b10d-2c56e359c3bb |  | checkpoint | W-N
button | 9c6102a6-6af6-582f-b34c-d0eb93785a4f |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | b720d213-3f51-53b6-a5a5-14d9b877255c |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 3ff57f6f-7d61-4328-ae9a-889cc6d2ee6c |  | checkpoint | B-N
button | a2c3311f-319b-5340-a658-d46d17c2bd77 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 4877c8c8-eef6-5ecd-8bfb-b83bbd4b904a |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | cac2b1f3-b411-4ec9-8814-87c194603224 |  | checkpoint | R-E
button | ccbea4e6-80ce-5526-a285-93b56c1384df |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 96871594-a87a-5d28-8a5b-cfc2b9dc9d0b |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 3ffd3ec4-dbde-4082-b569-5d08acbec281 |  | checkpoint | W-E
button | 8965c822-04f9-55cf-951f-5ba61123f22c |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 0d686dc2-1a52-5be8-b36d-6909a37f2c4f |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | e9083a50-4c3b-4382-9700-a8de9e654525 |  | checkpoint | B-E
button | 820de140-0575-5936-9d37-3b64d320489a |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 213182a6-0653-5767-9dc0-31a947da6ceb |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | e64ac7ba-1607-4ff5-8cb6-d0567d4db251 |  | checkpoint | N-E
button | 5be7cda6-dacf-5b45-9a4c-09f61f5c2f3b |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 4e5f42a4-56dd-5ff3-ac48-cc3a42e72347 |  | textbox | Actual Reading if <200MΩ/<500MΩ
holdpoint | 101aba1c-8202-4327-9a19-cdc1f43535a6 |  | signoff | Checked By (Heyday):
checklist-sectioned | fdead114-deb8-44bc-b55d-be88024af9f4 |  | checklist | Subcircuits (Energised) |  |  |  | 2759 | Yes | Testing & Commissioning - Subcircuits (Energised) | 41ec70c3-50a9-49d7-add7-39fb11f7c280
checkpoint-group | c3037dc6-5437-4d3a-b0e8-e43b354e9e31 |  | section | Voltage
checkpoint-status | fb6e4570-b4cb-43ab-9082-051d819f2387 |  | checkpoint | Red - White
text | cc1852b5-a858-5622-a499-3f6f7a5ecf0c |  | textbox | Voltage (V)
checkpoint-status | 9b24a948-75c0-422d-ac9d-8b597617acad |  | checkpoint | Red - Blue
text | 907067cd-77b3-58fa-b9df-fa4d5dc2626a |  | textbox | Voltage (V)
checkpoint-status | 716ace7e-cce9-4389-8bf2-0852ecf28ed9 |  | checkpoint | White - Blue
text | 0c0a9199-cf09-571e-a421-0e9413ed7efb |  | textbox | Voltage (V)
checkpoint-status | 00955b7e-5a72-498e-b9b9-44d726b1737b |  | checkpoint | Red - Neutral
text | 7cb95a8c-b08d-53bb-9f92-c42b900dd157 |  | textbox | Voltage (V)
checkpoint-status | 7d03839b-63b6-432a-80a9-184c0e4f8de6 |  | checkpoint | White - Neutral
text | 1d76cae3-8545-5350-8895-f5dfbba90860 |  | textbox | Voltage (V)
checkpoint-status | 046f1ac1-9e92-4f8f-9792-f9b78602f279 |  | checkpoint | Blue - Neutral
text | 04f6bb60-9d27-5a2b-abf6-5c0fc9f7bca1 |  | textbox | Voltage (V)
checkpoint-status | 85ee5f16-6867-4227-8168-4abf62726adb |  | checkpoint | Red - Earth
text | 558df863-72c1-5a49-a741-d97bb562cae1 |  | textbox | Voltage (V)
checkpoint-status | 92d818e7-0134-4120-8c38-5989b5693ba4 |  | checkpoint | White - Earth
text | 6f194aae-c3d4-543a-8770-022b84d0a96e |  | textbox | Voltage (V)
checkpoint-status | 11027c91-4c93-48f9-8748-342c95cb2978 |  | checkpoint | Blue - Earth
text | 49ce1391-484c-5415-9c72-afa45c4c7b32 |  | textbox | Voltage (V)
checkpoint-group | 1395c343-7cad-4eac-b2ef-0e94635c4b64 |  | section | Earth Fault Loop Impedance Test - (N/A if the circuit is RCD Protected)
checkpoint-status | 3b5353b1-0122-40f9-bdef-a7d49ee87f9a |  | checkpoint | Impedance
text | 6fe7d82f-84cb-53e9-af32-5b53073c1c82 |  | textbox | Record Inpedance (Ω)
text | 0280d8cc-33c9-558c-8058-c3e02dc3acd8 |  | textbox | Target Impedance (Ω)
checkpoint-status | 62ce819a-2a7d-4c5a-b870-7e3b02d2a275 |  | checkpoint | RCD/RCBO Tripping Test
text | 508af3fc-b279-5a1b-8447-ce5b88e6c620 |  | textbox | Trip Current (mA)
text | 298fdfb3-9ea0-51aa-b3da-88668aff353b |  | textbox | Trip Time (ms)
holdpoint | 94e2fe6c-163e-4db7-ab76-95e5fccaa1fa |  | signoff | Checked By (Heyday):
checklist-sectioned | 3ca3689f-77c0-48c2-ab24-e1d735cf09e7 |  | checklist | 3 Phase Subcircuit |  |  |  | 12 | Yes | Testing & Commissioning - 3 Phase Subcircuit | 19071929-685f-49b6-b72e-0610d6396ab2
checkpoint-group | 861fd99c-dca8-43d2-8e4b-f8409081293a |  | section | Pre-requisite Works
checkpoint-status | 6da69891-19bb-46f6-a2d4-9b9cf3d8e4bc |  | checkpoint | Insulation Damage
checkpoint-status | 7225f360-ac04-4778-95db-9dbcc07e76ac |  | checkpoint | Correct Type of Termination
checkpoint-status | 3971722c-baa9-43a9-aa06-c86c6056edfb |  | checkpoint | Correct Colour Code
checkpoint-status | 9708cbf1-ec02-4027-9710-1f71e383629d |  | checkpoint | Correct Outlet Rating and Size
checkpoint-status | e327169b-3ebd-4006-adbb-d344cb7384ca |  | checkpoint | Earth Continuity
text | d1fad654-d6b7-5aaa-ad18-5ced852d1212 |  | textbox | Resistance (Ω)
text | cff9a586-87b0-558c-b1af-f9b5e784901c |  | textbox | Target Resistance (Ω)
checkpoint-status | 21706f16-3e14-4132-869a-39878965623e |  | checkpoint | Polarity Check
button | a878f000-c1ad-5c8c-917d-0e62e1a0e5c2 |  | button | No Transposition | YES,NO
button | b8ec0463-70f4-5599-97fb-21e80b4abc49 |  | button | Switch in Active | YES,NO
checkpoint-group | 9cac9730-f4a3-4380-b5fb-b44eee12d42e |  | section | Insulation Resistance
checkpoint-status | 96dd6692-f9e5-4dbd-8b51-64a37deb1e6e |  | checkpoint | R-W
button | 2b39491a-1d6a-511a-82f4-71cfabd13a8c |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | d348ccc8-6968-5dae-a021-9c9ceffa5e6f |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | f206d7ac-521d-4be4-8f41-eea8e2e1e3bf |  | checkpoint | R-B
button | 52a2c584-84aa-5609-880b-8300f96e8f5e |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | f9cb7812-44c5-52af-a9b2-3ffb8d4e72a6 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 882b4c0f-8dcb-4d8c-8881-b4c7b13c157a |  | checkpoint | W-B
button | c6af3168-67a5-5e0e-935f-deba5b39563d |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 92fa960a-d385-55d2-a305-6489a079a3f0 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 8ed72945-9322-49ab-879b-2450c3ad8f68 |  | checkpoint | R-N
button | f3510836-c94f-5348-bc00-0fe3bd323739 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 8f7cadda-8d23-53d8-af25-7ee29ed9e6e2 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 3ce7661c-5fca-41d4-a5a5-790a3a4b01c6 |  | checkpoint | W-N
button | 4037876f-d6e5-5dbc-9a61-0e8ea3923279 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | d477f3c7-aa58-5755-aa05-0b066a1b7cef |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 9651f12e-c9a4-442d-bc8c-f11c854fa56e |  | checkpoint | B-N
button | 4605fcfd-7b25-5173-a9e7-a07339fd902c |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | a0128354-5305-5bf4-8282-5f7a8295fc7f |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 6e4631a7-7c3b-405e-ab1b-9f82b89f9fd9 |  | checkpoint | R-E
button | c64a6297-5d59-5b92-87a9-d2b62a3fbf04 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 144b208d-ae23-5be7-9e51-128cf9d3dcc2 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 0fccc83f-b50d-4cc0-a288-d4c98f56d0fd |  | checkpoint | W-E
button | a0b931b0-76eb-54d1-bfa0-459efcda5dcf |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 84054121-9153-5416-93f7-c6d93908d8d6 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | fc799b05-5f47-4321-a8db-0c227ad69d10 |  | checkpoint | B-E
button | 729c09c8-067e-5ce3-8113-46aaef757ae0 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | f51bf965-727e-5964-8a37-3fb5928b1a41 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 827f6e60-be17-4eca-9c30-2c54ef6f95c4 |  | checkpoint | N-E
button | 977a6a16-6d9e-51d3-9adc-0d181d6c3fed |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 22efc18d-777c-5ae2-9787-29ab2333ca6e |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-group | e60f69f2-5a59-44f0-8566-b462615f9a6b |  | section | Voltage
checkpoint-status | cac5f44a-a6bc-43b1-bc53-f27a0da64f14 |  | checkpoint | Red - White
text | d4f6e39a-cf4b-52ba-bdcb-be3fcffe2da4 |  | textbox | Voltage (V)
checkpoint-status | 04166c8d-957b-4eff-8864-5075cad5d374 |  | checkpoint | Red - Blue
text | c2419cc4-d59c-522d-bc84-c1b9e086ff6d |  | textbox | Voltage (V)
checkpoint-status | 8d39a288-efcc-46a4-94b9-e7db2c44ff87 |  | checkpoint | White - Blue
text | b6a6b526-117f-5e79-8caf-03a2f65b3c2c |  | textbox | Voltage (V)
checkpoint-status | 37f3f198-3fa3-4e3c-8adc-2d6c6cbb04a1 |  | checkpoint | Red - Neutral
text | 84e20906-51b7-5586-ba8a-2d4a0116eb57 |  | textbox | Voltage (V)
checkpoint-status | ba9cca36-b89a-4d4e-91ec-08c54b9d4d4d |  | checkpoint | White - Neutral
text | 5b8dd4b2-2a55-5141-8932-7780c4377448 |  | textbox | Voltage (V)
checkpoint-status | 105d0dae-3ddb-45ad-8b9a-83a2318b7f89 |  | checkpoint | Blue - Neutral
text | d043e074-431b-5586-a349-5e7e8b33c605 |  | textbox | Voltage (V)
checkpoint-status | f2f49762-0dc4-40de-95b0-61b04776d6e4 |  | checkpoint | Red - Earth
text | d88e464b-bed5-5f0c-af21-50d796bb2403 |  | textbox | Voltage (V)
checkpoint-status | 2d1255f8-a0dd-4086-9488-3b81ccfe8362 |  | checkpoint | White - Earth
text | 525be556-c6cd-5964-97e9-9b8c22e9604b |  | textbox | Voltage (V)
checkpoint-status | f436332f-ea9d-4c26-baaf-6498f0980e05 |  | checkpoint | Blue - Earth
text | a12e795b-46a0-5ee2-be31-e824ee9c758c |  | textbox | Voltage (V)
checkpoint-group | 4bb0e1c9-4368-4df3-bb6e-c9fb61376ee0 |  | section | Earth Fault Loop Impedance Test / RCD-RCBO Tripping Test
checkpoint-status | b0df5f2e-1ff1-49a7-8eba-c133f962acfe |  | checkpoint | Impedance - (N/A if the circuit is RCD Protected)
text | b044fe0b-852f-5b44-844f-169a2ebc699d |  | textbox | Record Inpedance (Ω)
text | b93650ce-1006-567a-bce0-c07128c7e1cf |  | textbox | Target Impedance (Ω)
checkpoint-status | 79eb7072-a04e-4b6a-85e5-30b4b5f2109d |  | checkpoint | RCD-RCBO Tripping Test
text | abf38619-a914-59e4-97ed-521a8167c7c6 |  | textbox | Trip Current (mA)
text | 273439a4-eb3c-5eaa-b343-12c237a4b61d |  | textbox | Trip Time (ms)
holdpoint | 6aa7fba7-6aac-4dd5-a301-11e58a52dfb3 |  | signoff | Checked By (Heyday):
checklist-sectioned | 10d56c3d-cdad-465f-b948-220f28af9777 |  | checklist | Single Phase Subcircuit |  |  |  | 38 | Yes | Testing & Commissioning - Single Phase Subcircuit | d39c9bf5-d9de-48e6-bf12-2665475ce605
checkpoint-group | 99fcf775-d9d9-45aa-bc40-72ea8e95beac |  | section | Pre-requisite Works
checkpoint-status | b6245e80-1e48-4375-9cfc-b3295cba6b21 |  | checkpoint | Insulation Damage
checkpoint-status | c960e5b7-636f-44eb-8b9e-1acc1f6c3372 |  | checkpoint | Correct Type of Termination
checkpoint-status | 830d7519-7adc-4fe4-990f-97619c9fa743 |  | checkpoint | Correct Colour Code
checkpoint-status | 6623d9a4-6615-4c48-a1c0-4c32931da7b4 |  | checkpoint | Correct Outlet Rating and Size
checkpoint-status | 6af80b46-6884-4add-b7f2-b4eb130de2b9 |  | checkpoint | Earth Continuity
text | 060aa90b-811f-5ad5-a5da-76c27b44531f |  | textbox | Resistance (Ω)
text | d99c08c2-b8bd-562c-a170-aa9811cdc9a6 |  | textbox | Target Resistance (Ω)
checkpoint-status | 7eec440f-bc3f-455d-bf19-55fc824a350a |  | checkpoint | Polarity Check
button | 440b6016-299e-5394-867f-385fa07202af |  | button | No Transposition | YES,NO
button | 053b0de7-0eb6-5547-9d2d-46e1f3bf95e9 |  | button | Switch in Active | YES,NO
checkpoint-group | f4a80d27-97cd-4a26-b498-168f68df6e9a |  | section | Insulation Resistance
checkpoint-status | 8ba76168-4007-4b84-a280-12de7c138cd0 |  | checkpoint | R-N
button | 537274d1-6646-5c85-9b27-ebf56328087c |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 6dafc51c-6de6-5824-870b-a7a7a90a7265 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | db4bc454-6f5c-491f-a3a3-dfaca4127ad2 |  | checkpoint | R-E
button | 8982dd66-b9fb-5b80-853e-77054ede7db5 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | ae800fe7-c015-5255-b809-77f63aec3189 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 40c2ab33-5545-4ccd-9b21-54406f15e189 |  | checkpoint | N-E
button | b6de9cfe-c2d0-5ae3-97a9-4ecc322b1504 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 7eaa26a2-e6bf-5dbe-bc66-803628eeb184 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-group | 28c42bf5-375b-4323-800e-8f7333eb5598 |  | section | Voltage
checkpoint-status | c4eb594f-a5e8-4bda-ad37-025dc2ed4b10 |  | checkpoint | Red - Neutral
text | 40d5203f-80a5-5632-8e29-135176de772d |  | textbox | Voltage (V)
checkpoint-status | 23234cdd-c1ec-4a2d-a172-b8a9451f300a |  | checkpoint | Red - Earth
text | fb73a258-9d7e-5f99-b38f-64a76c6df601 |  | textbox | Voltage (V)
checkpoint-group | b0eba347-4d78-4768-a547-43d5a8d27339 |  | section | Earth Fault Loop Impedance Test / RCD-RCBO Tripping Test
checkpoint-status | 9af5b6e3-ad80-4327-acd6-fd1c0042d1b4 |  | checkpoint | Impedance - (N/A if the circuit is RCD Protected)
text | ca658463-6c9b-535c-9f84-e77a01da0d98 |  | textbox | Record Inpedance (Ω)
text | 35a29d49-1248-5728-ad7c-5f968884a5b1 |  | textbox | Target Impedance (Ω)
checkpoint-status | 4429efd3-4f70-4c1d-b68e-8e99ef5835f9 |  | checkpoint | RCD/RCBO Tripping Test
text | e3ba2339-b613-58ff-83a6-2095d2667dcd |  | textbox | Trip Current (mA)
text | e0ca11a2-eb7e-51dd-ad53-5839c860a2f7 |  | textbox | Trip Time (ms)
holdpoint | 858b7cb6-6ac1-489a-b2ee-fa203eaa4510 |  | signoff | Checked By (Heyday):