## zres_siteapp
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | 3ca3689f-77c0-48c2-ab24-e1d735cf09e7 |  | checklist | 3 Phase Subcircuit |  |  |  |  | Yes | Testing & Commissioning - 3 Phase Subcircuit | 19071929-685f-49b6-b72e-0610d6396ab2
checkpoint-group | 861fd99c-dca8-43d2-8e4b-f8409081293a |  | section | Pre-requisite Works
checkpoint-status | 6da69891-19bb-46f6-a2d4-9b9cf3d8e4bc |  | checkpoint | Insulation Damage
checkpoint-status | 7225f360-ac04-4778-95db-9dbcc07e76ac |  | checkpoint | Correct Type of Termination
checkpoint-status | 3971722c-baa9-43a9-aa06-c86c6056edfb |  | checkpoint | Correct Colour Code
checkpoint-status | 9708cbf1-ec02-4027-9710-1f71e383629d |  | checkpoint | Correct Outlet Rating and Size
checkpoint-status | e327169b-3ebd-4006-adbb-d344cb7384ca |  | checkpoint | Earth Continuity
text | d1fad654-d6b7-5aaa-ad18-5ced852d1212 |  | textbox | Resistance (Ω)
checkpoint-status | 21706f16-3e14-4132-869a-39878965623e |  | checkpoint | Polarity Check
button | a878f000-c1ad-5c8c-917d-0e62e1a0e5c2 |  | button | No Transposition | YES,NO
button | b8ec0463-70f4-5599-97fb-21e80b4abc49 |  | button | Switch in Active | YES,NO
checkpoint-group | 9cac9730-f4a3-4380-b5fb-b44eee12d42e |  | section | Insulation Resistance
checkpoint-status | 96dd6692-f9e5-4dbd-8b51-64a37deb1e6e |  | checkpoint | R-W
button | 2b39491a-1d6a-511a-82f4-71cfabd13a8c |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | d348ccc8-6968-5dae-a021-9c9ceffa5e6f |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | f206d7ac-521d-4be4-8f41-eea8e2e1e3bf |  | checkpoint | R-B
button | 52a2c584-84aa-5609-880b-8300f96e8f5e |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | f9cb7812-44c5-52af-a9b2-3ffb8d4e72a6 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 882b4c0f-8dcb-4d8c-8881-b4c7b13c157a |  | checkpoint | W-B
button | c6af3168-67a5-5e0e-935f-deba5b39563d |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 92fa960a-d385-55d2-a305-6489a079a3f0 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 8ed72945-9322-49ab-879b-2450c3ad8f68 |  | checkpoint | R-N
button | f3510836-c94f-5348-bc00-0fe3bd323739 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 8f7cadda-8d23-53d8-af25-7ee29ed9e6e2 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 3ce7661c-5fca-41d4-a5a5-790a3a4b01c6 |  | checkpoint | W-N
button | 4037876f-d6e5-5dbc-9a61-0e8ea3923279 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | d477f3c7-aa58-5755-aa05-0b066a1b7cef |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 9651f12e-c9a4-442d-bc8c-f11c854fa56e |  | checkpoint | B-N
button | 4605fcfd-7b25-5173-a9e7-a07339fd902c |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | a0128354-5305-5bf4-8282-5f7a8295fc7f |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 6e4631a7-7c3b-405e-ab1b-9f82b89f9fd9 |  | checkpoint | R-E
button | c64a6297-5d59-5b92-87a9-d2b62a3fbf04 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 144b208d-ae23-5be7-9e51-128cf9d3dcc2 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 0fccc83f-b50d-4cc0-a288-d4c98f56d0fd |  | checkpoint | W-E
button | a0b931b0-76eb-54d1-bfa0-459efcda5dcf |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 84054121-9153-5416-93f7-c6d93908d8d6 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | fc799b05-5f47-4321-a8db-0c227ad69d10 |  | checkpoint | B-E
button | 729c09c8-067e-5ce3-8113-46aaef757ae0 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | f51bf965-727e-5964-8a37-3fb5928b1a41 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 827f6e60-be17-4eca-9c30-2c54ef6f95c4 |  | checkpoint | N-E
button | 977a6a16-6d9e-51d3-9adc-0d181d6c3fed |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 22efc18d-777c-5ae2-9787-29ab2333ca6e |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-group | e60f69f2-5a59-44f0-8566-b462615f9a6b |  | section | Voltage
checkpoint-status | cac5f44a-a6bc-43b1-bc53-f27a0da64f14 |  | checkpoint | Red - White
text | d4f6e39a-cf4b-52ba-bdcb-be3fcffe2da4 |  | textbox | Voltage (V)
checkpoint-status | 04166c8d-957b-4eff-8864-5075cad5d374 |  | checkpoint | Red - Blue
text | c2419cc4-d59c-522d-bc84-c1b9e086ff6d |  | textbox | Voltage (V)
checkpoint-status | 8d39a288-efcc-46a4-94b9-e7db2c44ff87 |  | checkpoint | White - Blue
text | b6a6b526-117f-5e79-8caf-03a2f65b3c2c |  | textbox | Voltage (V)
checkpoint-status | 37f3f198-3fa3-4e3c-8adc-2d6c6cbb04a1 |  | checkpoint | Red - Neutral
text | 84e20906-51b7-5586-ba8a-2d4a0116eb57 |  | textbox | Voltage (V)
checkpoint-status | ba9cca36-b89a-4d4e-91ec-08c54b9d4d4d |  | checkpoint | White - Neutral
text | 5b8dd4b2-2a55-5141-8932-7780c4377448 |  | textbox | Voltage (V)
checkpoint-status | 105d0dae-3ddb-45ad-8b9a-83a2318b7f89 |  | checkpoint | Blue - Neutral
text | d043e074-431b-5586-a349-5e7e8b33c605 |  | textbox | Voltage (V)
checkpoint-status | f2f49762-0dc4-40de-95b0-61b04776d6e4 |  | checkpoint | Red - Earth
text | d88e464b-bed5-5f0c-af21-50d796bb2403 |  | textbox | Voltage (V)
checkpoint-status | 2d1255f8-a0dd-4086-9488-3b81ccfe8362 |  | checkpoint | White - Earth
text | 525be556-c6cd-5964-97e9-9b8c22e9604b |  | textbox | Voltage (V)
checkpoint-status | f436332f-ea9d-4c26-baaf-6498f0980e05 |  | checkpoint | Blue - Earth
text | a12e795b-46a0-5ee2-be31-e824ee9c758c |  | textbox | Voltage (V)
checkpoint-group | 4bb0e1c9-4368-4df3-bb6e-c9fb61376ee0 |  | section | Earth Fault Loop Impedance Test / RCD-RCBO Tripping Test
checkpoint-status | b0df5f2e-1ff1-49a7-8eba-c133f962acfe |  | checkpoint | Impedance - (N/A if the circuit is RCD Protected)
text | b044fe0b-852f-5b44-844f-169a2ebc699d |  | textbox | Record Inpedance (Ω)
text | b93650ce-1006-567a-bce0-c07128c7e1cf |  | textbox | Target Impedance (Ω)
checkpoint-status | 79eb7072-a04e-4b6a-85e5-30b4b5f2109d |  | checkpoint | RCD-RCBO Tripping Test
text | abf38619-a914-59e4-97ed-521a8167c7c6 |  | textbox | Trip Current (mA)
text | 273439a4-eb3c-5eaa-b343-12c237a4b61d |  | textbox | Trip Time (ms)
holdpoint | 6aa7fba7-6aac-4dd5-a301-11e58a52dfb3 |  | signoff | Checked By (Heyday):
checklist-sectioned | 10d56c3d-cdad-465f-b948-220f28af9777 |  | checklist | Single Phase Subcircuit |  |  |  |  | Yes | Testing & Commissioning - Single Phase Subcircuit | d39c9bf5-d9de-48e6-bf12-2665475ce605
checkpoint-group | 99fcf775-d9d9-45aa-bc40-72ea8e95beac |  | section | Pre-requisite Works
checkpoint-status | b6245e80-1e48-4375-9cfc-b3295cba6b21 |  | checkpoint | Insulation Damage
checkpoint-status | c960e5b7-636f-44eb-8b9e-1acc1f6c3372 |  | checkpoint | Correct Type of Termination
checkpoint-status | 830d7519-7adc-4fe4-990f-97619c9fa743 |  | checkpoint | Correct Colour Code
checkpoint-status | 6623d9a4-6615-4c48-a1c0-4c32931da7b4 |  | checkpoint | Correct Outlet Rating and Size
checkpoint-status | 6af80b46-6884-4add-b7f2-b4eb130de2b9 |  | checkpoint | Earth Continuity
text | 060aa90b-811f-5ad5-a5da-76c27b44531f |  | textbox | Resistance (Ω)
checkpoint-status | 7eec440f-bc3f-455d-bf19-55fc824a350a |  | checkpoint | Polarity Check
button | 440b6016-299e-5394-867f-385fa07202af |  | button | No Transposition | YES,NO
button | 053b0de7-0eb6-5547-9d2d-46e1f3bf95e9 |  | button | Switch in Active | YES,NO
checkpoint-group | f4a80d27-97cd-4a26-b498-168f68df6e9a |  | section | Insulation Resistance
checkpoint-status | 8ba76168-4007-4b84-a280-12de7c138cd0 |  | checkpoint | R-N
button | 537274d1-6646-5c85-9b27-ebf56328087c |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 6dafc51c-6de6-5824-870b-a7a7a90a7265 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | db4bc454-6f5c-491f-a3a3-dfaca4127ad2 |  | checkpoint | R-E
button | 8982dd66-b9fb-5b80-853e-77054ede7db5 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | ae800fe7-c015-5255-b809-77f63aec3189 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 40c2ab33-5545-4ccd-9b21-54406f15e189 |  | checkpoint | N-E
button | b6de9cfe-c2d0-5ae3-97a9-4ecc322b1504 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 7eaa26a2-e6bf-5dbe-bc66-803628eeb184 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-group | 28c42bf5-375b-4323-800e-8f7333eb5598 |  | section | Voltage
checkpoint-status | c4eb594f-a5e8-4bda-ad37-025dc2ed4b10 |  | checkpoint | Red - Neutral
text | 40d5203f-80a5-5632-8e29-135176de772d |  | textbox | Voltage (V)
checkpoint-status | 23234cdd-c1ec-4a2d-a172-b8a9451f300a |  | checkpoint | Red - Earth
text | fb73a258-9d7e-5f99-b38f-64a76c6df601 |  | textbox | Voltage (V)
checkpoint-group | b0eba347-4d78-4768-a547-43d5a8d27339 |  | section | Earth Fault Loop Impedance Test / RCD-RCBO Tripping Test
checkpoint-status | 9af5b6e3-ad80-4327-acd6-fd1c0042d1b4 |  | checkpoint | Impedance - (N/A if the circuit is RCD Protected)
text | ca658463-6c9b-535c-9f84-e77a01da0d98 |  | textbox | Record Inpedance (Ω)
text | 35a29d49-1248-5728-ad7c-5f968884a5b1 |  | textbox | Target Impedance (Ω)
checkpoint-status | 4429efd3-4f70-4c1d-b68e-8e99ef5835f9 |  | checkpoint | RCD/RCBO Tripping Test
text | e3ba2339-b613-58ff-83a6-2095d2667dcd |  | textbox | Trip Current (mA)
text | e0ca11a2-eb7e-51dd-ad53-5839c860a2f7 |  | textbox | Trip Time (ms)
holdpoint | 858b7cb6-6ac1-489a-b2ee-fa203eaa4510 |  | signoff | Checked By (Heyday):