## ITP Cover Page
Northern Access Road - Watermain Inspection and Test Plan
Project: Tauriko Enabling Project
Number and Revision: DN1210-SP2 - ITP 011-003 - Rev 1
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | Tauriko Enabling Project |  |  |  |  | ITP Number: |  |  | ITP 011-003
Project Number: |  |  | DN1210-SP2 |  |  |  |  | ITP Status: |  |  | IFC
ITP Description: |  |  | Northern Access Road Watermain |  |  |  |  | Revision: | 1000 |  | 1
Contract Number: |  |  | 8287 |  |  |  |  | Drawing Sets: |  |  | 2-32735.02-WSP-DR-WAT
Customer: |  |  | Waka Kotahi |  |  |  |  | Specification: |  |  | Section 22
Quality Specified: |  |  | ISO 9001:2015
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  | Responsibilities Key
0 | Draft for Approval | 2025-05-09 |  | WSP |  | CWP Section 4: It's unclear how you intend to install the stub flanges, backing rings, and T-sections for the AV and FH connections between the pulling the main through the sleeve and placing the 114m section in the trench. - This is noted in our stages of works showing installation areas. CWP Section 4: There needs to be sufficient shoulder for butt welding the stubs in the correct position. If the full string is pre-welded, then you need to cut and weld in the trench?, which is not ideal and poses construction and alignment risks. - This is shown in our stages. CWP Section 4: If electrofusion welding is proposed for these sections, it must be clearly stated in the methodology and pre-approved by TCC. - Noted this. There shouldnt be any EF welding in this area. CWP Section 4: Can you please review methodology and sequencing, detailing how AV/FH connections and T-sections will be installed and whether butt weld or electrofusion will be used. - Amended and added stages to show more clearly how our works will take place. ITP 4.4 Compaction Testing : Added appendix XVIII to ITP ITP 3.3 Pipeline Pressure Test: Added PS 22.7.12 and appendix XXI to ITP ITP 11 Air Valves: Added Project Drawings (232735.02-WSP-DR-WAT SHEET 0314 to 0316) ITP 12 Fire Hydrant: Added Project Drawings (232735.02-WSP-DR-WAT SHEET 0322) Item 3.4 make ref to EF weld test, but there should be no EF weld test without prior approval from TCC. Added to necessary sections of ITP: Paeangaroa Sand - 9 average CIV, 7% min CIV Wilson No.2 Sand - 4% CIV |  |  |  | A | Action |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  | CR | Customer Rep
[10 empty] | C | Check |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  | PM | Project Manager
[10 empty] | E | Examine |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) |  | HSE | HSE Manager / Rep
[10 empty] | H | Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) |  | PE/SE | QA Manager / Rep
[10 empty] | I | Inspection (Formal inspection activity to be undertaken and recorded) |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[10 empty] | O | Operation |  | QE | Quality Engineer
[10 empty] | R | Review |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  | SV | Surveyor
[10 empty] | V | Visual Verification |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point (Review of text reports/records or other evidence of compliance) |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  | Signature: |  |  | Date:
Downer PM |  | NICK ADAMS |  |  | #VALUE! |  | 23/05/2025 | Downer PM |  | NICK ADAMS
Downer QM |  | CORDELIA GIRDLER-BROWN |  |  |  |  | 26/05/2025 | Downer QM |  | CORDELIA GIRDLER-BROWN
Client (If Applicable) | [7 empty] | Client (If Applicable)

## ITP Master Body
Retaining Wall 4 - Watermain
Tauriko Enabling Works
DN1210 - SP2- ITP010-003-002 - REV 0
Item No. | Inspection and Test Point | Detail / Activity | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Testing Quantity Required (based from schedule qtys) | Verification Activity |  | Downer Conformance of Compliance Signoff
[7 empty] | Activity | By | ConQA Signature | Date | Comments / Closeout Details | ENGINEERS COMMENTS - Date: | DOWNER RESPONSE - Date:
3 | PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS - ALL TESTS TO BE NO OLDER THAN 3 MONTHS
3.1 | Extent of Line Setout | Ensure line and level of Watermain has been marked out and agreed with Engineer in accordance with Watermain drawings. Identify any clashes before construction. LOT- markup | As Per Drawings & Markup drawing | Design Drawings | ITP Sign Off / Mark-up | Prior to Construction & Every Revision of IFC Drawings/Data. | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.2 | Pipe Laying | Method statement | As Per Specification and IFC Drawings | PS- 22.3 Appendix V | Watermain Construction Work Pack Sign off | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.3 | Pipeline Pressure Testing | Method statement | As Per Specification and IFC Drawings | PS- 22.3 PS 22.7.12 Appendix V Appendix XXI | Watermain Pipeline Pressure Testing Work Pack Sign off | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG |  |  |  | Add PS 22.7.12 and ad Appendix XXI | Added PS 22.7.12 and appendix XXI to ITP
3.4 | EF Pre Construction Weld Tests (if required) | Passing result in accordance with ISO21751 (strip bend test) tested by an IANZ accredited laboratory). There should be no EF weld test without prior approval from TCC. | Passing result in accordance with ISO21751 (strip bend test) tested by an IANZ accredited laboratory. TCC Approval Prior to Works | ISO21751 TCC IDC DS-7.6.4.b.ii PS-22.9.6 | Laboratory Test Report | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG |  |  |  | Item 3.4 make ref to EF weld test, but there should be no EF weld test without prior approval from TCC. | Add that there should be approval from TCC prior to construction
3.5 | Butt-Fusion pre construction weld test | One weld on the most common size of pipes used for the project. One weld on the thickest wall (highest PN) pipe | Test to be down in accordance of ISO 13953 for tensile strength and failure mode. WMS Report | PS 22.9.6 (a) ISO 13953 Standard | Visual Inspection | Two test welds per operative(Welder) | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.6 | Material grading: Materials (Gap65/AP65) | NZS4407:2015, Test 3.8.1 - Particle Size Distribution | No Particles >200mm Maximum fines 10% passing 75micron sieve | PS 22.13.1 Appendix XVIII PS 16.5.5 Appendix V | Lab Test Report NZS 4407.3.8.1 | Stockpile Size (m3): 0-400 - 2 tests 400-1,500 - 3 tests 1,500-4,000 - 4 tests >4,000 - 1 test for each additional 1,000m3 Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.7 | Weathering index: Materials (Gap65/AP65) | NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate | AA, AB, AC, BA, BB, or CA | Appendix XVIII PS 16.5.5 Appendix V NZS4407:2015 Test 3.11 | IANZ Accredited Report | 2 Tests Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.8 | Crushing Resistance: Materials (Gap65/AP65) | NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load | >100KN | Appendix XVIII Appendix V NZS4407:2015 Test 3.10 | IANZ Accredited Report | 2 Tests Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.9 | Maximum Dry Density and Optimum Water Content | NZS4402:1986, Test 4.1.2 - Heavy Compaction Test | Report Value Only | Appendix XVIII Appendix V NZS4402:1986 Test 4.1.2 | IANZ Accredited Report | 1 Test Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.1 | Material grading: Materials (GAP20/19mm chip/Sand SAP7) | Bedding/Side Zone/ Overlay Zone/Embedment Zone | Sieve Size % Passing 19.0mm 85-100% passing 9.5mm 25-55% passing 4.75mm 0-10% passing 2.36mm 0-5% passing 0.075mm 0-2% passing | AS/NZS 2566.2 PS 22.4.5 | Lab Test Report NZS 4407.2015 Test3.8.1 | 0-400m3 2 Test 400-1500m3 3 Test 1500-4000m3 4 Test >4000 1 Test Additional 1000m3 | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.11 | Soaked CBR | NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR) | >80% | Project Specifications 20.9 TCC-IDC IT-4.8 table 4.6 | IANZ Accredited Report | IANZ Accredited Report | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.12 | Pipes (DN315 PE100 PN16) | Manufacturer's record and location of extrusion plants. Name of the proposed PE resin, the manufacturer, production information on the properties of resin. Full Traceability information and certification of analysis for the resin batch. | Full Traceability information and certification of Material and resin. | PS-22.4.1 (d) | Full Traceability information and certification of Material and resin. Delivery Dockets | Prior to construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.13 | Valves, Adaptors, Flanges and Fittings | Have a pressure rating no less than the designed pressure. Mechanically, chemically and electrically compatible with the class and material of the pipe. Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose. | Engineer approval AS/NZS 4129 | PS-22.4.2 | Delivery Dockets | Prior to construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.14 | Fusion Joint Compatibility | Confirm pipe and fittings compatibility for fusion welding | No defects, compatible resin types per NZS/AS 2033 | NZS/AS 2033:1980, Clause 4.2 | Test Report | 1 per material type | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | ENG
3.15 | Pipe and fittings. | Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Design Drawings | Delivery Dockets / Inspection Checksheet (DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.16 | Valves, Adaptors, Flanges, Caps and Fittings | Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition. | Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition. | PS-22.4.2 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.17 | Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65) | Confirm Specification and material in good condition. | Confirm Specification and material in good condition. | PS-22.4.1 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.18 | Bidim/Geogrid | BIDIM A29 Durogrid 30/30 or similar. | Site Engineer Approval | PS-22.4.1 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.19 | Pre-cast Manholes | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Design Drawings | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.2 | KWIK Spacers | Placing spacers on DN315 pipe when being inserted into DN560 sleeve | Model: HDXT43 (43mm). 1.5m spacing | Project Drawings (232735.02-WSP-DR-WAT) Sheet 0312 | Visual Insepction, Photographs | Pipe under NAR | I Formal inspection activity to be undertaken and recorded | PE/SE
4 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE INSTALLATION - Excavation and Laying
4.1 | Foundation Compliance | On Granular or Cohesive Material | Granular Material: Scala 3 blows/100mm (Or) Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa | Appendix V Table 21:11 | Scala/Shear test result | One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. | W Review of text reports/records or other evidence of compliance | SE
4.2 | Undercut approval | Trench Foundation (subgrade) | Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material. | PS-21.6.5 Table 21.5 | Lab Test Report / Wastewater line record | If Undercut required | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.3 | Undercut Backfill Compliance | On Granular Material / On each layer as per specification / on the trench foundation. | Average 95% MDD, min >92% OR Clegg 25% CIV | PS- 16.5.12 | Lab Test Report / Wastewater line record | Every Undercut | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.4 | Bedding Zone Compaction Testing | On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip) | Bedding Zone: 100mm minimum thickness (compacted) over the bottom of the trench. Minimum Compaction- 85%MDD Paeangaroa Sand - 9 average CIV, 7% min CIV Wilson No.2 Sand - 4% CIV | IFC Drawing 0320-1 AS/NZS 2566.2/2002 Appendix XVIII Site Instruction | Lab Test Report | As per WM Specification. One test per 20m evenly spaced intervals. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  | Add appendix XVIII to ITP | Added appendix XVIII. Paeangaroa Sand - 9 average CIV, 7% min CIV Wilson No.2 Sand - 4% CIV
4.5 | Laying of Pipes (DN315 PE Pipe) | Lay in straight lines, beginning at the lower end of the line. Lay all pipe with manufacturing codes and class markings facing upwards. | As Per Drawings. Facing upwards | PS22.7.1 C | Visual Inspection / Wastewater line record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.6 | Compaction of Pipe Embedment Material | Compact embedment to required density | Achieves 85% MDD, as per project drawings SHEET 0320 | Project Specification 22.13.1 | BACKFILL Check Sheet | Every 20m, 200mm lift | W Review of text reports/records or other evidence of compliance | ENG
4.7 | Cold Bending of Pipe | Verify minimum bend radius | Min bend radius 50x pipe diameter (31.5m) | Contract Specification 21.6.6 | Survey As-Built Records | Every cold bend | I Formal inspection activity to be undertaken and recorded | ENG
4.8 | Pipe Installation on Curved Alignments | All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202) | AS Per POP 202 | PS 22.7.1 D | Visual Inspection / Wastewater line record | Every Line | M Monitor on Random Basis | SE
4.9 | Tracer Wire Installation | Install tracer wire along pipe | 4mm² multi-strand polythene sleeved copper cable, strapped every 3m with slack | Project Specification 22.7.3 | BACKFILL Check Sheet | Every 20m | R review | ENG
4.1 | Northen Access Pipe Caping | PETROLATUM WRAP SYSTEM | IN ACCORDANCE WITH PROJECT SPECIFICATION as per sheet 0307 | Project Drawings (232735.02-WSP-DR-WAT) | Photographic Evidence | Pipe end | W Review of text reports/records or other evidence of compliance | ENG
4.11 | Northen Access Pipe Caping | STUB FLANGE AND GALVANISED BACKING RING (PN16) | IN ACCORDANCE WITH PROJECT SPECIFICATION as per sheet 0305 | Project Drawings (232735.02-WSP-DR-WAT) | Photographic Evidence | Pipe end | W Review of text reports/records or other evidence of compliance | ENG
4.12 | DN315 SLEEVED ROAD CROSSING (Sleeve is already installed only pulling DN315 through) | THE OUTER ENDS OF THE SLEEVE ARE TO BE FILLED AND SEALED WITH EXPANDING 'PU' FOAM. ANNULUS TO BE GROUTED AFTER INSTALLATION. | REFER TO SHEET No's 312 | Project Drawings (232735.02-WSP-DR-WAT) | Photographic Evidence | PIPE SLEEVE ENDS | I Formal inspection activity to be undertaken and recorded | ENG
5 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Joint and Connection
5.1 | Flanges | Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification. | Flanges to AS/NZS 4087 | PS 22.7.5 Appendix XXII | Visual Inspection | First flanged joint | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
5.2 | Bends | PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings or approcval from engineer. Fitting must meets the same PN rating as the adjacent PE 100. Fittings must be suitable for producing the joints shown on the Drawings. | PIPA POP 006 and AS/NZS 4129 | PS 22.4.2 Appendix XXII | Visual Inspection | Project Drawings (232735.02-WSP-DR-WAT SHEET) | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE/ENG
6 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Butt-Fusion Welding
6.1 | Butt-Fusion Welding | Use only semi-automatic or automatic welding machines. Maintain a site record for all butt-fusion welds. The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct. | Site Butt Fusion Welding record to be filled out. (Refer to CWP) WMS Report | Appendix XXII PS 22.9.4 C | Visual Inspection / Butt Fusion welding records checklist. WMS Report | Every Welding Point | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
6.2 | Butt-Fusion Construction Weld Test | Test at least two welds from the first 50 welds. One of the welds to be selected by the Engineer for satisfactory result. | Tensile testing and ductility of welds. 95% tensile strength; welds aligned | PS- 22.9.6 (a) (iv) | Test report | Two welds for the first 50 welds | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
6.3 | Survey | Inspection of Pipeline Inverts | Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance | PS- 21.7.6 Table 21.15 | Survey Data / As-built record | Pipeline invert to be surveyed at chainages as indicated in the drawings. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
6.4 | Photograph of Each Weld | Take sharply focused photo while clamped | Unique weld identifier visible | N/A | Weld Records; Photos | Each weld | I Formal inspection activity to be undertaken and recorded | SUB
6.5 | Weld Treatment for Corrosion Resistance | Treat welded areas to restore corrosion resistance | Treated weld areas | Project Drawings (232735.02-WSP-DR-WAT) | QA Documents from Welders | Each weld | W Review of text reports/records or other evidence of compliance | ENG
7 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Backfill
7.1 | Emebment Zone - (Side Haunch Overlay ) | Granular Sand backfill Compacted in 200mm Layers. NDM/CleggTesting to be completed on maximum 200mm lifts of overlays . NDM BS to be Carried Out | in 200mm layers. More than 85% of MDD Paeangaroa Sand - 9 average CIV, 7% min CIV Wilson No.2 Sand - 4% CIV | Project Drawing 0320 Site Instruction | Lab Report / Watermain line record | One test per 20m evenly spaced intervals. 200mm lift | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  |  | Paeangaroa Sand - 9 average CIV, 7% min CIV Wilson No.2 Sand - 4% CIV
7.2 | Pipe Markers | Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings. Mark fire hydrant positions in accordance with SNZ PAS 4509 | AS Per Drawings. | PS 22.7.3 a | Visual Inspection / Watermain line record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
7.3 | Backfill Compaction Testing | GAP65/AP65 Backfill Compacted in 200mm Layers. NDM Testing to be completed on maximum 200mm lifts of backfill. | GAP65/AP65or site won material Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill. 95% NDM on Shared and Carriageway. OR 28% CIV For site won min >60kpa Ave > 80kpa | PS- 22.13.5 NDM Standerd 25832 NZS 4402 Test 4.1.3 IFC Drawing 0320-1 | Lab Report / Watermain line record | As per WM Specification. One test per 20m evenly spaced intervals. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
8 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Inspection
8.1 | Pipe Inspection | Inspection of Drainage line | Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness | Internal | Watermain line record | Continious 1 per Line | I Formal inspection activity to be undertaken and recorded | SE
9 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE TESTING
9.1 | Pressure Acceptance Testing | Backfill/cover with embedment before testing End caps in place, provision for filling the pipeline and bleeding air. | Potable Watermain Pipelines – 1250kPa Ensure the STP is not more than 25% above the rated pressure of any pipeline component. | PS 22.7.12(d) PS 22.7.13(b) | Test Report Pressure Log in.csv or .xlsx format | All Pipeline All valves | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
9.2 | Swab New PE Watermain | Swab to remove debris and air | Water running clear & removed entrapped air | TCC IDC TS-7 | Swabbing Check Sheet | All new pipe installed | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SUP/SE
9.3 | Pressure Test New PE Watermain | Conduct pressure test. Due to not commissioning the pipe until later in the project, CB will complete our own pressure testing upon installation of the pipe, with the full pressure testing and chlorination to be completed once the pipe is ready to be commissioned. | No leaks, no failure of any pipe, fitting or other pipeline component. | TCC IDC TS-7.1c Pressure Rebound Test Method; TS-7.1a Constant Pressure Test Method | TS-7.1a/c Pressure Test Method (Test Report) | All new pipe installed & swabbing passed | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SUP/SE
9.4 | Chlorinate New PE Watermain | Chlorinate watermain | 5+ pH on chlorine tester | TCC IDC IT-7.4.1 Disinfection Procedure | Picture; Signed Chlorination Check Sheet | All new pipe installed & pressure test passed | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SUP/SE
9.5 | E. Coli Test New PE Watermain | Test for bacterial contamination | <1 E. coli; <1 Coliforms | TCC IDC IT-7.5 E. coli Sampling | E. coli Test Report | All new pipe installed & chlorine test passed | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SUP/SE
10 | CONSTRUCTION ACTIVITY - WATERMAIN Manhole installation
10.1 | Foundation Compliance | On Granular or Cohesive Material | Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa | Appendix V Table 21:11 | Shear vane or Scala test result | 1 Test/Manhole | W Review of text reports/records or other evidence of compliance | SE
10.2 | Undercut approval | On Subgrade | Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material. | Table 21.5 | Lab Test Report | If Undercut required | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
10.3 | Undercut Backfill Compliance AP65 | On Granular Material | Average 95% MDD, min >92% OR Clegg 25% CIV | PS- 16.5.12 | Lab Test Report | 1 Test per Undercut | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
10.4 | Bedding Compaction Testing Sand/AP65 | On Granular Material | Average 95% MDD, min >92% OR Clegg 25% CIV Paeangaroa Sand - 9 average CIV, 7% min CIV Wilson No.2 Sand - 4% CIV | PS- 16.5.12 PS- 21.6.11 | Lab Test Report | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  |  | Paeangaroa Sand - 9 average CIV, 7% min CIV Wilson No.2 Sand - 4% CIV
10.5 | Survey | Inspection of Structure | Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm. | PS- 21.7.6 | Survey Data | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SV
10.6 | Sidefill Compaction Testing | From the bedding layer to the overlay layer of pipe. | AP20/GAP20 Testing to be completed on maximum 200mm lifts of backfill - 85% MDD AP20/19mm chip | PS- Table 21.12 | Lab Test Report | 4 Density test per layer at Quarter Points around the Structure. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
10.7 | Backfill Compaction Testing | From Overlay layer to the subgrade layer | AP65 Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal. AP65-Clegg28%CIV | PS- 16.5.12 | Lab Test Report | 4 Density test per layer at Quarter Points around the Structure. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
10.8 | Manhole | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Design Drawings | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
10.9 | MH joints inspection | Inspection of joints | Right joint type used, no visual leak or breakage | PS 22.7.10 | Visual inspection | 1 Test/Manhole | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
10.1 | Inspection | Inspection of Structure | Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure. | PS- 21.6.11 | Manhole Record | 1 Checksheet per manhole/catchpit | I Formal inspection activity to be undertaken and recorded | SE
10.11 | Plumb | The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise. | The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise. | PS-22.7.10 | Survey Data | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SV
10.12 | Step Rungs | Step rungs evenly spaced at nominal 300mm vertical intervals | Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover | PS-22.7.11 | Visual inspection | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
11 | CONSTRUCTION ACTIVITY - AIR VALVES
11.1 | Installation of Isolation Valve | Verify installation per manufacturer’s instructions | Installed as per manufacturer’s instructions. Project Specifications | PS-22.4.2 Project Drawings (232735.02-WSP-DR-WAT SHEET 0314 to 0316) | Air Valve & Isolation Valve Check Sheet | Each isolation valve | I Formal inspection activity to be undertaken and recorded | ENG |  |  |  | No Ref to IFC Drawing | Added Project Drawings (232735.02-WSP-DR-WAT SHEET 0314 to 0316)
11.2 | Installation of Air Valve | Verify installation per manufacturer’s instructions | Installed as per manufacturer’s instructions | PS-22.4.2 Project Drawings (232735.02-WSP-DR-WAT SHEET 0314 to 0316) | Air Valve & Isolation Valve Check Sheet | Each air valve | I Formal inspection activity to be undertaken and recorded | ENG |  |  |  | No Ref to IFC Drawing | Added Project Drawings (232735.02-WSP-DR-WAT SHEET 0314 to 0316)
11.3 | Backfill Compaction Testing | From Overlay layer to the subgrade layer | AP65 Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal. AP65-Clegg28%CIV | PS- 16.5.12 PS- 22.13.5 NDM Standerd 25832 NZS 4402 Test 4.1.3 IFC Drawing 0320-1 | Lab Test Report | 4 Density test per layer at Quarter Points around the Structure. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
12 | CONSTRUCTION ACTIVITY - FIRE HYDRANTS
12.1 | Chamber Location | Location of hydrants and air valve chambers are to be confirmed on site with the TCC Engineer and offset as far back off the seal as possible. | Engineer to confirm onsite location TCC Engineer approval | Project Drawings (232735.02-WSP-DR-WAT SHEET 0322) | PS-22.5.11 TCC sign-off | Checksheet | "HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point." | ENG |  |  |  | No Ref to IFC Drawing | Added Project Drawings (232735.02-WSP-DR-WAT SHEET 0322)
12.2 | Hydrant Surround Blocks, Height to Suit | Hydrant box with 150 x 150mm concrete surround to be finished flush with surrounding ground. | 232735.02-WSP-DR-WAT Typical FH SHEET 0322 | Project Drawings (232735.02-WSP-DR-WAT SHEET 0322) | PS-22.5.11 Checksheet | Supervisor to check. Checksheet | I Formal inspection activity to be undertaken and recorded | ENG |  |  |  | No Ref to IFC Drawing | Added Project Drawings (232735.02-WSP-DR-WAT SHEET 0322)
12.3 | Install Ductile Iron FH | Heavy duty valve box installed as per TCC's Code of Practice | Contractor to ensure flange drilling on DN80 end of reducer matches flange drilling on DN80 hydrant riser | Project Drawings (232735.02-WSP-DR-WAT SHEET 0322) | PS-22.5.11 Checksheet | Checksheet | I Formal inspection activity to be undertaken and recorded | ENG |  |  |  | No Ref to IFC Drawing | Added Project Drawings (232735.02-WSP-DR-WAT SHEET 0322)
12.4 | Concrete Pedestal on Offset Bend | 3mm rubber seat between bend and pedestal 25MPa concrete pedestal | Typical FH sheet 0322 | Project Drawings (232735.02-WSP-DR-WAT SHEET 0321 to 0322) | PS-22.5.11 Checksheet | Per offset | I Formal inspection activity to be undertaken and recorded | ENG |  |  |  | No Ref to IFC Drawing | Added Project Drawings (232735.02-WSP-DR-WAT SHEET 0321 to 0322)
12.5 | Anchor block and to extend past edge of concrete | DN315 - Type 1 Anchor 2000(L) x 600(W) x 2500mm deep concrete anchor block | In accordance with project specification as per sheet 0307 | Project Drawings (232735.02-WSP-DR-WAT SHEET 0321) | Engineer Approval | SH29/Northen Access Rd intersection | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG |  |  |  | No Ref to IFC Drawing | Added Project Drawings (232735.02-WSP-DR-WAT SHEET 0321)
13 | POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
13.1 | Survey As-Builts | Quality Check on Nee pipeline and structure based on the tolerances in RITS | Meets spec as per drawings and capture any NCR or change to design. | Project Specifications | Red pen markup only | Post works completion of a lot | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE