## ITP Cover Page
Northern Access Road Watermain sleeve - Inspection and Test Plan
Project: Tauriko Enabling Project-SP2
Number and Revision: DN1210-SP2 - 011-005 - Rev 2
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | Tauriko Enabling Project-SP2 | [5 empty] | ITP Number: |  |  | 011-005
Project Number: |  |  | DN1210-SP2 | [5 empty] | ITP Status: |  |  | IFC
ITP Description: |  |  | Northern Access Road Water main sleeve | [5 empty] | Revision: | 1000 |  | 2
Contract Number: |  |  | NZTA 8287 | [5 empty] | Drawing Sets: |  |  | 232735.02-WSP-DR-WAT (03,10,11,112,209,214,219,312,320)
Customer: |  |  | Waka Kotahi | [5 empty] | Specification: |  |  | Project specification - Section 22.1 to Section 22.5
Quality Specified: |  |  | ISO9001:2015
Review / Update History | [10 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  |  | Revision Details: |  |  |  | Activity Key |  |  | Responsibilities Key
0 | Draft for Approval | 20/02/2025 |  | Cordelia Girdler-Brown & Nick Adams |  |  | As per the Email on 25/02/2025: a. 3.1.1 ENG hold point changed to SE hold point b. 3.5.2 Added material delivery hold point c. Change section 4.2 from butt welding EF welding d. Added section 3.4.2 for EF coupler testing |  |  |  | A | Action |  | ENG | Engineer / Engineer's Rep
[11 empty] | B | Report by Breach |  | CR | Customer Rep
[11 empty] | C | Check |  | PD | Project Director
[11 empty] | D | Dimension Inspection |  | PM | Project Manager
[11 empty] | E | Examine |  | OP | Operations Manager
[11 empty] | HP | Hold Point (Engineer) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) |  | HSE | HSE Manager / Rep
1 | Draft for Approval | 2025-03-03 |  | Cordelia Girdler-Brown & Nick Adams |  |  | Section 3.3 ITP material change from AP20 to 19mm chip |  |  |  | H | Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) |  | QM | QA Manager / Rep
[11 empty] | I | Inspection (Formal inspection activity to be undertaken and recorded) |  | PE | Project Engineer
2 | Draft for Approval | 2025-07-03 |  | Cordelia Girdler-Brown & Nick Adams | [6 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[11 empty] | O | Operation |  | QE | Quality Engineer
[11 empty] | R | Review |  | SUP | Superintendent / Supervisor
[11 empty] | S | Subcontractor |  | SV | Surveyor
[11 empty] | V | Visual Verification |  | TPI | Third Party Inspector
[11 empty] | W | Witness Point (Review of text reports/records or other evidence of compliance) |  | SPEC | Specialist
SECTION 2A – ITP Approval | [8 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  |  | Date: | Position |  | Name: |  | Signature: |  |  | Date:
Downer PM |  | Nick Adams | [6 empty] | Downer PM |  | Nick Adams
Downer QM |  | CORDELIA GIRDLER-BROWN | [6 empty] | Downer QM |  | CORDELIA GIRDLER-BROWN
Client (If Applicable) | [8 empty] | Client (If Applicable)

## ITP Master Body
Northern Access road watermain sleeve Inspection and test plan
Tauriko Enabling Works - SP2
DN1210-SP2-ITP011.005 - REV0
Item No. | Inspection and Test Point | Detail / Activity | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Testing Quantity Required (based from schedule qtys) | Verification Activity |  | Downer Conformance of Compliance Signoff
[7 empty] | Activity | By | ConQA Signature | Date | Comments / Closeout Details | ENGINEERS COMMENTS - Date: | DOWNER RESPONSE - Date:
SECTION 3 – PRE-CONSTRUCTION - MATERIAL, PERSONEL & THIRD PARY APPROVALS
3.1 | GENERAL
3.1.1 | Extent of Line Setout | Ensure line and level of watermain sleeve has been marked out and agreed with Engineer in accordance with water RM drawings. Identify any clashes before construction. LOT- markup | As Per Drawings & Markup drawing | Design Drawings | ITP Sign Off / Mark-up | Prior to Construction & Every Revision of IFC Drawings/Data. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  | 3.1.1. can be an internal hold point (H) | Changes made
3.2 | MATERIAL TESTING- AP65
3.2.1 | Material grading: Materials (Gap65/AP65) | NZS4407:2015, Test 3.8.1 - Particle Size Distribution | No Particles >200mm Maximum fines 10% passing 75micron sieve | PS 22.13.1 Appendix XVIII PS 16.5.5 Appendix V | Lab Test Report NZS 4407.3.8.1 | Stockpile Size (m3): 0-400 - 2 tests 400-1,500 - 3 tests 1,500-4,000 - 4 tests >4,000 - 1 test for each additional 1,000m3 Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.2.2 | Weathering index: Materials (Gap65/AP65) | NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate | AA, AB, AC, BA, BB, or CA | Appendix XVIII PS 16.5.5 Appendix V | IANZ Accredited Report | 2 Tests Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.2.3 | Crushing Resistance: Materials (Gap65/AP65) | NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load | >100KN | Appendix XVIII Appendix V | IANZ Accredited Report | 2 Tests Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.2.4 | Maximum Dry Density and Optimum Water Content | NZS4402:1986, Test 4.1.2 - Heavy Compaction Test | Report Value Only | Appendix XVIII Appendix V | IANZ Accredited Report | 1 Test Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.3 | MATERIAL TESTING- 19mm chip
3.3.1 | Material grading: | Bedding/Side Zone/ Overlay Zone/Embedment Zone | Sieve Size % Passing 19.0mm 85-100% passing 9.5mm 25-55% passing 4.75mm 0-10% passing 2.36mm 0-5% passing 0.075mm 0-2% passing | AS/NZS 2566.2 PS 22.4.5 | Lab Test Report NZS 4407.2015 Test3.8.1 | 0-400m3 2 Test 400-1500m3 3 Test 1500-4000m3 4 Test >4000 1 Test Additional 1000m3 | HP | ENG
3.3.4 | Geotextile/Geogrid | Minimum Strength Class C & Filter Class 1 or TNZ F/7geotextile is to be used in Trench Backfill of Drainage pipe in Wet conditions. | Engineers Site Representative to inspect trench. | PS-16.5.7 | Certification | 1 time | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.4 | MATERIAL TESTING
3.4.1 | Pipes (Sleeve) | Manufacturer's record and location of extrusion plants. Name of the proposed PE resin, the manufacturer, production information on the properties of resin. Full Traceability information and certification of analysis for the resin batch. | Engineer Approval | PS-22.4.1 (d) | Full Traceability information and certification of Material and resin. Delivery Dockets | Prior to Procurement | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.4.2 | Electrofusion (EF) coupler | Confirm the diameter and size and the EF coupler | Engineer Approval | PS- 22.9.5 | Manufucture records | Prior to Procurement | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.5 | MATERIAL DELIVERY
3.5.1 | Pipe and fittings. DN560 PE100 SDR 11 | Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | As Per Drawings | Design Drawings | Delivery Dockets / Inspection Checksheet (DG-QA-TP019) | Each Delivery to site | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.5.2 | Material delivery | Embedment and beckfill | Embedment and beckfill | Design Drawings | Delivey dockets | Each Delivery to site | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  | 3.5. Material Delivery section to also include delivery of the various backfill materials requiring delivery dockets as records. | Changes made
SECTION 4 – CONSTRUCTION ACTIVITY
4.1 | Watermains Sleeve
4.1.1 | Foundation Compliance | On Granular or Cohesive Material | Granular Material: Scala 3 blows/100mm (Or) Cohesive Material: Vane Shear Strength 70kPa | PS 21.6.5 and AS/NZS 2566.2 | Scala/Shear test result | One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. | W Review of text reports/records or other evidence of compliance | SE
4.1.2 | Undercut approval | Trench Foundation | 300mm Max cut IFC Drawing Sheet 320 (Or) Engineers approval | IFC Drawing WAT 0320. AS/NZS 2566.2/2002 | Lab Test Report / Watermainline record | If Undercut required | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.1.3 | Undercut Backfill Compliance | On Granular Material / On each layer as per specification / on the trench foundation. | Visiual Inspection | IFC Drawing WAT 0320 | Lab Test Report / Watermainline record | Every Undercut | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.1.4 | Bedding Zone Compaction Testing (PE Pipe). | On Granular Material / On each layer as per specification (19mm chip) NDM testing as per NZS4407:2015, Test 4.3 | Bedding Zone: 150mm minimum thickness (compacted) over the bottom of the trench. Minimum Compaction- 85% MDD | IFC Drawing 0320-1 AS/NZS 2566.2/2002 | NDM:Lab Test Report | As per Water Specification. One test per 20m evenly spaced intervals. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.1.5 | Laying of Pipes | Lay in straight lines, beginning at the lower end of the line. Lay all pipe with manufacturing codes and class markings facing upwards. | As Per Drawings. Facing upwards | PS22.7.1 C | Visual Inspection / Watermain line record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.2 | Electrofusion Welding
4.2.2 | Electrofusion (EF) Welding | Required if Butt fusion welding cannot be perform. EF Jointing in accordance with PIPA POP 001. The lead welder or welding supervisor must verify on the site record form. | WMS Report Checklist (refer to CWP). | PS 22.9.5 Appendix 22 | Visual Inspection / Electrofusion (EF) welding record checklist. WMS Report | Every Welding Point | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.2.3 | Electrofusion (EF) construction weld test | EF weld quality to be maintained. | EF coupler and EF saddle testing | PS- 22.9.6 (b) (iv) | Test report | 1 in 10 test | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
4.2.4 | Survey | Inspection of Pipeline Inverts | Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance | PS- 21.7.6 Table 21.15 | Survey Data / As-built record | Pipeline invert to be surveyed at chainages as indicated in the drawings. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.3 | WATERMAIN - Backfill
4.3.1 | Emebment Zone - (Side Haunch Overlay ) | 19mm chip backfill Compacted in 200mm Layers. NDM/CleggTesting to be completed on maximum 200mm lifts of overlays . NDM BS to be Carried Out | in 200mm layers. More than 85% of MDD. | NZS 4407:2015 Test 4.3 Nuclear Moisture Density Gauge; BS | Lab Report / Watermainline record | One test per 20m evenly spaced intervals. 200mm lift | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.3.2 | Pipe Markers | Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings. Mark fire hydrant positions in accordance with SNZ PAS 4509 | AS Per Drawings. | PS 22.7.3 a | Visual Inspection / Watermainline record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.3.3 | Backfill Compaction Testing | GAP65/AP65/LRAP65 Backfill Compacted in 200mm Layers. NDM Testing to be completed on maximum 200mm lifts of backfill. | GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill. LRAP65- achive 90% NDM on Grassed Area and 95% NDM on Shared and Carriageway. OR Clegg 28CIV | PS- 22.13.5 NDM Standerd 25832 NZS 4402 Test 4.1.3 | Lab Report / Watermainline record | As per 200mm lift One test per 20m evenly spaced intervals. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.4 | WATERMAIN Sleeve- Inspection
4.4.1 | Watermain sleeve inspection - Pipe Inspection | Inspection of Watermain sleeve | Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness | Internal | Watermain line record | Continious 1 per Line | I Formal inspection activity to be undertaken and recorded. | SE
SECTION 5– POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - ACCEPTANCE BEFORE COMMENCING DISINFECTION WORK
5.1 | Survey As-Builts | Quality Check on sleeve based on the tolerances in RITS | Meets spec as per drawings and capture any NCR or change to design. | Project Specifications | CAD File as per PS12.3 and Red pen markup only | Post works completion of a lot | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE