## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DN1210-SP2-011-003 ITP Northern access road Watermain | itp |  |  |  |  | DN1210-SP2-011-003 ITP Northern access road Watermain Rev 1
section | 3.0 - PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS - ALL TESTS TO BE NO OLDER THAN 3 MONTHS
checkpoint | 3.1 - Extent of Line Setout
label | Detail / Activity - Ensure line and level of Watermain has been marked out and agreed with Engineer in accordance with Watermain drawings.
label | ○ Identify any clashes before construction.
label | ○ LOT- markup
label | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
label | Standard / Specification - Design Drawings
label | Verifying Document - ITP Sign Off / Mark-up
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Pipe Laying
label | Detail / Activity - Method statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - PS- 22.3 Appendix V
label | Verifying Document - Watermain Construction Work Pack Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Pipeline Pressure Testing
label | Detail / Activity - Method statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - PS- 22.3, PS 22.7.12, Appendix V, Appendix XXI
label | Verifying Document - Watermain Pipeline Pressure Testing Work Pack Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4 - EF Pre Construction Weld Tests (if required)
label | Detail / Activity - Passing result in accordance with ISO21751 (strip bend test) tested by an IANZ accredited laboratory).
label | ○ There should be no EF weld test without prior approval from TCC.
label | Acceptance / Conformance Criteria - Passing result in accordance with ISO21751 (strip bend test) tested by an IANZ accredited laboratory.
label | ○ TCC Approval Prior to Works
label | Standard / Specification - ISO21751, TCC IDC DS-7.6.4.b.ii, PS-22.9.6
label | Verifying Document - Laboratory Test Report
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5 - Butt-Fusion pre construction weld test
label | Detail / Activity - One weld on the most common size of pipes used for the project.
label | ○ One weld on the thickest wall (highest PN) pipe
label | Acceptance / Conformance Criteria - Test to be down in accordance of ISO 13953 for tensile strength and failure mode.
label | ○ WMS Report
label | Standard / Specification - PS 22.9.6 (a), ISO 13953 Standard
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.6 - Material grading: Materials (Gap65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
label | Acceptance / Conformance Criteria - No Particles >200mm
label | ○ Maximum fines 10% passing 75micron sieve
label | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
label | Verifying Document - Lab Test Report NZS 4407.3.8.1
label | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
label | ○ 0-400 - 2 tests
label | ○ 400-1,500 - 3 tests
label | ○ 1,500-4,000 - 4 tests
label | ○ >4,000 - 1 test for each additional 1,000m3
label | — Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.7 - Weathering index: Materials (Gap65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
label | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
label | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V NZS4407:2015 Test 3.11
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.8 - Crushing Resistance: Materials (Gap65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
label | Acceptance / Conformance Criteria - >100KN
label | Standard / Specification - Appendix XVIII, Appendix V NZS4407:2015 Test 3.10
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.9 - Maximum Dry Density and Optimum Water Content
label | Detail / Activity - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
label | Acceptance / Conformance Criteria - Report Value Only
label | Standard / Specification - Appendix XVIII, Appendix V NZS4402:1986 Test 4.1.2
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.10 - Material grading: Materials (GAP20/19mm chip/Sand SAP7)
label | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
label | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
label | 19.0mm ¦¦ 85-100% passing
label | 9.5mm ¦¦ 25-55% passing
label | 4.75mm ¦¦ 0-10% passing
label | 2.36mm ¦¦ 0-5% passing
label | 0.075mm ¦¦ 0-2% passing
label | Standard / Specification - AS/NZS 2566.2, PS 22.4.5
label | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
label | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
label | 400-1500m3 ¦¦ 3 Test
label | 1500-4000m3 ¦¦ 4 Test
label | >4000 ¦¦ 1 Test Additional 1000m3
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.11 - Soaked CBR
label | Detail / Activity - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
label | Acceptance / Conformance Criteria - >80%
label | Standard / Specification - Project Specifications 20.9 TCC-IDC IT-4.8 table 4.6
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - IANZ Accredited Report
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.12 - Pipes (DN315 PE100 PN16)
label | Detail / Activity - Manufacturer's record and location of extrusion plants.
label | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
label | ○ Full Traceability information and certification of analysis for the resin batch.
label | Acceptance / Conformance Criteria - Full Traceability information and certification of Material and resin.
label | Standard / Specification - PS-22.4.1 (d)
label | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.13 - Valves, Adaptors, Flanges and Fittings
label | Detail / Activity - Have a pressure rating no less than the designed pressure.
label | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
label | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
label | Acceptance / Conformance Criteria - Engineer approval AS/NZS 4129
label | Standard / Specification - PS-22.4.2
label | Verifying Document - Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.14 - Fusion Joint Compatibility
label | Detail / Activity - Confirm pipe and fittings compatibility for fusion welding
label | Acceptance / Conformance Criteria - No defects, compatible resin types per NZS/AS 2033
label | Standard / Specification - NZS/AS 2033:1980, Clause 4.2
label | Verifying Document - Test Report
label | Testing Quantity Required (based from schedule qtys) - 1 per material type
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - ENG
checkpoint | 3.15 - Pipe and fittings.
label | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Standard / Specification - Design Drawings
label | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.16 - Valves, Adaptors, Flanges, Caps and Fittings
label | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
label | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
label | Standard / Specification - PS-22.4.2
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.17 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65)
label | Detail / Activity - Confirm Specification and material in good condition.
label | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
label | Standard / Specification - PS-22.4.1
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.18 - Bidim/Geogrid
label | Detail / Activity - BIDIM A29 Durogrid 30/30 or similar.
label | Acceptance / Conformance Criteria - Site Engineer Approval
label | Standard / Specification - PS-22.4.1
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.19 - Pre-cast Manholes
label | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Standard / Specification - Design Drawings
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.2 - KWIK Spacers
label | Detail / Activity - Placing spacers on DN315 pipe when being inserted into DN560 sleeve
label | Acceptance / Conformance Criteria - Model: HDXT43 (43mm). 1.5m spacing
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT) Sheet 0312
label | Verifying Document - Visual Insepction, Photographs
label | Testing Quantity Required (based from schedule qtys) - Pipe under NAR
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded
label | Verification Activity: By - PE/SE
section | 4.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE INSTALLATION - Excavation and Laying
checkpoint | 4.1 - Foundation Compliance
label | Detail / Activity - On Granular or Cohesive Material
label | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
label | (Or)
label | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
label | Standard / Specification - Appendix V Table 21:11
label | Verifying Document - Scala/Shear test result
label | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
label | Verification Activity: Activity - W
label | ○ Review of text reports/records or other evidence of compliance
label | Verification Activity: By - SE
checkpoint | 4.2 - Undercut approval
label | Detail / Activity - Trench Foundation (subgrade)
label | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
label | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
label | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
label | Standard / Specification - PS-21.6.5 Table 21.5
label | Verifying Document - Lab Test Report / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - If Undercut required
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.3 - Undercut Backfill Compliance
label | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
label | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
label | OR
label | ○ Clegg 25% CIV
label | Standard / Specification - PS- 16.5.12
label | Verifying Document - Lab Test Report / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Every Undercut
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.4 - Bedding Zone Compaction Testing
label | Detail / Activity - On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip)
label | Acceptance / Conformance Criteria - Bedding Zone:
label | ○ 100mm minimum thickness (compacted) over the bottom of the trench.
label | ○ Minimum Compaction- 85%MDD
label | ○ Paeangaroa Sand - 9 average CIV, 7% min CIV
label | ○ Wilson No.2 Sand - 4% CIV
label | Standard / Specification - IFC Drawing 0320-1, AS/NZS 2566.2/2002 Appendix XVIII Site Instruction
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - As per WM Specification. One test per 20m evenly spaced intervals.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.5 - Laying of Pipes (DN315 PE Pipe)
label | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
label | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
label | Acceptance / Conformance Criteria - As Per Drawings.
label | ○ Facing upwards
label | Standard / Specification - PS22.7.1 C
label | Verifying Document - Visual Inspection / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.6 - Compaction of Pipe Embedment Material
label | Detail / Activity - Compact embedment to required density
label | Acceptance / Conformance Criteria - Achieves 85% MDD, as per project drawings SHEET 0320
label | Standard / Specification - Project Specification 22.13.1
label | Verifying Document - BACKFILL Check Sheet
label | Testing Quantity Required (based from schedule qtys) - Every 20m, 200mm lift
label | Verification Activity: Activity - W
label | ○ Review of text reports/records or other evidence of compliance
label | Verification Activity: By - ENG
checkpoint | 4.7 - Cold Bending of Pipe
label | Detail / Activity - Verify minimum bend radius
label | Acceptance / Conformance Criteria - Min bend radius 50x pipe diameter (31.5m)
label | Standard / Specification - Contract Specification 21.6.6
label | Verifying Document - Survey As-Built Records
label | Testing Quantity Required (based from schedule qtys) - Every cold bend
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded
label | Verification Activity: By - ENG
checkpoint | 4.8 - Pipe Installation on Curved Alignments
label | Detail / Activity - All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
label | Acceptance / Conformance Criteria - AS Per POP 202
label | Standard / Specification - PS 22.7.1 D
label | Verifying Document - Visual Inspection / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - M
label | ○ Monitor on Random Basis
label | Verification Activity: By - SE
checkpoint | 4.9 - Tracer Wire Installation
label | Detail / Activity - Install tracer wire along pipe
label | Acceptance / Conformance Criteria - 4mm² multi-strand polythene sleeved copper cable, strapped every 3m with slack
label | Standard / Specification - Project Specification 22.7.3
label | Verifying Document - BACKFILL Check Sheet
label | Testing Quantity Required (based from schedule qtys) - Every 20m
label | Verification Activity: Activity - R
label | ○ Review
label | Verification Activity: By - ENG
checkpoint | 4.10 - Northen Access Pipe Caping
label | Detail / Activity - PETROLATUM WRAP SYSTEM
label | Acceptance / Conformance Criteria - IN ACCORDANCE WITH PROJECT SPECIFICATION as per sheet 0307
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
label | Verifying Document - Photographic Evidence
label | Testing Quantity Required (based from schedule qtys) - Pipe end
label | Verification Activity: Activity - W
label | ○ Review of text reports/records or other evidence of compliance
label | Verification Activity: By - ENG
checkpoint | 4.11 - Northen Access Pipe Caping
label | Detail / Activity - STUB FLANGE AND GALVANISED BACKING RING (PN16)
label | Acceptance / Conformance Criteria - IN ACCORDANCE WITH PROJECT SPECIFICATION as per sheet 0305
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
label | Verifying Document - Photographic Evidence
label | Testing Quantity Required (based from schedule qtys) - Pipe end
label | Verification Activity: Activity - W
label | ○ Review of text reports/records or other evidence of compliance
label | Verification Activity: By - ENG
checkpoint | 4.12 - DN315 SLEEVED ROAD CROSSING (Sleeve is already installed only pulling DN315 through)
label | Detail / Activity - THE OUTER ENDS OF THE SLEEVE ARE TO BE FILLED AND SEALED WITH EXPANDING 'PU' FOAM. ANNULUS TO BE GROUTED AFTER INSTALLATION.
label | Acceptance / Conformance Criteria - REFER TO SHEET No's 312
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
label | Verifying Document - Photographic Evidence
label | Testing Quantity Required (based from schedule qtys) - PIPE SLEEVE ENDS
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded
label | Verification Activity: By - ENG
section | 5.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Joint and Connection
checkpoint | 5.1 - Flanges
label | Detail / Activity - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
label | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
label | Standard / Specification - PS 22.7.5 Appendix XXII
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - First flanged joint
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Bends
label | Detail / Activity - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings or approcval from engineer.
label | ○ Fitting must meets the same PN rating as the adjacent PE 100.
label | ○ Fittings must be suitable for producing the joints shown on the Drawings.
label | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
label | Standard / Specification - PS 22.4.2 Appendix XXII
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - Project Drawings (232735.02-WSP-DR-WAT SHEET)
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE/ENG
section | 6.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Butt-Fusion Welding
checkpoint | 6.1 - Butt-Fusion Welding
label | Detail / Activity - Use only semi-automatic or automatic welding machines.
label | ○ Maintain a site record for all butt-fusion welds.
label | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
label | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
label | ○ WMS Report
label | Standard / Specification - Appendix XXII PS 22.9.4 C
label | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report
label | Testing Quantity Required (based from schedule qtys) - Every Welding Point
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.2 - Butt-Fusion Construction Weld Test
label | Detail / Activity - Test at least two welds from the first 50 welds.
label | ○ One of the welds to be selected by the Engineer for satisfactory result.
label | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
label | ○ 95% tensile strength; welds aligned
label | Standard / Specification - PS- 22.9.6 (a) (iv)
label | Verifying Document - Test report
label | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.3 - Survey
label | Detail / Activity - Inspection of Pipeline Inverts
label | Acceptance / Conformance Criteria - Vertical design Setout:
label | ○ Pipes ≤ 1% grade: +/- 10mm variance
label | ○ Pipes > 1% grade: +/- 20mm variance
label | Horizontal design Setout:
label | ○ +/-30mm variance
label | Standard / Specification - PS- 21.7.6 Table 21.15
label | Verifying Document - Survey Data / As-built record
label | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 6.4 - Photograph of Each Weld
label | Detail / Activity - Take sharply focused photo while clamped
label | Acceptance / Conformance Criteria - Unique weld identifier visible
label | Standard / Specification - N/A
label | Verifying Document - Weld Records; Photos
label | Testing Quantity Required (based from schedule qtys) - Each weld
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded
label | Verification Activity: By - SUB
checkpoint | 6.5 - Weld Treatment for Corrosion Resistance
label | Detail / Activity - Treat welded areas to restore corrosion resistance
label | Acceptance / Conformance Criteria - Treated weld areas
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
label | Verifying Document - QA Documents from Welders
label | Testing Quantity Required (based from schedule qtys) - Each weld
label | Verification Activity: Activity - W
label | ○ Review of text reports/records or other evidence of compliance
label | Verification Activity: By - ENG
section | 7.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Backfill
checkpoint | 7.1 - Emebment Zone - (Side Haunch Overlay )
label | Detail / Activity - Granular Sand backfill Compacted in 200mm Layers.
label | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays.
label | ○ NDM BS to be Carried Out
label | Acceptance / Conformance Criteria - in 200mm layers.
label | ○ More than 85% of MDD
label | ○ Paeangaroa Sand - 9 average CIV, 7% min CIV
label | ○ Wilson No.2 Sand - 4% CIV
label | Standard / Specification - Project Drawing 0320 Site Instruction
label | Verifying Document - Lab Report / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals. 200mm lift
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 7.2 - Pipe Markers
label | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
label | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
label | Acceptance / Conformance Criteria - AS Per Drawings.
label | Standard / Specification - PS 22.7.3 a
label | Verifying Document - Visual Inspection / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 7.3 - Backfill Compaction Testing
label | Detail / Activity - GAP65/AP65 Backfill Compacted in 200mm Layers.
label | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
label | Acceptance / Conformance Criteria - GAP65/AP65or site won material Backfill Compacted in 200mm layers.
label | ○ Testing to be completed on maximum 200mm lifts of backfill.
label | ○ 95% NDM on Shared and Carriageway.
label | OR
label | ○ 28% CIV
label | ○ For site won min >60kpa
label | ○ Ave > 80kpa
label | Standard / Specification - PS- 22.13.5, NDM Standerd 25832, NZS 4402 Test 4.1.3, IFC Drawing 0320-1
label | Verifying Document - Lab Report / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - As per WM Specification. One test per 20m evenly spaced intervals.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | 8.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Inspection
checkpoint | 8.1 - Pipe Inspection
label | Detail / Activity - Inspection of Drainage line
label | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
label | Standard / Specification - Internal
label | Verifying Document - Watermain line record
label | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded
label | Verification Activity: By - SE
section | 9.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE TESTING
checkpoint | 9.1 - Pressure Acceptance Testing
label | Detail / Activity - Backfill/cover with embedment before testing
label | ○ End caps in place, provision for filling the pipeline and bleeding air.
label | Acceptance / Conformance Criteria - Potable Watermain Pipelines – 1250kPa
label | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
label | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b)
label | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
label | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9.2 - Swab New PE Watermain
label | Detail / Activity - Swab to remove debris and air
label | Acceptance / Conformance Criteria - Water running clear & removed entrapped air
label | Standard / Specification - TCC IDC TS-7
label | Verifying Document - Swabbing Check Sheet
label | Testing Quantity Required (based from schedule qtys) - All new pipe installed
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SUP/SE
checkpoint | 9.3 - Pressure Test New PE Watermain
label | Detail / Activity - Conduct pressure test. Due to not commissioning the pipe until later in the project, CB will complete our own pressure testing upon installation of the pipe, with the full pressure testing and chlorination to be completed once the pipe is ready to be commissioned.
label | Acceptance / Conformance Criteria - No leaks, no failure of any pipe, fitting or other pipeline component.
label | Standard / Specification - TCC IDC TS-7.1c Pressure Rebound Test Method; TS-7.1a Constant Pressure Test Method
label | Verifying Document - TS-7.1a/c Pressure Test Method (Test Report)
label | Testing Quantity Required (based from schedule qtys) - All new pipe installed & swabbing passed
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SUP/SE
checkpoint | 9.4 - Chlorinate New PE Watermain
label | Detail / Activity - Chlorinate watermain
label | Acceptance / Conformance Criteria - 5+ pH on chlorine tester
label | Standard / Specification - TCC IDC IT-7.4.1 Disinfection Procedure
label | Verifying Document - Picture; Signed Chlorination Check Sheet
label | Testing Quantity Required (based from schedule qtys) - All new pipe installed & pressure test passed
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SUP/SE
checkpoint | 9.5 - E. Coli Test New PE Watermain
label | Detail / Activity - Test for bacterial contamination
label | Acceptance / Conformance Criteria - <1 E. coli; <1 Coliforms
label | Standard / Specification - TCC IDC IT-7.5 E. coli Sampling
label | Verifying Document - E. coli Test Report
label | Testing Quantity Required (based from schedule qtys) - All new pipe installed & chlorine test passed
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SUP/SE
section | 10.0 - CONSTRUCTION ACTIVITY - WATERMAIN Manhole installation
checkpoint | 10.1 - Foundation Compliance
label | Detail / Activity - On Granular or Cohesive Material
label | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
label | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
label | Standard / Specification - Appendix V Table 21:11
label | Verifying Document - Shear vane or Scala test result
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - W
label | ○ Review of text reports/records or other evidence of compliance
label | Verification Activity: By - SE
checkpoint | 10.2 - Undercut approval
label | Detail / Activity - On Subgrade
label | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
label | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
label | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
label | Standard / Specification - Table 21.5
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - If Undercut required
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10.3 - Undercut Backfill Compliance AP65
label | Detail / Activity - On Granular Material
label | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
label | OR
label | ○ Clegg 25% CIV
label | Standard / Specification - PS- 16.5.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 10.4 - Bedding Compaction Testing Sand/AP65
label | Detail / Activity - On Granular Material
label | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
label | OR
label | ○ Clegg 25% CIV
label | ○ Paeangaroa Sand - 9 average CIV, 7% min CIV
label | ○ Wilson No.2 Sand - 4% CIV
label | Standard / Specification - PS- 16.5.12, PS- 21.6.11
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 10.5 - Survey
label | Detail / Activity - Inspection of Structure
label | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
label | Standard / Specification - PS- 21.7.6
label | Verifying Document - Survey Data
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SV
checkpoint | 10.6 - Sidefill Compaction Testing
label | Detail / Activity - From the bedding layer to the overlay layer of pipe.
label | Acceptance / Conformance Criteria - AP20/GAP20
label | ○ Testing to be completed on maximum 200mm lifts of backfill - 85% MDD
label | ○ AP20/19mm chip
label | Standard / Specification - PS- Table 21.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 10.7 - Backfill Compaction Testing
label | Detail / Activity - From Overlay layer to the subgrade layer
label | Acceptance / Conformance Criteria - AP65
label | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
label | ○ AP65-Clegg28%CIV
label | Standard / Specification - PS- 16.5.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 10.8 - Manhole
label | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Standard / Specification - Design Drawings
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 10.9 - MH joints inspection
label | Detail / Activity - Inspection of joints
label | Acceptance / Conformance Criteria - Right joint type used, no visual leak or breakage
label | Standard / Specification - PS 22.7.10
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10.10 - Inspection
label | Detail / Activity - Inspection of Structure
label | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
label | Standard / Specification - PS- 21.6.11
label | Verifying Document - Manhole Record
label | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole/catchpit
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded
label | Verification Activity: By - SE
checkpoint | 10.11 - Plumb
label | Detail / Activity - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
label | Acceptance / Conformance Criteria - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
label | Standard / Specification - PS-22.7.10
label | Verifying Document - Survey Data
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SV
checkpoint | 10.12 - Step Rungs
label | Detail / Activity - Step rungs evenly spaced at nominal 300mm vertical intervals
label | Acceptance / Conformance Criteria - Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover
label | Standard / Specification - PS-22.7.11
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | 11.0 - CONSTRUCTION ACTIVITY - AIR VALVES
checkpoint | 11.1 - Installation of Isolation Valve
label | Detail / Activity - Verify installation per manufacturer’s instructions
label | Acceptance / Conformance Criteria - Installed as per manufacturer’s instructions. Project Specifications
label | Standard / Specification - PS-22.4.2 Project Drawings (232735.02-WSP-DR-WAT SHEET 0314 to 0316)
label | Verifying Document - Air Valve & Isolation Valve Check Sheet
label | Testing Quantity Required (based from schedule qtys) - Each isolation valve
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded
label | Verification Activity: By - ENG
checkpoint | 11.2 - Installation of Air Valve
label | Detail / Activity - Verify installation per manufacturer’s instructions
label | Acceptance / Conformance Criteria - Installed as per manufacturer’s instructions
label | Standard / Specification - PS-22.4.2 Project Drawings (232735.02-WSP-DR-WAT SHEET 0314 to 0316)
label | Verifying Document - Air Valve & Isolation Valve Check Sheet
label | Testing Quantity Required (based from schedule qtys) - Each air valve
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded
label | Verification Activity: By - ENG
checkpoint | 11.3 - Backfill Compaction Testing
label | Detail / Activity - From Overlay layer to the subgrade layer
label | Acceptance / Conformance Criteria - AP65
label | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
label | ○ AP65-Clegg28%CIV
label | Standard / Specification - PS- 16.5.12, PS- 22.13.5, NDM Standerd 25832, NZS 4402 Test 4.1.3, IFC Drawing 0320-1
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | 12.0 - CONSTRUCTION ACTIVITY - FIRE HYDRANTS
checkpoint | 12.1 - Chamber Location
label | Detail / Activity - Location of hydrants and air valve chambers are to be confirmed on site with the TCC Engineer and offset as far back off the seal as possible.
label | Acceptance / Conformance Criteria - Engineer to confirm onsite location
label | ○ TCC Engineer approval
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT SHEET 0322)
label | Verifying Document - PS-22.5.11 TCC sign-off
label | Testing Quantity Required (based from schedule qtys) - Checksheet
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 12.2 - Hydrant Surround Blocks, Height to Suit
label | Detail / Activity - Hydrant box with 150 x 150mm concrete surround to be finished flush with surrounding ground.
label | Acceptance / Conformance Criteria - 232735.02-WSP-DR-WAT Typical FH SHEET 0322
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT SHEET 0322)
label | Verifying Document - PS-22.5.11 Checksheet
label | Testing Quantity Required (based from schedule qtys) - Supervisor to check. Checksheet
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded
label | Verification Activity: By - ENG
checkpoint | 12.3 - Install Ductile Iron FH
label | Detail / Activity - Heavy duty valve box installed as per TCC's Code of Practice
label | Acceptance / Conformance Criteria - Contractor to ensure flange drilling on DN80 end of reducer matches flange drilling on DN80 hydrant riser
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT SHEET 0322)
label | Verifying Document - PS-22.5.11 Checksheet
label | Testing Quantity Required (based from schedule qtys) - Checksheet
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded
label | Verification Activity: By - ENG
checkpoint | 12.4 - Concrete Pedestal on Offset Bend
label | Detail / Activity - 3mm rubber seat between bend and pedestal 25MPa concrete pedestal
label | Acceptance / Conformance Criteria - Typical FH sheet 0322
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT SHEET 0321 to 0322)
label | Verifying Document - PS-22.5.11 Checksheet
label | Testing Quantity Required (based from schedule qtys) - Per offset
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded
label | Verification Activity: By - ENG
checkpoint | 12.5 - Anchor block and to extend past edge of concrete
label | Detail / Activity - DN315 - Type 1 Anchor 2000(L) x 600(W) x 2500mm deep concrete anchor block
label | Acceptance / Conformance Criteria - In accordance with project specification as per sheet 0307
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT SHEET 0321)
label | Verifying Document - Engineer Approval
label | Testing Quantity Required (based from schedule qtys) - SH29/Northen Access Rd intersection
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
section | 13.0 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
checkpoint | 13.1 - Survey As-Builts
label | Detail / Activity - Quality Check on Nee pipeline and structure based on the tolerances in RITS
label | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
label | Standard / Specification - Project Specifications
label | Verifying Document - Red pen markup only
label | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature
checklist | DN1210-SP2-011-005 ITP Northern access road Watermain sleeve | itp |  |  |  |  | DN1210-SP2-011-005 ITP Northern access road Watermain sleeve Rev 2
section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL, PERSONEL & THIRD PARY APPROVALS
checkpoint | 3.1.1 - Extent of Line Setout
label | Detail / Activity - Ensure line and level of watermain sleeve has been marked out and agreed with Engineer in accordance with water RM drawings.
label | ○ Identify any clashes before construction.
label | ○ LOT- markup
label | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
label | Standard / Specification - Design Drawings
label | Verifying Document - ITP Sign Off / Mark-up
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 3.2.1 - Material grading: Materials (Gap65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
label | Acceptance / Conformance Criteria - No Particles >200mm
label | ○ Maximum fines 10% passing 75micron sieve
label | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
label | Verifying Document - Lab Test Report NZS 4407.3.8.1
label | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
label | ○ 0-400 - 2 tests
label | ○ 400-1,500 - 3 tests
label | ○ 1,500-4,000 - 4 tests
label | ○ >4,000 - 1 test for each additional 1,000m3
label | — Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2.2 - Weathering index: Materials (Gap65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
label | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
label | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2.3 - Crushing Resistance: Materials (Gap65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
label | Acceptance / Conformance Criteria - >100KN
label | Standard / Specification - Appendix XVIII, Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2.4 - Maximum Dry Density and Optimum Water Content
label | Detail / Activity - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
label | Acceptance / Conformance Criteria - Report Value Only
label | Standard / Specification - Appendix XVIII, Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3.1 - Material grading:
label | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
label | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
label | 19.0mm ¦¦ 85-100% passing
label | 9.5mm ¦¦ 25-55% passing
label | 4.75mm ¦¦ 0-10% passing
label | 2.36mm ¦¦ 0-5% passing
label | 0.075mm ¦¦ 0-2% passing
label | Standard / Specification - AS/NZS 2566.2, PS 22.4.5
label | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
label | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
label | 400-1500m3 ¦¦ 3 Test
label | 1500-4000m3 ¦¦ 4 Test
label | >4000 ¦¦ 1 Test Additional 1000m3
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3.4 - Geotextile/Geogrid
label | Detail / Activity - Minimum Strength Class C & Filter Class 1 or TNZ F/7geotextile is to be used in Trench Backfill of Drainage pipe in Wet conditions.
label | Acceptance / Conformance Criteria - Engineers Site Representative to inspect trench.
label | Standard / Specification - PS-16.5.7
label | Verifying Document - Certification
label | Testing Quantity Required (based from schedule qtys) - 1 time
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4.1 - Pipes (Sleeve)
label | Detail / Activity - Manufacturer's record and location of extrusion plants.
label | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
label | ○ Full Traceability information and certification of analysis for the resin batch.
label | Acceptance / Conformance Criteria - Engineer Approval
label | Standard / Specification - PS-22.4.1 (d)
label | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4.2 - Electrofusion (EF) coupler
label | Detail / Activity - Confirm the diameter and size and the EF coupler
label | Acceptance / Conformance Criteria - Engineer Approval
label | Standard / Specification - PS- 22.9.5
label | Verifying Document - Manufucture records
label | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5.1 - Pipe and fittings DN560 PE100 SDR 11
label | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Acceptance / Conformance Criteria - As Per Drawings
label | Standard / Specification - Design Drawings
label | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 3.5.2 - Material delivery
label | Detail / Activity - Embedment and beckfill
label | Acceptance / Conformance Criteria - Embedment and beckfill
label | Standard / Specification - Design Drawings
label | Verifying Document - Delivey dockets
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | SECTION 4 – CONSTRUCTION ACTIVITY
checkpoint | 4.1.1 - Foundation Compliance
label | Detail / Activity - On Granular or Cohesive Material
label | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
label | (Or)
label | ○ Cohesive Material: Vane Shear Strength 70kPa
label | Standard / Specification - PS 21.6.5 and AS/NZS 2566.2
label | Verifying Document - Scala/Shear test result
label | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
label | Verification Activity: Activity - W
label | ○ Review of text reports/records or other evidence of compliance
label | Verification Activity: By - SE
checkpoint | 4.1.2 - Undercut approval
label | Detail / Activity - Trench Foundation
label | Acceptance / Conformance Criteria - 300mm Max cut
label | ○ IFC Drawing Sheet 320
label | (Or)
label | ○ Engineers approval
label | Standard / Specification - IFC Drawing WAT 0320. AS/NZS 2566.2/2002
label | Verifying Document - Lab Test Report / Watermainline record
label | Testing Quantity Required (based from schedule qtys) - If Undercut required
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.1.3 - Undercut Backfill Compliance
label | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
label | Acceptance / Conformance Criteria - Visiual Inspection
label | Standard / Specification - IFC Drawing WAT 0320
label | Verifying Document - Lab Test Report / Watermainline record
label | Testing Quantity Required (based from schedule qtys) - Every Undercut
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.1.4 - Bedding Zone Compaction Testing (PE Pipe)
label | Detail / Activity - On Granular Material / On each layer as per specification (19mm chip) NDM testing as per NZS4407:2015, Test 4.3
label | Acceptance / Conformance Criteria - Bedding Zone: 150mm minimum thickness (compacted) over the bottom of the trench.
label | ○ Minimum Compaction- 85% MDD
label | Standard / Specification - IFC Drawing 0320-1, AS/NZS 2566.2/2002
label | Verifying Document - NDM:Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - As per Water Specification. One test per 20m evenly spaced intervals.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.1.5 - Laying of Pipes
label | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
label | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
label | Acceptance / Conformance Criteria - As Per Drawings. Facing upwards
label | Standard / Specification - PS22.7.1 C
label | Verifying Document - Visual Inspection / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.2.2 - Electrofusion (EF) Welding
label | Detail / Activity - Required if Butt fusion welding cannot be perform.
label | ○ EF Jointing in accordance with PIPA POP 001.
label | ○ The lead welder or welding supervisor must verify on the site record form.
label | Acceptance / Conformance Criteria - WMS Report Checklist (refer to CWP).
label | Standard / Specification - PS 22.9.5, Appendix 22
label | Verifying Document - Visual Inspection / Electrofusion (EF) welding record checklist. WMS Report
label | Testing Quantity Required (based from schedule qtys) - Every Welding Point
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.2.3 - Electrofusion (EF) construction weld test
label | Detail / Activity - EF weld quality to be maintained.
label | Acceptance / Conformance Criteria - EF coupler and EF saddle testing
label | Standard / Specification - PS- 22.9.6 (b) (iv)
label | Verifying Document - Test report
label | Testing Quantity Required (based from schedule qtys) - 1 in 10 test
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2.4 - Survey
label | Detail / Activity - Inspection of Pipeline Inverts
label | Acceptance / Conformance Criteria - Vertical design Setout:
label | ○ Pipes ≤ 1% grade: +/- 10mm variance
label | ○ Pipes > 1% grade: +/- 20mm variance
label | Horizontal design Setout:
label | ○ +/-30mm variance
label | Standard / Specification - PS- 21.7.6 Table 21.15
label | Verifying Document - Survey Data / As-built record
label | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.3.1 - Emebment Zone - (Side Haunch Overlay)
label | Detail / Activity - 19mm chip backfill Compacted in 200mm Layers.
label | ○ NDM/Clegg Testing to be completed on maximum 200mm lifts of overlays .
label | ○ NDM BS to be Carried Out
label | Acceptance / Conformance Criteria - in 200mm layers.
label | ○ More than 85% of MDD.
label | Standard / Specification - NZS 4407:2015 Test 4.3 Nuclear Moisture Density Gauge; BS
label | Verifying Document - Lab Report / Watermainline record
label | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals. 200mm lift
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.3.2 - Pipe Markers
label | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
label | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
label | Acceptance / Conformance Criteria - AS Per Drawings.
label | Standard / Specification - PS 22.7.3 a
label | Verifying Document - Visual Inspection / Watermainline record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.3.3 - Backfill Compaction Testing
label | Detail / Activity - GAP65/AP65/LRAP65 Backfill Compacted in 200mm Layers.
label | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
label | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers.
label | ○ Testing to be completed on maximum 200mm lifts of backfill.
label | ○ LRAP65- achive 90% NDM on Grassed Area and 95% NDM on Shared and Carriageway.
label | OR
label | ○ Clegg 28CIV
label | Standard / Specification - PS- 22.13.5, NDM Standerd 25832, NZS 4402 Test 4.1.3
label | Verifying Document - Lab Report / Watermainline record
label | Testing Quantity Required (based from schedule qtys) - As per 200mm lift, One test per 20m evenly spaced intervals.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.4.1 - Watermain sleeve inspection - Pipe Inspection
label | Detail / Activity - Inspection of Watermain sleeve
label | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
label | Standard / Specification - Internal
label | Verifying Document - Watermain line record
label | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - SE
section | SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - ACCEPTANCE BEFORE COMMENCING DISINFECTION WORK
checkpoint | 5.1 - Survey As-Builts
label | Detail / Activity - Quality Check on sleeve based on the tolerances in RITS
label | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
label | Standard / Specification - Project Specifications
label | Verifying Document - CAD File as per PS12.3 and Red pen markup only
label | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature