## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | 101C-SDC-TMP-CON-ITP-008 - 3 - Suspended Concrete Slab |  |  |  |  | Yes | 101C-SDC-TMP-CON-ITP-008 - 3 - Suspended Concrete Slab | 1639df78-2a9c-465d-9c59-469669b9f384
checkpoint-group |  |  | section | Prior to Formwork Deck Handover
checkpoint-status |  |  | checkpoint | Current Drawing Status - Refer Aconex Document Register for latest approved Shop Drawings. Record drawings used at time of pour on ITP.
text | 71577392-12c1-515b-a87b-92b6737e8527 |  | textbox | Architectural Drawings
text | 35391470-e1ca-5251-ae7d-50a6f778b833 |  | textbox | Structural Drawings
checkpoint-status |  |  | checkpoint | Concrete Mix Design
text | aa0b26bf-fcf3-566e-823c-bba049b0a821 |  | textbox | Confirm Mix Design
checkpoint-status |  |  | checkpoint | Set-out - Surveyor set out slab grids to allow formwork construction
checkpoint-status |  |  | checkpoint | Survey & Set-out of formwork correct. Check correct heights for formwork soffit, Top of Concrete (TOC) and falls
label | 7e92b3f4-2de1-5ce1-87ec-7db3a674d241 |  | note | Attach Surveyor Formwork As-Built to ITP
checkpoint-status |  |  | checkpoint | Site Instructions - Copies of design changes, emails and site advices and the like to be attached.
checkpoint-status |  |  | checkpoint | Bondek (where applicable) - Back propping installed for pre pour and deflection & gaps sealed to prevent dripping
checkpoint-status |  |  | checkpoint | Structural Steel Sign off from Steel installer and Structural Engineer (where applicable for bondek slabs)
checkpoint-status |  |  | checkpoint | Formwork Sign-off - Area cleaned of all excess formwork, sawdust, reo and debris prior to pour. Safe Access to deck available.materials before handover deck
label | 41e7a28f-8521-5b18-a4e6-d67e7a5df259 |  | note | Attach formworkers ITP (referencing all hobs, steps, cast-ins, HDB's, bearing strips, polystyrene, fillets, etc… installed correctly)
checkpoint-group |  |  | section | Prior to Concrete Pour
checkpoint-status |  |  | checkpoint | Structural Compliance - Engineers approval for concrete placement required with list of defects to be completed
label | 9e61c242-2c12-584a-ab33-a3a588135238 |  | note | Attach structural engineers inspection report and evidence of close-out
checkpoint-status |  |  | checkpoint | Formwork Engineers Sign-off - Attach Sign-off
checkpoint-status |  |  | checkpoint | Post Tensioning - Check Subcontractor ITP complete, and attach to this ITP.
checkpoint-status |  |  | checkpoint | Screen Needle Cast-in's - Inspect all screen needles are installed in accordance with relevant shop drawings
label | 528ef2fc-3f99-53f3-a276-ddcef0e4da30 |  | note | Attach sign-off from Formworker
checkpoint-status |  |  | checkpoint | Curtain Wall Bracket Cast-in's - Inspect all Curtain wall brackets/rebates are installed in accordance with relevant shop drawings. Surveyor to confirm locations are correct.
label | 48245463-11d7-5676-8374-8cb3d0502001 |  | note | Attach Curtain Wall subcontractors sign-off & ITP from formworker
checkpoint-status |  |  | checkpoint | Crane/Hoist Bracket Cast-in's - Inspect all hoist and crane brackets are installed in accordance with relevant shop drawings. Surveyor to confirm locations are correct.
label | 4c3b3f45-78b0-55bc-9628-c84b2cacceae |  | note | Hoist and Crane contractor to inspect and sign-off cast-in position.
checkpoint-status |  |  | checkpoint | Temporary Penetrations - Inspect formwork penetrations in accordance with temporary works design. Surveyor to confirm locations are correct.
label | 4e806b36-cb1b-5334-8aab-68cb0e0307f4 |  | note | Temporary Penetrations may include: formwork hoist, concrete boom, etc…
checkpoint-status |  |  | checkpoint | In-Slab Services - Electrical subcontractor to sign off that all penetrations are installed in accordance with the design. Attach contractors ITP
checkpoint-status |  |  | checkpoint | In-Slab Services - Hydraulic subcontractor to sign off that all penetrations are installed in accordance with the design. Attach contractors ITP
checkpoint-status |  |  | checkpoint | In-Slab Services - Mechanical subcontractor to sign off that all penetrations are installed in accordance with the design. Attach contractors ITP
checkpoint-status |  |  | checkpoint | In-Slab Services - Fire Subcontractor to sign off that all penetrations are installed in accordance with the design. Attach contractors ITP
checkpoint-status |  |  | checkpoint | In-Slab Services - Security Subcontractor to sign off that all penetrations are installed in accordance with the design. Attach contractors ITP
checkpoint-status |  |  | checkpoint | Formwork Cast-ins - All timber fillets, drip grooves, Rebates, and proprietary shear connectors installed as required
checkpoint-status |  |  | checkpoint | Starter Bars - Confirm all starter bars for walls and columns installed as required per structural and architectural drawings and survey pins
checkpoint-status |  |  | checkpoint | Water Stops - Confirm installation of any proprietary water stops as required (ie; at CJ’s, etc…)
checkpoint-status |  |  | checkpoint | Reinforcement Cover - Check top RLs for all reinforcement, ensuring adequate concrete cover. Confirm with Concreter. Confirm that plastic bar chairs are used everywhere, particularly at exposed off-form soffits.
checkpoint-status |  |  | checkpoint | Attach Reinforcement contractors ITP
checkpoint-status |  |  | checkpoint | Concrete Falls - Check if concrete has falls, and ensure shutters, timbers, spacers are used to create folds where necessary
label | 0c708f08-397b-5649-92f4-d4d6c37335ab |  | note | Cross-check the following drawings: See Hydraulic, Architectural Concrete Outlines and Structural drawings
checkpoint-status |  |  | checkpoint | Cleaning of Deck - Clean off decks and beams prior to pour and ensure all exposed off-form soffits are free of any dust, stains, and rust marks. Hose down if necessary.
checkpoint-group |  |  | section | During Concrete Pour
checkpoint-status |  |  | checkpoint | Concrete Placement Checklist
boolean | 7913c179-94c9-519d-a948-d0a9c94253c5 |  | tickbox | Structural Engineer & Formwork Engineer Sign-off Received
boolean | 79922c4d-a7b3-5475-9417-7a5ba8f297fa |  | tickbox | Confirm Delivery Docket References correct mix design
boolean | 3c0e5aa6-2340-5e95-b8cf-be49dd705115 |  | tickbox | Plant and equipment checklist completed on concrete pump and lines
boolean | 931fdd79-290f-5785-802c-dba7dfd82152 |  | tickbox | Confirm concrete tester on-site and correct location of concrete pour provided to them for test results
label | 248d7a4c-044f-5752-bebe-bb2ab35d27b9 |  | note | 1, 4, 7, 28 & 56 day compressive test results to be issued by batch plant
checkpoint-status |  |  | checkpoint | Concrete Finish - Ensure concrete contractor is aware of required concrete surface finish.
checkpoint-status |  |  | checkpoint | Slab Curing - Check cured when bleed water stops and able to access slab without marking and also amount used complies
checkpoint-status |  |  | checkpoint | Concrete Falls - Confirm concrete has falls to drainage points in slab.
checkpoint-status |  |  | checkpoint | Attach Concrete Place Contractors ITP
checkpoint-status |  |  | checkpoint | Trade Representatives - Ensure a representative from each of the following is on site and witnessing the pour:
boolean | 274596a9-8284-55c2-a562-3a463c31a7f4 |  | tickbox | Form Worker
boolean | 6e693d5b-96b7-5efd-a753-91817e4b9749 |  | tickbox | Electrician
boolean | 4d76e6fc-1f2c-55c3-a91d-791136188cdf |  | tickbox | Plumber
boolean | a671c5d5-4c08-5660-a9d1-8999d27af5cf |  | tickbox | Post Tensioner
checkpoint-status |  |  | checkpoint | Confirm Form Worker has labour below deck inspecting all joints (particularly at columns & walls) and is immediately cleaning any slurry.
checkpoint-group |  |  | section | After Concrete Pour
checkpoint-status |  |  | checkpoint | Confirm Surveyor is out next day to carry out survey of finished concrete. Attach As built Survey Plan.
checkpoint-status |  |  | checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
label | 22ed6f70-72b8-5528-9059-0ffa3d38f35d |  | note | 6mm +/- from design RL
label | 74023c59-165d-53fa-bcb2-6f6223d28ae6 |  | note | 6mm +/- from 3.0m straight edges
checkpoint-status |  |  | checkpoint | Exposed Concrete Finish - Confirm finish of concrete is adequate for application (broom/trowel/helicopter finish), refer to AS3610 (Class 1, 2 or 3)
checkpoint-status |  |  | checkpoint | Concrete Test Results - Note test results on ITP and attach:
text | a1ddf03f-e21d-552c-b850-a1e687cafdac |  | textbox | 1 Day
text | fe30e90a-5fb4-5064-a514-5f52dfe6511f |  | textbox | 4 Day
text | 8becb43c-e7d2-5896-bc57-4c3a4c1c9126 |  | textbox | 7 Day
text | f9ca7c0a-9042-5d98-bf73-7ed0fad33737 |  | textbox | 28 Day
text | d3436848-b341-5571-8ded-d3c90f10030f |  | textbox | 56 Day
checkpoint-status |  |  | checkpoint | Initial Stressing - Concrete has achieved required strength MPa (10 MPa and confirmed by Concrete contractor)
label | c63b12e5-d21d-5ebd-a6d0-4bbcbc26a6ec |  | note | Concrete Contractor must issue Concrete test results, verbal not accepted
checkpoint-status |  |  | checkpoint | Final Stressing - Concrete has achieved required strength Mpa (22 Mpa and confirmed by concrete contractor)
label | 1188e90e-ee7d-54b8-b59d-1a0cd8f0a55d |  | note | Concrete Contractor must issue Concrete test results, verbal not accepted
checkpoint-status |  |  | checkpoint | Stressing Sign-off - Before stripping can commence final stress complete, Ducts grouted and PT supervisor issues verification records
label | fff3426b-83cc-50f5-8e4a-d67a41db9099 |  | note | Attach Post Tension Contractors ITP
checkpoint-status |  |  | checkpoint | Extension Records Approval - Engineer approval of extension records following final stress
text | 2c04992a-3395-5768-9381-56b23470d61c |  | textbox | Record date when props were removed if not given approval by engineer
checkpoint-status |  |  | checkpoint | All non-conformances closed out and accepted by Structural Engineer and Architect.
holdpoint |  |  | signoff | Final ITP Review & Sign-off by Project Engineer
checklist-sectioned |  |  | checklist | 101C-SDC-TMP-CON-ITP-007b - 3 - Stairs FRP Works |  |  |  |  | Yes | 101C-SDC-TMP-CON-ITP-007b - 3 - Stairs FRP Works | 355d3d5f-c93a-4903-b4f9-30f8ed07dbd0
checkpoint-group |  |  | section | Prior to Concrete Pour
checkpoint-status |  |  | checkpoint | Confirm bottom, mid & top of stair RL's on Architectural Concrete Outlines.
text | e8432eb9-d3bf-54c0-ab3c-5666ea19e365 |  | textbox | Bottom Landing RL
text | 522ca3ff-d379-52e2-a9ab-3283d628ca54 |  | textbox | Mid Landing RL
text | 1f24f4ff-b86c-5894-b788-58006e9dca4d |  | textbox | Top Landing RL
checkpoint-status |  |  | checkpoint | Confirm Re-boxes/cast-in bars are installed to correct heights at landings, based on nominated design RL's.
checkpoint-status |  |  | checkpoint | Confirm any starter bars on landings for dividing walls, etc… are installed as per Structural Drawings
checkpoint-status |  |  | checkpoint | Check for reinforcement cover as per Structural Drawings.
label | efda221b-4598-5123-8e20-9290008eb0dc |  | note | Cover requirement generally 30mm
checkpoint-status |  |  | checkpoint | Confirm all cast in elements installed (eg, stair handrails, etc…)
checkpoint-status |  |  | checkpoint | Confirm all formwork is clean and free of debris.
checkpoint-status |  |  | checkpoint | Confirm any conventional parts of stairs have been formed in accordance with the relevant shop drawings and standards.
label | 939e6cf6-de24-5941-9f7b-742819c18525 |  | note | Statutory Requirements (Dimensions in mm): Riser: Min. 115, Max. 190 Going: Min. 240, Max. 355 Ensure consistency
checkpoint-status |  |  | checkpoint | Confirm cast-in of anti-slip items if required (eg, carborundum powder, stair nosings, etc…);
checkpoint-status |  |  | checkpoint | Obtain certificate from Structural Engineer prior to concrete pour and attached completed Inspection Report.
checkpoint-status |  |  | checkpoint | Confirm MPa, slump and agg. size of concrete prior to ordering.
text | cd6146d1-2ebb-56b4-9646-825e787cf64d |  | textbox | Concrete Mpa/Mix Design
checkpoint-status |  |  | checkpoint | Obtain subcontractors ITP (Steel Fixer) & attach to ITP
checkpoint-status |  |  | checkpoint | Obtain subcontractors ITP (Form Worker) & attach to ITP
checkpoint-group |  |  | section | During Concrete Pour
checkpoint-status |  |  | checkpoint | If the stairs are being used as access to a leading deck, ensure alternative access is established prior to pouring.
checkpoint-status |  |  | checkpoint | Confirm concrete tester onsite during concrete pour, and the following tests have been requested.
label | 061bea70-3313-5d8d-aec5-01c437d7de85 |  | note | 7 Day
label | 362ef73f-a50c-537b-9a30-8b523e267b2c |  | note | 28 Day
label | cec00985-e38f-58cf-b784-74ea822c451f |  | note | Ensure concrete tester is aware of pour locations
checkpoint-status |  |  | checkpoint | Ensure a representative from each of the following is on site and witnessing the pour:
boolean | 31fa7557-407d-52d8-a95f-0c8ea6e688a3 |  | tickbox | Form Worker
boolean | c3976a82-9072-5fb6-9178-4fea09025f3a |  | tickbox | Electrician
boolean | 7d8cbc69-dd58-5e21-aabf-06c1380565c3 |  | tickbox | Plumber / Fire services
checkpoint-status |  |  | checkpoint | Ensure concreters have correct finishing tools (eg, carborundum powder, etc…).
checkpoint-status |  |  | checkpoint | Ensure only rubber tipped vibrators are used to prevent formwork damage.
checkpoint-status |  |  | checkpoint | Obtain Subcontractors ITP (Concretor) & attach to this ITP
checkpoint-status |  |  | checkpoint | Ensure Form Worker labour is available to clean up any slurry runs at bottom of stairs, immediately after pour.
checkpoint-group |  |  | section | After Concrete Pour
checkpoint-status |  |  | checkpoint | Confirm tolerance of finished concrete surfaces:
label | 0d39ffe8-ee98-52fa-b9f2-bc81f956f666 |  | note | 6mm +/- from design RL
label | 6ba58a59-474a-533c-8221-6387e7075c24 |  | note | 6mm +/- from 3.0m straight edges.
checkpoint-status |  |  | checkpoint | If an as-built survey is required, confirm Surveyor is out next day to carry out survey of finished concrete. Attach As built Survey Plan
checkpoint-status |  |  | checkpoint | Obtain all concrete tests at 7 days. Attach to ITP
checkpoint-status |  |  | checkpoint | Obtain all concrete tests at 28 days. Attach to ITP
holdpoint |  |  | signoff | Final ITP Review & Sign-off by Project Engineer
checklist-sectioned |  |  | checklist | Services Rough-in - Mechanical |  |  |  |  | Yes | Services Rough-in - Mechanical | 36032e1f-08c7-4798-85f9-a88cbbaa88a4
checkpoint-group |  |  | section | Fire Rating
checkpoint-status |  |  | checkpoint | Check 1m benchmark has been set and agreed for services installation heights
label | 579f9123-3374-5836-ac43-fe5a828138a3 |  | note | Attach Photo of benchmark for reference
checkpoint-status |  |  | checkpoint | Ensure services are installed neatly through fire rated walls
label | 397a683d-d621-5e20-b423-4f27b3e40358 |  | note | Sheet areas of wall where services are to penetrate first (ie; above entry door), then install services to avoid non-compliances with sheeting.
checkpoint-status |  |  | checkpoint | Confirm any Mechanical cable/conduit penetrating the fire rated walls are sealed on both sides with intumescent fire mastic (conned around cable/penetration)
checkpoint-status |  |  | checkpoint | Confirm at least 100mm separation between mechanical cables/conduits and any other services (200mm form fire dampers) where passing through a fire rated wall.
checkpoint-status |  |  | checkpoint | Fire Damper Checklist:
boolean | ac10f03a-aa17-55e5-a529-80e3147b66ab |  | tickbox | Ensure fire dampers installed at least 200mm away from other services where penetrating a fire rated wall
boolean | db700811-8eb9-53e5-a2a0-13d2fb4ca159 |  | tickbox | Ensure inside of damper penetration is lined ans sealed with fire rated plasterboard prior to damper installation
boolean | 654871d3-603a-5c2e-a267-129c343c87d3 |  | tickbox | Ensure two layers of fire rated plasterboard installed each side of wall for damper installation (if not install additional layer locally as required)
boolean | 15e12a42-5deb-5286-8333-b3de7844e62a |  | tickbox | Ensure provision for access (panels) installed for future damper inspection (both within ceiling and connecting ductwork)
boolean | 2662999a-56ca-50a5-8632-cbb37034b936 |  | tickbox | Ensure flanges installed around all 4 sides of damper and no gaps visible.
boolean | 2b0e251f-2475-5730-a7c5-bf73830ffe37 |  | tickbox | Fire Damper Approval - Check installation against data sheet/test report from contractor
boolean | 9683530d-6b5f-5110-a473-ae71c785e5e8 |  | tickbox | Attach photos of compliant installation
checkpoint-status |  |  | checkpoint | Intubatt (Fibre Board Products) used with services
boolean | 9ea5ae42-c65f-54a8-85ad-655436c59b47 |  | tickbox | Ensure fixings at 200mm centres and washers are visible
boolean | 87be9ee9-3198-5fd4-8a87-3dd44ee53223 |  | tickbox | Ensure exposed edges of the board are covered with sealant to prevent deterioration over time
boolean | 0b0f6c01-e457-551f-8547-d314db186ee1 |  | tickbox | Ensure where service penetrates the board that fire wrap and sealant are used to close any gaps
boolean | dc6fbf24-21e9-5b9e-a598-c61a9a880cd3 |  | tickbox | Attach photos of compliant installation
checkpoint-status |  |  | checkpoint | Retro-Fit Fire Collars - Ensure correct size collar for service and that hole around services is sealed (coned) with fire rated sealant prior to installation.
label | d0f85ae5-ba43-5e5c-ae2e-7ee29560690a |  | note | Ensure an Acrylic Sealant is used (not intumescent sealant) when installing around fire collars
checkpoint-status |  |  | checkpoint | Confirm statuatory fire labels are installed adjacent services prior to sheeting. Attach photos for record.
checkpoint-group |  |  | section | Mechanical Services
checkpoint-status |  |  | checkpoint | Confirm Latest Mechanical Plans are being used with Contractor (Refer Aconex)
text | 61c46027-bcc9-5900-987f-5e08ddaf35a6 |  | textbox | Record Plan numbers and revisions
checkpoint-status |  |  | checkpoint | Complete visual check that all flexible and ridgid ductwork has been installed per plans (also reference architectural RCP for future grille locations).
label | 026f863d-ed5a-5289-a8e6-afe5e5077462 |  | note | Review to ensure no damages - take photos for record.
label | bec36726-f912-5ca6-890f-fb002a04b6d0 |  | note | Review support straps to flexible ductwork are installed evenly to prevent restrictions
text | 943134e1-1399-55cb-9087-a3e835e04ffe |  | textbox | Record any deviations from plans and reasons why.
checkpoint-status |  |  | checkpoint | Confirm wiring of AC controls are located per architectural requirements
label | 0bcfc15d-bdd1-53f1-915d-0c958bfbebd1 |  | note | Refer to drawing: FJMT-A-61500 & specific apartment plan on Aconex for guidance
checkpoint-status |  |  | checkpoint | Typical Mechanical Services Rough-in Heights - Spot check each room as follows:
label | 0b78e874-7ab3-5117-b88d-0d11639e552e |  | note | A/C Control & Thermostat - 75mm below home automation unit to top of controller where applicable
label | 28539a7a-b4aa-5295-bf65-3db6d2d97474 |  | note | A/C Control & Thermostat - 75mm above light switch to bottom of controller where applicable
text | e1ffc51b-695e-514e-bd82-e1b6c96fd28b |  | textbox | Record any deviations from typical heights and reasons why.
checkpoint-status |  |  | checkpoint | Review connections between flexible and ridgid ducting to ensure mechanically fixed and sealed.
checkpoint-status |  |  | checkpoint | Review connection between ductwork and façade to ensure mechanically fixed, sealed and a canvas connection is used to allow movement.
label | c30828b9-ccf2-561b-a60a-bd1f9928dce2 |  | note | Plenum box should be installed to curtain wall panel prior to installation to ensure properly sealed
checkpoint-status |  |  | checkpoint | Review Electrical Panel and Filter locations to FCUs to ensure they are not blocked and are accessible.
checkpoint-status |  |  | checkpoint | Review condensate drains and trays have been connected to hydraulic drainage and water tested to check for leaks.
label | 3548a6c0-4a34-5780-8f3a-82ae8f90f256 |  | note | Check that condensate drain pipes have positive fall all the way to tundish point & 25mm air gap above tundish visible. Attach photos for record.
checkpoint-status |  |  | checkpoint | Confirm refrigerant testing of lines completed prior to sheeting to check for leaks.
holdpoint |  |  | signoff | HOLD POINT - Contractor to sign off on testing. Attach test sheet
checkpoint-status |  |  | checkpoint | Review thermal insulation installed on refrigerant lines from the riser all the way to the FCU connection point.
checkpoint-status |  |  | checkpoint | Confirm Installation of earthquake bracing as required by standard
checkpoint-status |  |  | checkpoint | Confirm adaptable apartment future provisons installed if applicable
checkpoint-status |  |  | checkpoint | Services Checking Consultant Inspection Completed prior to Sheeting
holdpoint |  |  | signoff | HOLD POINT - Confirm Inspection items closed & Photos attached
checkpoint-status |  |  | checkpoint | Attach Subcontractor ITP
checkpoint-group |  |  | section | Mechanical Services - Acoustic Requirements
checkpoint-status |  |  | checkpoint | Confirm flexible ductwork is acoustically rated (ie. Inner flex is perforated and insulation lining between inner and outer flex).
checkpoint-status |  |  | checkpoint | Review AC Fan Coil Unit (FCU) has vibration isolation (rubber) mounts or springs installed
checkpoint-status |  |  | checkpoint | Review Toilet/Laundry/Kitchen Exhaust fans have vibration islation (rubber) mounts or springs installed
checkpoint-status |  |  | checkpoint | Review where flexible ductwork passes through full height acoustic walls (eg. Wet areas) - ensure wrapped in sheet metal and caulked (max. 10-15mm gap around service)
checkpoint-status |  |  | checkpoint | Review ductwork joints to ensure sealed properly (with "Emer-seal" joint sealant) to prevent noise resulting from air leakage
checkpoint-group |  |  | section | Sign-off
checkpoint-status |  |  | checkpoint | Subcontractor Signoff
holdpoint |  |  | signoff | Subcontractor Sign-off
checkpoint-status |  |  | checkpoint | SDC Signoff
holdpoint |  |  | signoff | SDC Sign-off
checklist-sectioned |  |  | checklist | Framing/Sheeting |  |  |  |  | Yes | Framing/Sheeting | 37102f3d-3041-437b-a7a1-a758bb233171
checkpoint-group |  |  | section | Survey/Wall Framing
checkpoint-status |  |  | checkpoint | Confirm set-out of walls in correct locations & cross check with surveyors grids.
text | bf593cf7-e545-5d09-9b0b-ec0e6373d66f |  | textbox | Confirm wall set-out plan/revision used for set-out
checkpoint-status |  |  | checkpoint | Confirm that 1m benchmark has been reviewed and agreed. Ensure it is marked on most relevant permanent structure.
label | 172e069e-c65b-54dc-b5a7-1c15435da685 |  | note | Attach photo of 1m benchmark for reference.
checkpoint-status |  |  | checkpoint | Review wall types are installed correctly per architectural wall type details.
checkpoint-status |  |  | checkpoint | Review wet area framing to ensure square and plumb to take tiling.
checkpoint-status |  |  | checkpoint | Strengthening Requirements - Confirm all noggins, trimming blocks and struts have been appropriately installed to support the following items (Min. 12mm structural plywood). Ensure to cross check relevant drawings:
label | 2c5a047b-960f-5c5f-aa3a-0cb88c8cc8cb |  | note | Appliances (Wall mounted dryers, etc…)
label | c1b1f60c-6dc9-5f9a-8745-995ef2938d45 |  | note | Bathroom Accessories (Robe hooks, towel rails, shower shelves, toilet roll holders, adaptable handrails, etc…)
label | 925b3429-826e-5c1e-b9d5-42f3bd35a048 |  | note | Bathroom Furniture (Mirror Cabinets, Vanity Basins, shower roses, etc…)
label | 3d0db52b-01eb-5cce-8cbf-3a3679aa89de |  | note | Services (pendant lighting, display screens, TV areas, etc…)
checkpoint-status |  |  | checkpoint | Adaptable Apartments - Check blocking installed to cater for post adaptation layouts
checkpoint-status |  |  | checkpoint | Confirm that all framing is square at corners (check top, middle & bottom of frame junctions)
checkpoint-status |  |  | checkpoint | Confirm studs not bridging or touching hydraulic pipes, mechanical units, columns in intertenancy walls or lift shaft walls to ensure vibration is not transferred through walls
checkpoint-status |  |  | checkpoint | Deflection Requirements - Ensure gap is present (10-15mm) at top of stud inside head track
checkpoint-status |  |  | checkpoint | Joinery Openings - check gaps between framing to joinery + wall finishes will fit (5mm tolerance)
checkpoint-status |  |  | checkpoint | Stud Spacing - Spot check studwork is spaced at 600mm maximum per Architectural Specification. Check additional studwork reinforcement at openings (ie; double studwork).
label | 39866e90-f81a-57a8-a328-13140080c264 |  | note | Staggered Studs (if required) - to be installed at 300mm centres alternating per architectural specification
checkpoint-status |  |  | checkpoint | Movement Joints - check walls are discontinued where they pass over building movement joints.
checkpoint-status |  |  | checkpoint | Services Risers - Ensure stud and trackwork is kept a minimum of 20mm away from vertical services within risers per acoustic specification
checkpoint-status |  |  | checkpoint | Engineered Designs - Spot check any engineered framing designs and attached engineers review and sign-off on system.
checkpoint-group |  |  | section | Wall Sheeting
checkpoint-status |  |  | checkpoint | Confirm acoustic/thermal insulation installed to achieve design ratings
label | 9214adb6-d2ff-5660-8c6b-148031b3d64c |  | note | Cross check product ratings against architectural insulation plans
checkpoint-status |  |  | checkpoint | Confirm there is a minimum of 45mm cavity between the residential intertenancy wall studwork per Acoustic Details/Wall type Plans
checkpoint-status |  |  | checkpoint | Confirm door frames are installed vertical and plumb and at correct height.
label | 6dd1553e-b07f-5f38-8ad6-7ad960f7ad18 |  | note | Check metal door frames in wet areas are outside of membrane zone (ie; notched accordingly).
checkpoint-status |  |  | checkpoint | HOLD POINT - Confirm Acoustic Consultant Inspection Completed prior to sheeting walls
holdpoint |  |  | signoff | Review & Sign-off by Acoustic Consultant
checkpoint-status |  |  | checkpoint | Check plasterboard sheets installed with 10-15mm gap at top and bottom to allow for deflection and fire sealant.
checkpoint-status |  |  | checkpoint | Control Joints - Ensure controls joints installed in wall runs larger than 12m in length.
checkpoint-status |  |  | checkpoint | Check correct plasterboard linings installed (type and thickness) per architectural wall types
checkpoint-status |  |  | checkpoint | Ensure sheets are staggered on multiple sheet layer walls. Stagger all sheet joints by minimum 200mm per architectural specification.
checkpoint-status |  |  | checkpoint | Confirm plasterboard lining installed to wet areas are sealed up to concrete soffit on both sides of wall where adjacent to habitable rooms.
checkpoint-status |  |  | checkpoint | Confirm all services penetrations through wet area walls adjacent to habitable rooms are sealed and caulked for acoustic performance.
label | 2e46ccf7-7f4f-5172-a94e-48007bf168d3 |  | note | Check that mechanical flex ducts are not passing through walls - to be rigid ductwork or sleave installed over.
checkpoint-status |  |  | checkpoint | Check intertenancy walls extend to façade panels, leave 10-15mm gap and caulked with fire sealant.
checkpoint-group |  |  | section | Sheeting Ceilings
checkpoint-status |  |  | checkpoint | Confirm ceiling insulation complete where applicable
checkpoint-status |  |  | checkpoint | Confirm provisions made in ceiling framing for access panels and air grilles were required by architectural RCP
label | 7fdffaac-406b-5801-bef2-6361fc7b31f7 |  | note | Spot check access panels installed to allow access to fire dampers and mechanical fans
checkpoint-status |  |  | checkpoint | Confirm ceiling framing bulkheads are square and level
checkpoint-status |  |  | checkpoint | Confirm furring channels do not clash with other services (eg; downlights, access panels, mechanical exhaust, sprinkler heads, etc…).
checkpoint-status |  |  | checkpoint | HOLD POINT - Confirm Acoustic Consultant Inspection Completed prior to sheeting
holdpoint |  |  | signoff | Review & Sign-off by Acoustic Consultant
checkpoint-status |  |  | checkpoint | HOLD POINT - Confirm BCA consultant inspection of services penetrations through fire rated walls prior to sheeting ceilings
holdpoint |  |  | signoff | Review & Sign-off by BCA consultant
checkpoint-status |  |  | checkpoint | Confirm Plasterboard fixings are at correct intervals
label | 47cc8396-5364-55eb-8c95-5ebafa007f1a |  | note | For painted surfaces, screw fixing onto sheeted frames should be max 400mm spacing. Refer to Manufacturer’s Installation guide
checkpoint-status |  |  | checkpoint | Confirm Villaboard/FC (wet area) fixings are of the correct intervals
label | be026fdc-1154-5e26-8d0d-16328c8b72b7 |  | note | For 9mm Villaboard/FC: Tiled wall screw fixings must be max 150mm spacing. Stud centres to be 400mm. Refer to Manufacturer’s Installation guide
checkpoint-status |  |  | checkpoint | Control Joints - Ensure ceiling bays are not larger than 10m x 7m without a joint or wall break.
checkpoint-status |  |  | checkpoint | Attach Subcontractor ITP for the Works
checkpoint-status |  |  | checkpoint | HOLD POINT - OK to proceed to painting
label | b4d64f56-0ea4-5b50-a1c8-90071a066939 |  | note | All defects completed?
checkpoint-group |  |  | section | Sign-off
checkpoint-status |  |  | checkpoint | Subcontractor Signoff
holdpoint |  |  | signoff | Subcontractor Sign-off
checkpoint-status |  |  | checkpoint | SDC Signoff
holdpoint |  |  | signoff | SDC Sign-off
checklist-sectioned |  |  | checklist | Services Rough-in - Hydraulic |  |  |  |  | Yes | Services Rough-in - Hydraulic | 52d7daf4-794d-446c-abfc-f79ea2f171de
checkpoint-group |  |  | section | Fire Rating
checkpoint-status |  |  | checkpoint | Check 1m benchmark has been set and agreed for services installation heights
label | 6d45aecf-5f00-53c7-acce-1a9ad270aa4b |  | note | Attach Photo of benchmark for reference
checkpoint-status |  |  | checkpoint | Ensure services are installed neatly through fire rated walls
label | 67875932-c3f7-5c83-a864-e1e0307faf26 |  | note | Sheet areas of wall where services are to penetrate first (ie; above entry door), then install services to avoid non-compliances with sheeting.
checkpoint-status |  |  | checkpoint | Confirm any PEX pipes penetrating the fire rated walls are sealed on both sides with intumescent fire mastic (conned around pipe)
checkpoint-status |  |  | checkpoint | Confirm at least 100mm separation between hydraulic services and any other services (200mm form fire dampers) where passing through a fire rated wall.
checkpoint-status |  |  | checkpoint | Intubatt (Fibre Board Products) used with services
boolean | 694aa2e0-d35e-57eb-b45c-2c331dfbfa8b |  | tickbox | Ensure fixings at 200mm centres and washers are visible
boolean | 15e0764b-848b-51c5-98e9-bfdfd0d9d0c5 |  | tickbox | Ensure exposed edges of the board are covered with sealant to prevent deterioration over time
boolean | dee391c5-a54f-5cca-9904-9b23adf2415f |  | tickbox | Ensure where service penetrates the board that fire wrap and sealant are used to close any gaps
boolean | c94f9e47-69db-51ea-a11f-00ff3f3c2998 |  | tickbox | Attach photos of compliant installation
checkpoint-status |  |  | checkpoint | Retro-Fit Fire Collars - Ensure correct size collar for service and that hole around services is sealed (coned) with fire rated sealant prior to installation.
label | b5851776-5b36-542b-b003-70123a8ffb63 |  | note | Ensure an Acrylic Sealant is used (not intumescent sealant) when installing around fire collars
checkpoint-status |  |  | checkpoint | Check copper or steel pipes penetrating fire walls have fire wrap installed with at least 3 stainless cable ties.
label | a9611b02-81c4-511f-903f-89d2ab3ccd57 |  | note | Ensure fire caulking is used to close any gaps around the pipe (coned) at the wall penetration prior and post wrap installation.
checkpoint-status |  |  | checkpoint | Confirm statuatory fire labels are installed adjacent services prior to sheeting. Attach photos for record.
checkpoint-group |  |  | section | Hydraulic Services
checkpoint-status |  |  | checkpoint | Confirm Latest Hydraulic drainage and pressure Plans are being used with Contractor (Refer Aconex)
text | 39db0f5a-035c-56b6-9f92-21237ebc4955 |  | textbox | Record Plan numbers and revisions
checkpoint-status |  |  | checkpoint | Service Installations - Complete visual check to confirm all hydraulic drainage and pressure services are installed per plans.
text | 4400c46f-7192-5e04-9924-7bba77b0d0b0 |  | textbox | Record any deviations from plans and reasons why.
checkpoint-status |  |  | checkpoint | Typical Hydraulic Services Rough-in Heights - Spot check each room as follows (centre line of fitting):
label | e11d0c11-c07d-5afe-8b40-b9be6bcf0f05 |  | note | External Balcony Tap - 450mm AFFL
label | 8b574fcd-6cbd-5a16-9f25-6cbf4ae4367c |  | note | External Balcony Gas Point - 450mm AFFL
label | 7eed5040-46b3-5ba6-87a7-69933ff20abd |  | note | Bathroom & Kitchens - Refer to apartment specific plans to confirm correct rough-in heights
text | fcc3b18c-557c-5c98-8621-14065b2c90f9 |  | textbox | Record any deviations from typical heights and reasons why.
checkpoint-status |  |  | checkpoint | Review hot water supply is on the left hand side and cold water supply on the right hand side to:
boolean | 8b967af4-0b78-5c94-98e5-a3fa24ebe97a |  | tickbox | Kitchen
boolean | 875eaa89-aff1-562a-8727-9daf9c65e277 |  | tickbox | Bathrooms
boolean | 9fbe428c-7f78-537c-9aa3-7c9b8ae160d9 |  | tickbox | Laundry
checkpoint-status |  |  | checkpoint | Confirm A/C tundish location has been supplied and trap prefilled
checkpoint-status |  |  | checkpoint | Confirm all in-wall hydraulic PC items installed (ie; in-built cisterns, mixer bodies, etc…)
checkpoint-status |  |  | checkpoint | Confirm all supply pipes are charged so any leaks can be identified now and in the future.
checkpoint-status |  |  | checkpoint | Confirm that pipework pressure, choke and hydrostatic testing has been completed.
label | 052af9f2-485c-526e-abf8-00e5c4fbb245 |  | note | Pipes should be left under test at 1500kPa (where applicable) for a minimum of 2hrs per the hydraulic specification. Provide time stamped before and after photos where relevant of pressure gauges.
holdpoint |  |  | signoff | HOLD POINT - Contractor to sign off on testing. Attach test sheet
checkpoint-status |  |  | checkpoint | Check minimum 25mm separation between gas/water services and power.
checkpoint-status |  |  | checkpoint | Check that any operable valves or equipment (ie; PAPA Valve or TMV) behind walls or ceilings have a suitable access panel installed adjacent.
checkpoint-status |  |  | checkpoint | Geberit Supertube - Complete visual check to ensure correct fittings are being used (search website link below for fitting types and install location reference). Review any horizontal pipe runs with 0% fall do not exceed 6m (which is the max. allowed by system).
label | 2279818c-3a25-5e17-bc98-45bb28d352a9 |  | note | Website Link: https://www.geberit.com.au/products/piping-systems-for-building-drainage/geberit-supertube/
checkpoint-status |  |  | checkpoint | Confirm drainage points are capped off prior to fit-out trades commencing to prevent blockages from construction debris.
checkpoint-status |  |  | checkpoint | Confirm adaptable apartment future provisons installed if applicable
checkpoint-status |  |  | checkpoint | Services Checking Consultant Inspection Completed prior to Sheeting
holdpoint |  |  | signoff | HOLD POINT - Confirm Inspection items closed & photos attached
checkpoint-status |  |  | checkpoint | Attach Subcontractor ITP
checkpoint-group |  |  | section | Hydraulic Services - Acoustic Requirements
checkpoint-status |  |  | checkpoint | Confirm PEX pipes running through studwork have gromets or silcone installed locally to prevent water hammer noise and damages.
checkpoint-status |  |  | checkpoint | Confirm no pipework is fixed to plasterboard or bridging cavities - should be fixed to studwork or blocking timbers.
checkpoint-status |  |  | checkpoint | Review pipe clamps to ensure they have resilient foam sleeves installed to prevent vibration and noise transfer to structure.
checkpoint-status |  |  | checkpoint | Pipe Lagging - Complete checks as listed below:
boolean | 26d6e0bd-598f-56d2-8088-2f558342c532 |  | tickbox | Review all waste and stormwater pipes located in risers and ceilings are lagged.
boolean | 5fc15055-55f5-55fe-8eb5-c595cad4bc70 |  | tickbox | Pipes running within 3m of A/C return air grille locations are to be double lagged.
boolean | 11c3aee9-b758-5f3d-ac7e-693ff23f9a15 |  | tickbox | Review pipework lagging is overlapped 50mm at lagging joints.
boolean | abd2e7a9-d1fb-5216-b320-4b98cc90bfba |  | tickbox | Where lagged pipes penetrate slabs, walls and risers, ensure lagging is flanged with 50mm overlap where it meets the penetrating surface.
boolean | ac7a9501-22f0-59f7-962c-7549efde62d9 |  | tickbox | Review lagging around pipes is clear of any part of the structure (ie; walls, ceilings, slabs, framework, other services, etc…).
checkpoint-group |  |  | section | Sign-off
checkpoint-status |  |  | checkpoint | Subcontractor Signoff
holdpoint |  |  | signoff | Subcontractor Sign-off
checkpoint-status |  |  | checkpoint | SDC Signoff
holdpoint |  |  | signoff | SDC Sign-off
checklist-sectioned |  |  | checklist | Waterproofing - Internal Areas |  |  |  |  | Yes | Waterproofing - Internal Areas | 554ded49-5030-4db7-9e47-02d4e6214d45
checkpoint-group |  |  | section | Prior to Works
checkpoint-status |  |  | checkpoint | Substrate - Review to ensure any voids or protrusions are filled and removed to provide smooth surface.
label | cdb190e7-0edd-5326-ae61-39d1b3113420 |  | note | Also ensure substrate is clean and free of any water, dust and debris.
checkpoint-status |  |  | checkpoint | Verify with Plumber that their drainage works are completed prior to membrane commencement.
label | 99b4d606-7467-5edc-9eac-ba1baed4a7db |  | note | Attach Subcontractor ITP where relevant.
checkpoint-status |  |  | checkpoint | Concrete Cracks - Review substrate for any cracking. Up to 2mm cracks fill with Polyurethane sealant. Above 2mm to be chased, cleaned and primed, then sealant applied.
checkpoint-status |  |  | checkpoint | Falls - Review concrete substrate to ensure min. 1:100 falls achieved and falling to floor wastes (1:60 falls in shower area).
checkpoint-status |  |  | checkpoint | Floor Wastes - Review puddle flange to ensure it is recessed and flush with floor substrate. The PVC flange should be lightly sanded to promote membrane adhersion.
label | 2c14f164-90ff-5f49-bd68-5acad6e82ec1 |  | note | Also check internal of floor wastes to ensure free from debris prior to waterproofing.
checkpoint-status |  |  | checkpoint | Substrate Moisture Content - Verify that waterproofing contractor has tested moisture content of concrete substrate and is happy to proceed with works (ie; below 5%).
text | 7d0eae13-a207-5936-b0f1-eafcf320e87c |  | textbox | Record moisture meter reading.
holdpoint |  |  | signoff | Subcontractor to sign-off on substrate.
checkpoint-status |  |  | checkpoint | Waterstop Angles - Check angles installed in correct position at wet area entry doors and showers.
label | 5d404057-7fcf-5f52-9f72-74f34c532ea2 |  | note | Also check angles are installed at correct heights based of agreed 1m mark from FFL.
checkpoint-status |  |  | checkpoint | Waterproofing Materials - Confirm approved waterproofing materials are being used for the works.
label | 5c7024eb-7e4c-5fc8-91c3-2a03b7389564 |  | note | Waterproofing Primer: Nitroprime 120. Waterproofing Membrane: Nitroproof 410.
checkpoint-status |  |  | checkpoint | Record product batch/serial numbers for tracking of any future defects.
text | c99f006d-47b4-5186-9293-839d13199f80 |  | textbox | Batch/Serial Numbers:
checkpoint-status |  |  | checkpoint | Membrane Supplier Inspection - Confirm membrane supplier inspection of substrate to ensure prepared in accordance with specification.
label | 89540209-1fad-5648-9dda-381e843dbbd3 |  | note | Attach record of inspection where applicable.
checkpoint-group |  |  | section | During Works
checkpoint-status |  |  | checkpoint | Sealant/Bond Breakers - Confirm applied to all wall/floor and wall/wall junctions as well as around any services penetrations and wall fixings (ie; screw fixings, etc…). Surfaces should be primed prior to application of sealant/bond breakers.
label | 5608da12-5f95-5f02-88ad-ea553679e412 |  | note | Waterproofing Sealant: Nitroseal SC600 (Check to ensure gaps not more than 20mm wide/deep for sealant application. Min. fillet of sealant should be 8mm wide for horizontal joints, 5mm wide for vertical). Bond Breaker: Nitroband Tape (ensure surface primed prior to install and overlapping at joints 150mm each side).
checkpoint-status |  |  | checkpoint | Floor Membrane - Confirm 1x coat of primer (Nitroprime 120 - 1hr curing time prior to membrane application) & x2 coats of membrane (Nitroproof 410 Parts A & B - requires 6hrs curing time between coats).
label | 285cc6e4-c324-5548-b8ae-4bce8505e689 |  | note | Attach progress photos of completed membrane works. Ensure no membrane on top of exposed floor angles. Ensure doorway is barricaded with signage to prevent damage from other trades.
checkpoint-status |  |  | checkpoint | Membrane Skirting Upturn - ensure membrane applied 150mm up wall from structural floor level per standards.
checkpoint-status |  |  | checkpoint | Wall Membrane - confirm membrane applied to whole shower, bath and basin areas where applicable. Ensure membrane extends at least 100mm past the extent of these areas and overlaps with floor membrane upturn.
label | 9af588be-730b-582a-9973-9ff15451cd17 |  | note | Attach progress photos of completed membrane works.
checkpoint-group |  |  | section | After Works
checkpoint-status |  |  | checkpoint | Flood Testing: Block floor waste points and fill room to door angle height and leave for 24hrs.
label | 20016548-2d23-5440-93ba-4df48fab1113 |  | note | NOTE: Verify that final coat of membrane has had 24hrs curing time prior to Flood testing.
label | ab2fa52c-3e08-578f-a092-d87ec0e2b90e |  | note | Mark water level at start of flood testing to verify for any leaks/drops in water level. Attach before and after photos with time/date stamps.
checkpoint-status |  |  | checkpoint | Verification of Flood Testing Results - Any leaks Found?
text | b66d49bd-0563-5fc7-a413-f8ff393fdd19 |  | textbox | Note if any leaks identified (if so re-membrane and test)?
holdpoint |  |  | signoff | Contractor to sign-off on flood testing results once passed.
checkpoint-status |  |  | checkpoint | Attach subcontractor ITP
checkpoint-group |  |  | section | Sign-off
checkpoint-status |  |  | checkpoint | Subcontractor Signoff
holdpoint |  |  | signoff | Subcontractor Sign-off
checkpoint-status |  |  | checkpoint | SDC Signoff
holdpoint |  |  | signoff | SDC Sign-off
checklist-sectioned |  |  | checklist | Level Compliance |  |  |  |  | Yes | Level Compliance | 7ffb8cab-1311-4a13-9264-3a88544e522e
checkpoint-group |  |  | section | Fire Rated Plasterboard Compliance
checkpoint-status |  |  | checkpoint | Attach Manufacturer Inspection Report for the level
checkpoint-status |  |  | checkpoint | Confirm all outstanding items have been closed out
holdpoint |  |  | signoff | HOLD POINT - Attach Close-out Confirmation & Photos
checkpoint-group |  |  | section | BCA Compliance
checkpoint-status |  |  | checkpoint | Attach BCA consultant fire compliance inspection report for the level
checkpoint-status |  |  | checkpoint | Confirm all outstanding items have been closed out
holdpoint |  |  | signoff | HOLD POINT - Attach Close-out Confirmation & Photos
checkpoint-group |  |  | section | Acoustic Compliance
checkpoint-status |  |  | checkpoint | Attach Acoustic Consultant Inspection Report for the level
checkpoint-status |  |  | checkpoint | Confirm all outstanding items have been closed out
holdpoint |  |  | signoff | HOLD POINT - Attach Close-out Confirmation & Photos
checklist-sectioned |  |  | checklist | Services Rough-in - Electrical |  |  |  |  | Yes | Services Rough-in - Electrical | 843c80d5-12db-4483-9933-365dd095463a
checkpoint-group |  |  | section | Fire Rating
checkpoint-status |  |  | checkpoint | Check 1m benchmark has been set and agreed for services installation heights
label | 4e3ce8a8-9ce9-5cef-a656-11fa8be01a3c |  | note | Attach Photo of benchmark for reference
checkpoint-status |  |  | checkpoint | Ensure services are installed neatly through fire rated walls
label | fd9c3fdc-76d2-53ee-846b-a52118975b88 |  | note | Sheet areas of wall where services are to penetrate first (ie; above entry door), then install services to avoid non-compliances with sheeting.
checkpoint-status |  |  | checkpoint | Confirm any cable/conduit penetrating the fire rated walls are sealed on both sides with intumescent fire mastic (conned around cable/penetration)
checkpoint-status |  |  | checkpoint | Confirm at least 100mm separation between cables/conduits and any other services (200mm form fire dampers) where passing through a fire rated wall.
checkpoint-status |  |  | checkpoint | Intubatt (Fibre Board Products) used with services
boolean | 385345a0-a743-5d42-83ba-477a94a07c5e |  | tickbox | Ensure fixings at 200mm centres and washers are visible
boolean | 9dafebea-a33a-55cf-9b8a-b5889507b074 |  | tickbox | Ensure exposed edges of the board are covered with sealant to prevent deterioration over time
boolean | 02706e39-ed99-5d49-85bc-15945a9790c1 |  | tickbox | Ensure where service penetrates the board that fire wrap and sealant are used to close any gaps
boolean | bdae01cc-e8a8-5eb2-8465-207f66b75b77 |  | tickbox | Attach photos of compliant installation
checkpoint-status |  |  | checkpoint | Retro-Fit Fire Collars - Ensure correct size collar for service and that hole around services is sealed (coned) with fire rated sealant prior to installation.
label | d853ec94-3817-5672-9c36-d3168d73d544 |  | note | Ensure an Acrylic Sealant is used (not intumescent sealant) when installing around fire collars
checkpoint-status |  |  | checkpoint | Fire Rated GPO Boxes - Check installation within fire rated walls is compliant
label | 07bb1f9a-1649-54b7-89cd-670771e3b598 |  | note | Max 3mm gap allowed between plasterboard lining and edge of box. Ensure gap is sealed with fire rated caulking.
checkpoint-status |  |  | checkpoint | Confirm statuatory fire labels are installed adjacent services prior to sheeting. Attach photos for record.
checkpoint-group |  |  | section | Electrical Services
checkpoint-status |  |  | checkpoint | Confirm Latest Electrical Lighting & Power Plans are being used with Contractor (Refer Aconex)
text | c936bcc2-fc62-515b-bdfa-2fbd6b8a63ab |  | textbox | Record Plan numbers and revisions
checkpoint-status |  |  | checkpoint | Typical Electrical Services Rough-in Heights - Spot check each room as follows (centre line of fitting):
label | e38d88b2-f6cc-527d-89cd-dfd95231f469 |  | note | Internal GPO's/TV/DATA Points - 300mm AFFL
label | 83e1d7ae-d1af-5e22-b3e0-c27aefbb90c3 |  | note | Internal Light Switches - 1000mm AFFL
label | 05194d08-8822-5c8d-b757-fd1dd2386673 |  | note | Home Automation Screen - 1500mm AFFL
label | 07ae4def-0457-5657-b758-168ebf2a3f9e |  | note | External Balcony GPO - 650mm AFFL
label | f1026381-e22b-551b-8691-8ddf10fed91d |  | note | External Balcony Lights - 2100mm AFFL
label | 90b73c89-f861-5dd9-af22-f2a8ced377ba |  | note | Interface with Joinery Elements - Check against joinery shop drawings to ensure correct location/height
text | 13cca90b-b37e-5196-ad7e-be3a4894a604 |  | textbox | Record any deviations from typical heights and reasons why.
checkpoint-status |  |  | checkpoint | Services Installations - Complete visual check that all wiring for GPO/DATA/TV Points & Light Switches are installed
text | dd35c79b-b8fb-5014-9cc0-cd387c0be03a |  | textbox | Record any deviations from plans and reasons why.
checkpoint-status |  |  | checkpoint | Confirm correct allocation of lighting quantities per architectural RCP drawings and rough-in installed
checkpoint-status |  |  | checkpoint | Confirm NBN cables have been roughed in to correct location & no 90 degree bends in conduit, sweeping bends only.
checkpoint-status |  |  | checkpoint | Confirm distribution board has been roughed in to correct location
checkpoint-status |  |  | checkpoint | Confirm intercom & home automation wiring in place
checkpoint-status |  |  | checkpoint | Confirm power provisions to all kitchen appliances per kitchen shop drawings
checkpoint-status |  |  | checkpoint | Confirm minimum 50mm separation between power and data cables (or physical insulated barrier installed). Check minimum 25mm separation between power and gas/water services.
checkpoint-status |  |  | checkpoint | Confirm Installation of earthquake bracing as required by standard
checkpoint-status |  |  | checkpoint | Confirm adaptable apartment future provisons installed if applicable
checkpoint-status |  |  | checkpoint | Services Checking Consultant Inspection Completed prior to Sheeting
holdpoint |  |  | signoff | HOLD POINT - Confirm Inspection items closed & Photos attached
checkpoint-status |  |  | checkpoint | Attach Subcontractor ITP
checkpoint-group |  |  | section | Sign-off
checkpoint-status |  |  | checkpoint | Subcontractor Signoff
holdpoint |  |  | signoff | Subcontractor Sign-off
checkpoint-status |  |  | checkpoint | SDC Signoff
holdpoint |  |  | signoff | SDC Sign-off
checklist-flat |  |  | checklist | SDC-TMP-CON-ITP-009 - 3 – RC Slab on Grade |  |  |  |  | Yes | SDC-TMP-CON-ITP-009 - 3 – RC Slab on Grade | 9514316c-69f4-4990-9d8f-e0a3152c40e8
checkpoint-status |  |  | checkpoint | Prior to Reinforcement: Attach Markup to confirm proposed pour zone
checkpoint-status |  |  | checkpoint | Prior to Reinforcement: Ensure detailed excavation is complete (Attach Excavation Contractor’s ITP)
checkpoint-status |  |  | checkpoint | Prior to Reinforcement: Confirm inground drainage and pit works has been completed and backfilled (Attach photos/confirmation)
checkpoint-status |  |  | checkpoint | Prior to Reinforcement: Confirm that substation earthing rods have been drilled, as AS Built red line survey (If applicable)
checkpoint-status |  |  | checkpoint | Prior to Reinforcement: Confirm min 100mm subsoil drainage has been installed as per geotechnical requirements (attach contractor’s ITP)
checkpoint-status |  |  | checkpoint | Prior to Reinforcement: Confirm Surveyor has provided set outs/ benchmarks (Attach survey)
checkpoint-status |  |  | checkpoint | Prior to Reinforcement: Confirm vapor barrier installed over subbase (Attach photos and confirm signed off by concrete place ITP)
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour: Attach formwork contractor’s ITP (including setdowns, hobs, Construction/key/movement joints, ect.)
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour: Attach Structural Engineers inspection report
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour: Attach Verification that structural engineer’s inspection report has been closed out to allow concrete pour (Attach Photos)
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour: Attach reinforcement contractor’s ITP
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour: Attach Hydraulic ITP (inground drainage and pipework)
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour: Attach Electrical ITP (Cast in conduits – if applicable)
checkpoint-status |  |  | checkpoint | During Concrete Pour: Attach Concrete place contractor’s ITP (including Ableflex)
checkpoint-status |  |  | checkpoint | After Concrete Pour: Confirm falls have been completed in concrete pour in accordance to architectural drawings
checkpoint-status |  |  | checkpoint | After Concrete Pour: Attach Concrete test results and confirm compliance with engineer requirements
checkpoint-status |  |  | checkpoint | After Concrete Pour: Confirm saw cuts installed as per engineer’s drawings
checkpoint-status |  |  | checkpoint | Signoffs: Site Engineer to signoff ITP has been completed
holdpoint |  |  | signoff | Signoff by Site Engineer
checkpoint-status |  |  | checkpoint | Signoffs: Project Engineer to review and confirm ITP has been completed
holdpoint |  |  | signoff | Signoff by Project Engineer
checklist-sectioned |  |  | checklist | Waterproofing - Balcony Areas |  |  |  |  | Yes | Waterproofing - Balcony Areas | 9c7db656-e30d-4bd9-a49c-805de47e7cd9
checkpoint-group |  |  | section | Prior to Works
checkpoint-status |  |  | checkpoint | Substrate - Review to ensure any voids or protrusions are filled and removed to provide smooth surface.
label | 19e171da-1973-52c2-824f-539b46134bbe |  | note | Also ensure substrate is clean and free of any water, dust and debris.
checkpoint-status |  |  | checkpoint | Verify with Plumber that their drainage works are completed prior to membrane commencement.
label | c38f5a78-fbaa-5942-bb3b-0098c6b8d89a |  | note | Attach Subcontractor ITP where relevant.
checkpoint-status |  |  | checkpoint | Concrete Cracks - Review substrate for any cracking. Up to 2mm cracks fill with Polyurethane sealant. Above 2mm to be chased, cleaned and primed, then sealant applied.
checkpoint-status |  |  | checkpoint | Falls - Review concrete substrate to ensure min. 1:100 falls achieved and falling to floor wastes.
checkpoint-status |  |  | checkpoint | Floor Wastes - Review puddle flange to ensure it is recessed and flush with floor substrate. The PVC flange should be lightly sanded to promote membrane adhersion.
label | 37a01a3d-dff5-5797-ad34-a52868febae2 |  | note | Also check internal of floor wastes to ensure free from debris prior to waterproofing.
checkpoint-status |  |  | checkpoint | Overflow Points - Review overflow points are installed correctly per plans (min. x2 per balcony) and pipework is proud of slab surface by min. 30mm.
label | 99ac1ea6-a0b1-57ef-80a9-9aabbba87852 |  | note | Check overflow points are connected below to curtain wall façade and not blocked.
checkpoint-status |  |  | checkpoint | Substrate Moisture Content - Verify that waterproofing contractor has tested moisture content of concrete substrate and is happy to proceed with works (ie; below 5%).
text | 360a10fa-ca0b-580b-befd-bb7ec6e8057a |  | textbox | Record moisture meter reading.
holdpoint |  |  | signoff | Subcontractor to sign-off on substrate.
checkpoint-status |  |  | checkpoint | Waterproofing Materials - Confirm approved waterproofing materials are being used for the works.
label | 634c5298-97a0-541f-ac32-71b2c07ab2f7 |  | note | Waterproofing Primer: Nitoprime 320PU. Waterproofing Membrane: Fosroc Polyurea WHE 110 + DULUX Luxafloor PTX
checkpoint-status |  |  | checkpoint | Record product batch/serial numbers for tracking of any future defects.
text | 7dafab42-df09-5cb4-9548-4b0f4c395d76 |  | textbox | Batch/Serial Numbers:
checkpoint-status |  |  | checkpoint | Membrane Supplier Inspection - Confirm membrane supplier inspection of substrate to ensure prepared in accordance with specification.
label | 195177ea-ef02-513e-ba70-f0dc82125b2b |  | note | Attach record of inspection where applicable.
checkpoint-group |  |  | section | During Works
checkpoint-status |  |  | checkpoint | Sealant/Bond Breakers - Confirm applied to all wall/floor and wall/wall junctions as well as around any services penetrations and wall fixings (ie; screw fixings, etc…). Surfaces should be primed prior to application of sealant/bond breakers.
label | 54a0fd2f-1518-50bf-a8a4-0b9b238e0719 |  | note | Waterproofing Sealant: Nitroseal PU250 or PU400 (Check to ensure gaps not more than 20mm wide/deep for sealant application. Min. fillet of sealant should be 5mm). Bond Breaker: Nitroband Tape (ensure surface primed prior to install and overlapping at joints 150mm each side).
checkpoint-status |  |  | checkpoint | Floor Membrane - Confirm 1x coat of primer (Nitoprime 320PU - 1hr curing time prior to membrane application) & x2 coats of membrane (Fosroc Polyurea WHE 110 + DULUX Luxafloor PTX - requires 24hrs curing time between coats).
label | b7856673-7c18-51e6-ba41-b57c6ed2557f |  | note | Attach progress photos of completed membrane works. Ensure no membrane on top of exposed elements (ie; curtain wall, etc…). Ensure balcony access is barricaded with signage to prevent damage from other trades.
checkpoint-status |  |  | checkpoint | Membrane Skirting Upturn - ensure membrane applied 150mm up wall from structural floor level per standards.
checkpoint-status |  |  | checkpoint | Wall Membrane - confirm membrane applied to wall substrate where taps installed (under finishes) and around curtain wall to slab junctions.
label | fb553774-6bab-5687-b702-c47629beec7c |  | note | Attach progress photos of completed membrane works.
checkpoint-group |  |  | section | After Works
checkpoint-status |  |  | checkpoint | Flood Testing: Block floor waste points & overflows and fill balcony to internal hob height and leave for 24hrs.
label | 5ebf07ee-48f4-5ba4-bee5-89912732e6bb |  | note | NOTE: Verify that final coat of membrane has had 24hrs curing time prior to Flood testing.
label | d72ddf45-f8d7-5c08-9d18-6b6e2ac3f029 |  | note | Mark water level at start of flood testing to verify for any leaks/drops in water level. Attach before and after photos with time/date stamps.
checkpoint-status |  |  | checkpoint | Verification of Flood Testing Results - Any leaks Found?
text | d1c5791e-407f-51c0-b95a-0027665c89a0 |  | textbox | Note if any leaks identified (if so re-membrane and test)?
holdpoint |  |  | signoff | Contractor to sign-off on flood testing results once passed.
checkpoint-status |  |  | checkpoint | Attach subcontractor ITP
checkpoint-group |  |  | section | Sign-off
checkpoint-status |  |  | checkpoint | Subcontractor Signoff
holdpoint |  |  | signoff | Subcontractor Sign-off
checkpoint-status |  |  | checkpoint | SDC Signoff
holdpoint |  |  | signoff | SDC Sign-off
checklist-flat |  |  | checklist | SDC-TMP-CON-ITP-006 - 4 – Pits, Pads and Strip Footings |  |  |  |  | Yes | SDC-TMP-CON-ITP-006 - 4 – Pits, Pads and Strip Footings | aaa9ea4f-9e04-4b4c-902d-5cdffa5f8cfd
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Attach markup structural plan identifying footings relevant to this ITP
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Confirm surveyor has provided setout for pad footing excavation (attach survey setout plan)
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Attach Geotech engineer bearing certification confirming approval of substrate complying with engineer’s requirements
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Confirm that either pre- applied membrane or Forecoin plastic has been installed to comply with electrolysis study (attach photos)
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Confirm excavation is free of debris and loose materials to walls and floor prior to handover (attach photos)
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Attach reinforcement contractors ITP (incl AEFAC Accredited installer signoff of any drill and epoxy bars to comply with structural engineer details)
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Confirm wall starter bars have been installed in accordance with surveyor setout and architectural outline drawings.
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Attach signoff from CFT Column contractor inspection approval of starter bars, castins and hold down bolts
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Attach waterproofing contractors ITP confirm tanking waterproofing and PVC water bar has been installed(attach waterproofing ITP)
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Confirm that waterproofing consultant has inspected works and defects closed out
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Attach hydraulic contractor's ITP confirming completion of any cast in as per hydraulic drawings
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Attach formwork ITP/Signoff that all formwork to kicker has been completed (sump, hobs, edge boards etc)
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Attach structural engineer’s inspection report
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Attach verification that structural engineer’s inspection report has been closed out to allow concrete pour
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Confirm concrete place contractor's order complies with engineer's strength of concrete, waterproofing additive and testing requirements
checkpoint-status |  |  | checkpoint | Prior to Concrete Place - Attach photo of formwork setting the level for concrete place contractor
checkpoint-status |  |  | checkpoint | Prior to Concrete Pour - Attach concrete place contractor’s ITP
checkpoint-status |  |  | checkpoint | After Concrete Pour - Confirm RL of poured footing complies with design RLs
checkpoint-status |  |  | checkpoint | After Concrete Pour - Confirm integrals falls have been completed in concrete to sump
checkpoint-status |  |  | checkpoint | After Concrete Pour - Attach concrete test results and confirm compliance with engineer requirements
checkpoint-status |  |  | checkpoint | Signoffs - Site Engineer to signoff ITP has been completed
holdpoint |  |  | signoff | Signoff by Site Engineer
checkpoint-status |  |  | checkpoint | Signoffs - Project Engineer to review and confirm ITP has been completed
holdpoint |  |  | signoff | Signoff by Project Engineer
checklist-sectioned |  |  | checklist | 01C-SDC-TMP-CON-ITP-007a - 3 - Jumpform |  |  |  |  | Yes | 01C-SDC-TMP-CON-ITP-007a - 3 - Jumpform | af2efa61-0e19-4197-9220-c65768e87a9c
checkpoint-group |  |  | section | Prior to Reinforcement
checkpoint-status |  |  | checkpoint | Confirm Jump No Seq and bottom and top RLs of proposed pour
text | fc09e239-cb41-5229-8b1b-6ae5ce6205f1 |  | textbox | Jump No Sequence
text | 75617b45-fc0d-579f-9246-d6705d97d9f2 |  | textbox | Bottom of Proposed Wall RL
text | 8179fb56-38cc-5e32-9066-d62c3cd214d9 |  | textbox | Top of Proposed Wall RL
checkpoint-status |  |  | checkpoint | Surveyor to complete survey of concrete walls below to confirm if walls need to be adjusted. Attach confirmation survey has been issued to formwork contractor via Aconex
text | acbaf781-9d79-57fa-9ed0-83bbeccd16c1 |  | textbox | Aconex Correspondence No.
checkpoint-status |  |  | checkpoint | Lift Requirements - Review formwork blockouts for lift openings and door thresholds in accordance with architectural elevations and lift shop drawings
checkpoint-status |  |  | checkpoint | Formwork Requirements - Confirm that all reboxes, couplers, shear key pockets and cast in plates to internal shutter as per structural engineer detail
checkpoint-status |  |  | checkpoint | Attach Sign Off from form worker contractor confirming all works completed and clear access for handover to steel fixers
checkpoint-group |  |  | section | Prior to Closing Shutters
checkpoint-status |  |  | checkpoint | Lift Requirements - Confirm any block out / penetrations required for lift buttons and indicators has been cast in by Form Worker
checkpoint-status |  |  | checkpoint | Confirm all outside reboxes & couplers are installed to required SSL + cover levels
checkpoint-status |  |  | checkpoint | Attach electrical contractors ITP to confirm any required conduit cast ins are completed
checkpoint-status |  |  | checkpoint | Attach reinforcement installer’s ITP
checkpoint-status |  |  | checkpoint | Reinforcement Checks (Refer Structural Engineers Drawings for Reference):
label | 3aabcaef-75b7-543f-9097-8ce3fe8da03c |  | note | Reinforcement cover sufficient
label | 5db9e275-7014-5d2c-9883-66249edf6d5d |  | note | Lap Length of bars sufficient
label | c270377a-5ff0-5bff-85ee-fcbf436be1aa |  | note | Starter bar length to next pour correct
label | 6e0fdbe0-6e0e-59e1-8ef2-ce14ae5842d5 |  | note | Lace bars installed to reboxes
checkpoint-status |  |  | checkpoint | Attach structural engineer’s inspection report
checkpoint-status |  |  | checkpoint | Attach verification that structural engineer’s inspection report has been closed out to allow concrete pour
checkpoint-status |  |  | checkpoint | Attach photos of all works completed prior to closing shutters
checkpoint-group |  |  | section | During Concrete Pouring
checkpoint-status |  |  | checkpoint | Confirm Concrete ordered is correct
text | 69fee95c-c606-5464-a090-2d97dcf397c7 |  | textbox | MPa/mix design
checkpoint-status |  |  | checkpoint | Confirm pour height with concrete Contractor prior to pouring
checkpoint-status |  |  | checkpoint | Attach form worker’s jumpform ITP
checkpoint-status |  |  | checkpoint | Attach concrete place contractor’s ITP
checkpoint-status |  |  | checkpoint | Confirm concrete tester onsite to take samples and ensure correct pour location is recorded
checkpoint-group |  |  | section | Prior to Jumping
checkpoint-status |  |  | checkpoint | Attach concrete test result to confirm min 15 MPa has been reached
checkpoint-status |  |  | checkpoint | Attach form worker’s Permit to Energise Jumpform.
label | 2ed66936-a16d-5a74-b215-f797fe5c331a |  | note | Note exclusion zone below and all penetrations to be blocked up and secure and any temporary services (hydraulic/electrical/static line) disconnected inside trailing decks
checkpoint-group |  |  | section | After Jumping
checkpoint-status |  |  | checkpoint | Form Worker to ensure that all z bar holes and jumpform pockets within the lift shaft has been patched and infilled in accordance with structural engineer drawings
checkpoint-status |  |  | checkpoint | Attach concrete test results 28d and confirm compliance with engineer requirements
checkpoint-status |  |  | checkpoint | Permit to Re-seat jumpform received (attach to ITP)
checkpoint-status |  |  | checkpoint | Surveyor to survey finished concrete walls (attach as-built to ITP)
holdpoint |  |  | signoff | Final ITP Review & Sign-off by Project Engineer
checklist-sectioned |  |  | checklist | Services Rough-in - Fire |  |  |  |  | Yes | Services Rough-in - Fire | d34f8106-ca46-4748-989b-55dd6e05b9c6
checkpoint-group |  |  | section | Fire Rating
checkpoint-status |  |  | checkpoint | Check 1m benchmark has been set and agreed for services installation heights
label | 702975bf-4441-551f-9e5a-f03921e79336 |  | note | Attach Photo of benchmark for reference
checkpoint-status |  |  | checkpoint | Ensure services are installed neatly through fire rated walls
label | d41cbda9-7f15-564f-97ee-294853e4f51a |  | note | Sheet areas of wall where services are to penetrate first (ie; above entry door), then install services to avoid non-compliances with sheeting.
checkpoint-status |  |  | checkpoint | Confirm any cables penetrating the fire rated walls are sealed on both sides with intumescent fire mastic (conned around cables)
checkpoint-status |  |  | checkpoint | Confirm at least 100mm separation between fire services and any other services (200mm form fire dampers) where passing through a fire rated wall.
checkpoint-status |  |  | checkpoint | Intubatt (Fibre Board Products) used with services
boolean | e0baf51d-b07b-5442-ae76-1856584df488 |  | tickbox | Ensure fixings at 200mm centres and washers are visible
boolean | a2281e37-fa0f-5c19-8425-231cb9c42e3b |  | tickbox | Ensure exposed edges of the board are covered with sealant to prevent deterioration over time
boolean | 5a6bed70-a200-5eaf-bf7b-205c6f1ffa14 |  | tickbox | Ensure where service penetrates the board that fire wrap and sealant are used to close any gaps
boolean | dbfb4beb-48c9-5956-b6e5-7d2155627076 |  | tickbox | Attach photos of compliant installation
checkpoint-status |  |  | checkpoint | Retro-Fit Fire Collars - Ensure correct size collar for service and that hole around services is sealed (coned) with fire rated sealant prior to installation.
label | bb5fbef9-4589-5fc5-837b-002ef8b45356 |  | note | Ensure an Acrylic Sealant is used (not intumescent sealant) when installing around fire collars
checkpoint-status |  |  | checkpoint | Check copper or steel pipes penetrating fire walls have fire wrap installed with at least 3 stainless cable ties.
label | 38cab4e9-51ce-5fd5-b296-706c0eca953c |  | note | Ensure fire caulking is used to close any gaps around the pipe (coned) at the wall penetration prior and post wrap installation.
checkpoint-status |  |  | checkpoint | Confirm statuatory fire labels are installed adjacent services prior to sheeting. Attach photos for record.
checkpoint-group |  |  | section | Fire Services
checkpoint-status |  |  | checkpoint | Confirm Latest Wet & Dry Fire Plans are being used with Contractor (Refer Aconex)
text | e0608021-f10c-55a7-9330-e0e9747b8568 |  | textbox | Record Plan numbers and revisions
checkpoint-status |  |  | checkpoint | Service Installations - Complete visual check to confirm all Wet & Dry fire services rough-in is installed per plans (also reference Architectural RCP).
text | 59ac44f3-5e35-5ffa-9952-45a611fec6e6 |  | textbox | Record any deviations from plans and reasons why.
checkpoint-status |  |  | checkpoint | Confirm all fire sprinkler pipes are charged so any leaks can be identified now and in the future.
checkpoint-status |  |  | checkpoint | Confirm any sprinkler pipes penetrating to the balcony are sealed at the external wall/window subhead.
checkpoint-status |  |  | checkpoint | Review sprinkler head and detector placement to ensure there are no obstructions to coverage.
checkpoint-status |  |  | checkpoint | Confirm that pipework pressure, choke and hydrostatic testing has been completed.
label | 62133283-1757-5944-b36f-444d94e0e94a |  | note | Pipes should be left under test for a minimum of 2hrs at 1400kPa. Provide time stamped before and after photos where relevant of pressure gauges.
holdpoint |  |  | signoff | HOLD POINT - Contractor to sign off on testing. Attach test sheet
checkpoint-status |  |  | checkpoint | Confirm adaptable apartment future provisons installed if applicable
checkpoint-status |  |  | checkpoint | Services Checking Consultant Inspection Completed prior to Sheeting
holdpoint |  |  | signoff | HOLD POINT - Confirm Inspection items closed & photos attached
checkpoint-status |  |  | checkpoint | Attach Subcontractor ITP
checkpoint-group |  |  | section | Sign-off
checkpoint-status |  |  | checkpoint | Subcontractor Signoff
holdpoint |  |  | signoff | Subcontractor Sign-off
checkpoint-status |  |  | checkpoint | SDC Signoff
holdpoint |  |  | signoff | SDC Sign-off
checklist-sectioned |  |  | checklist | 101C-SDC-TMP-CON-ITP-007 - 2- Concrete Columns Walls Verticals |  |  |  |  | Yes | 101C-SDC-TMP-CON-ITP-007 - 2- Concrete Columns Walls Verticals | f049abf5-edd6-416c-83b9-121dd092777f
checkpoint-group |  |  | section | Prior to Concrete Pour
checkpoint-status |  |  | checkpoint | Current Drawing Status - Refer Aconex Document Register for latest approved Shop Drawings. Record drawings used at time of pour on ITP.
text | be34bdae-f703-5862-8415-cd17d0848cba |  | textbox | Architectural Drawings
text | 98c3cdb3-0c8d-5188-bc6f-4dbea03affac |  | textbox | Structural Drawings
checkpoint-status |  |  | checkpoint | Ensure survey of column/wall positions are completed prior to commencing formwork
label | 83678975-8dac-5a3c-9344-1bc226ae18a7 |  | note | Attach surveyors as-built records to ITP
checkpoint-status |  |  | checkpoint | Reinforcement - Check Starter bars from previous pour installed in correct position (compare against survey points)
checkpoint-status |  |  | checkpoint | Reinforcement - Check for correct bar sizes and lap lengths between starter bars (top & bottom)
checkpoint-status |  |  | checkpoint | Cast-in Services - Electrical subcontractor to sign off that all Conduits / block-outs are installed in accordance with the design. Attach Contractors ITP
checkpoint-status |  |  | checkpoint | Cast-in Services - Hydraulics subcontractor to sign off that all Conduits / block-outs are installed in accordance with the design Attach Contractors ITP
checkpoint-status |  |  | checkpoint | Cast-in Services - Mechanical subcontractor to sign off that all Conduits / block-outs are installed in accordance with the design Attach Contractors ITP
checkpoint-status |  |  | checkpoint | Cast-in Services - Fire Subcontractor to sign off that all Conduits / block-outs are installed in accordance with the design Attach Contractors ITP
checkpoint-status |  |  | checkpoint | Cast-in Services - Security Subcontractor to sign off that all Conduits / block-outs are installed in accordance with the design
checkpoint-status |  |  | checkpoint | Confirm strength and mix design of concrete ordered with subcontractor prior to pour
text | 83416d4e-588a-5834-bfc7-cca8d9297375 |  | textbox | Concrete Mix Design:
checkpoint-status |  |  | checkpoint | Structural Engineer Sign-off - Foreman and subcontractor to sign off engineer’s report to verify that all work to be rectified was checked for compliance prior to pour
label | c4b3574e-3e4d-5d2d-9f51-2682acf11262 |  | note | Attach engineers inspection report and verification of rectification items being closed out.
checkpoint-status |  |  | checkpoint | Formwork Compliance - Confirm formwork is checked to achieve Class 2 finish to concrete:
boolean | 1c7ffae4-da3d-5f41-9776-0dc689ab6e2a |  | tickbox | Formwork is clean and free of debris
boolean | 9e437d63-5f9b-56ad-849a-dc1f97c98f02 |  | tickbox | No lipping of formwork between sheets
boolean | cc5eedd9-562a-5a3c-bbf8-35089fa64818 |  | tickbox | Fillets installed at all corners
boolean | f3d9af63-113f-5fa7-a734-818ad2f60b11 |  | tickbox | Form ties are installed at even spacing
boolean | 6b22574f-5639-5df7-bb94-dd6682f5e4e7 |  | tickbox | Check for correct reo cover at shutters
boolean | c78823d8-b08f-5d92-b36a-9adb285dda2f |  | tickbox | Splayed columns are at correct degrees per Architectural/Structural drawings
checkpoint-status |  |  | checkpoint | Area cleaned of all excess formwork, sawdust at base of columns, reo, and debris prior to pour
checkpoint-status |  |  | checkpoint | Attach formworkers ITP for column and wall formworking
checkpoint-status |  |  | checkpoint | Attach Steelfixers ITP for Column and wall reinforcement
checkpoint-group |  |  | section | During Concrete Pour
checkpoint-status |  |  | checkpoint | Concrete Placement Checklist
boolean | ef0d10f5-ca0a-5fbc-b5a2-88bcb5fc011a |  | tickbox | Structural Engineer & Formwork Engineer Sign-off Received
boolean | 4d43f38a-5927-5625-9cee-50b55ef49554 |  | tickbox | Confirm Delivery Docket References correct mix design
boolean | 6afa1aba-7909-5a62-8e46-39ab8780b801 |  | tickbox | Plant and Equipment checklist completed on concrete pump and lines
boolean | 75c379bc-ae8f-53e8-84f9-d4849bf5d7c7 |  | tickbox | Confirm concrete tester on-site and correct location of concrete pour provided to them for test results
label | 8eae3c07-4137-513b-83dc-1b73460911d1 |  | note | 7, 28 & 56 day compressive test results to be issued by batch plant
label | 0ba68840-1f2c-5ee0-8575-28464266daca |  | note | Batch plant to issue monthly dry shrinkage test results
checkpoint-status |  |  | checkpoint | Ensure a representative from each of the following is on site and witnessing the pour:
boolean | cfa21684-6574-52b3-ac38-ddba1bcb52d1 |  | tickbox | Form Worker
boolean | f0f49649-9514-5fe7-8657-bb359e1b359f |  | tickbox | Electrician
boolean | aab7c095-1bf7-539c-8343-065ddf77ee46 |  | tickbox | Plumber
checkpoint-status |  |  | checkpoint | Ensure only rubber tipped vibrators are used and care is taken not to damage shutters
checkpoint-status |  |  | checkpoint | Ensure Form Worker labour is available to clean up any slurry runs at bottom of walls, immediately after pour for off form finishes.
checkpoint-status |  |  | checkpoint | Attach Concrete Place contractors ITP
checkpoint-group |  |  | section | After Concrete Pour
checkpoint-status |  |  | checkpoint | Curing - Approved curing compound to be applied to columns following removal of formwork as required.
checkpoint-status |  |  | checkpoint | Confirm tolerance of finished concrete surfaces:
label | bef63090-e05d-52a2-9126-1efb628a4c99 |  | note | 5mm+/- in correct position
label | 97bd183b-4da4-5ec2-82e7-5e9c5d97eab4 |  | note | 5mm +/- from 3.0m straight edges.
label | 0e3449f9-ff48-5dad-aaa5-565606e686e0 |  | note | 5mm +/- from plumb.
checkpoint-status |  |  | checkpoint | As-Built Survey - Confirm Surveyor is out next day to carry out survey of finished concrete. Attach As Built Survey Plan
checkpoint-status |  |  | checkpoint | Concrete Test Results - Obtain all concrete test results. Confirm strength achieved after:
text | cd3ad7e9-18da-54e4-a3e6-dad00be42a1c |  | textbox | 7 Days MPa
text | 27a71ddb-793f-5e8c-a11c-83069ad213c8 |  | textbox | 28 Days MPa
text | 10ab75ae-4cdd-5660-a6b6-1d88aadbe99b |  | textbox | 56 Days MPa
checkpoint-status |  |  | checkpoint | All non-conformances closed out
holdpoint |  |  | signoff | Final ITP Review & Sign-off by Project Engineer