## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | LP Main Roof Testing Script |  |  |  |  | Yes | LP Main Roof Testing Script | 03b48139-b8c9-4a16-90e9-49e7b17f49d4
checkpoint-status |  |  | checkpoint | Visual Inspection
text | 484ee0d5-ca16-5568-baa2-85e702fd176e |  | textbox | Earth Connection Ref No.
text | c8fa53bf-3e1b-5033-bf25-a85e90dafe85 |  | textbox | Connection Type
text | 635b4096-dd9b-5e0c-bcd2-cbb16b80116a |  | textbox | Method
checkpoint-status |  |  | checkpoint | Ductor Test Performed With Satisfactory Result. With Any Result Deviating By More Than 50% From Alike Connections Investigated
text | cf42838c-41a4-55ae-ab31-230ea2f7d777 |  | textbox | Connection Point Tested to
text | b661b6d7-4bfd-5d27-b2a5-29f068cd2b09 |  | textbox | Low Ohm Resistance Test Result - Ductor Test (Ohms)
select | c760860d-0cd4-5f70-be19-02365e9d0490 |  | dropdown | Test Equipment Used | Meggar DLRO10X
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 23ec09b2-4d14-5abb-bb74-bcc6fd6ab5a0 |  | textbox | Tested By
text | 671a8746-d865-5f8e-b7bd-f628989398ec |  | textbox | Witnessed By
text | 79e9fd38-f843-5a68-a16c-84abc102ce2b |  | textbox | Date
checklist-flat |  |  | checklist | XFM/GEN Post Livening |  |  |  |  | Yes | XFM/GEN Post Livening | 0a6330e6-3c27-4ca5-b882-b811ad7faef1
checkpoint-no-status |  |  | checkpoint | Details
label | 67f11168-4d41-54f0-9e8a-381f5ede8c8b |  | note | Supply Cable Type - XLPE
select | a772e569-452d-5451-91e6-5a3d0a318532 |  | dropdown | Supply Cable Size | 240mm2, 400mm2
label | 0adb13a2-f5b6-5dd6-a7b4-977017714e66 |  | note | Earth Cable Type - PVC
label | 859b0164-0b83-57ea-94ce-43cb168b7860 |  | note | Earth Cable Size - 150mm2
select | f22a68fb-0fab-5ea0-bbd0-b886cab45ce8 |  | dropdown | Number Of Parallel Sets Of L1, L2, L3 And N | Three, Six, Nine
text | b1a52d07-b10c-5215-995b-8ae5d2918307 |  | textbox | Number Of Parallel Sets Of E
label | 87412bdb-2ccc-53e2-a461-2760c36ea72b |  | note | Breaker Size At MSB - 5000A
text | 068eb427-fc35-517b-84e4-6574ac6e93db |  | textbox | Record Size Breaker Is Set To
text | 8a71e945-911a-59fd-a61d-9c8e93c563ee |  | textbox | Record KA Rating Of Breaker
checkpoint-status |  |  | checkpoint | Test And Record Voltage Readings
text | 0f0df169-e820-54af-9cbb-c5e490128ec1 |  | textbox | Red To White
text | e2caa82c-a1f1-531a-9020-1688a685b3f9 |  | textbox | Red To Blue
text | 704578df-49fe-5572-bc30-53c3588a2608 |  | textbox | Red To Neutral
text | bf8f68b8-8e33-5645-a366-648f228f70a0 |  | textbox | Red To Earth
text | 856eefe8-874e-57ae-a76a-6fb83d9efdc5 |  | textbox | White To Blue
text | 8d72d90c-3ad8-5a63-8905-d6c7698f57cf |  | textbox | White To Neutral
text | e1dffafe-6e39-5368-be43-e2db3db8f032 |  | textbox | White To Earth
text | 99825529-e9b5-544e-98b1-1f6637165f47 |  | textbox | Blue To Neutral
text | 34aaf42a-4402-5ee9-8a39-442d7421c329 |  | textbox | Blue To Earth
text | 14c4164f-79ab-5cdb-b3e2-dfb9e3299c6c |  | textbox | Neutral To Earth
checkpoint-status |  |  | checkpoint | Confirm Polarity Is Correct
checkpoint-status |  |  | checkpoint | Perform and Record The Following
text | f47f2a36-a5c5-59f3-b795-6c42e3b4a061 |  | textbox | Red To Earth EFLI
text | c190b21a-3bf4-5e40-9714-366cdf5c7038 |  | textbox | Red To Earth PFC
text | 78df9e6d-5dde-5e5e-86c0-6048aee31718 |  | textbox | White To Earth EFLI
text | 1ab823f4-602d-51bc-bafe-e9259df35294 |  | textbox | White To Earth PFC
text | 5f4464e9-4c0b-588f-bb2e-c75442362822 |  | textbox | Blue To Earth EFLI
text | 1e5a77b6-d7ad-55b0-bac2-55ebc634be18 |  | textbox | Blue To Earth PFC
text | ef080d93-925e-5528-8e0f-8a34e6eae7b5 |  | textbox | Red To Neutral EFLI
text | 92a2637f-b468-50f8-baf0-e416fa0d0f05 |  | textbox | Red To Neutral PFC
text | af9f0f81-4f49-5ab4-9870-af7eb977c53f |  | textbox | White To Neutral EFLI
text | 8cc1f3d7-519e-569c-a212-3daf6d4acfe5 |  | textbox | White To Neutral PFC
text | 519b8ff8-d9fa-50e0-84bb-6ce03f179bc9 |  | textbox | Blue To Neutral EFLI
text | ff17db61-f599-5990-8d9b-309b5f03960c |  | textbox | Blue To Neutral PFC
checkpoint-status |  |  | checkpoint | Perform and Record The Following
text | 6721a494-5105-5947-9186-a5b4dd9b712d |  | textbox | Red To White Loop Impedance
text | 71289ebd-cfbc-51c7-8584-b6a5a19821f0 |  | textbox | Red To White PSCC
text | d3a5c060-3d7a-5934-8989-ce9009adbf3a |  | textbox | Red To Blue Loop Impedance
text | 6e992651-d553-5f43-b643-d5ef8ef5e5f6 |  | textbox | Red to Blue PSCC
text | eb88e227-7c6d-514e-8d61-258b88a50e9b |  | textbox | White To Blue Loop Impedance
text | 87defd61-9342-5ed0-8b28-ad0824861344 |  | textbox | White To Blue PSCC
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
select | e2ffe7ac-bf26-5fac-93a9-2b1648178323 |  | dropdown | Test Equipment Used | Fluke 1662, Fluke 1653B
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | a90f7198-ab4e-5703-84e2-496c6bb6b238 |  | textbox | Tested By
text | 39faaf2e-e951-594e-863f-b71262ce46c5 |  | textbox | Witnessed By
text | 73d1a6f8-8e23-5195-ad13-44bae873638e |  | textbox | Date
checklist-flat |  |  | checklist | LP DC Test Script |  |  |  |  | Yes | LP DC Test Script | 218e48c3-7528-46e5-aff3-9465d5131ef3
checkpoint-status |  |  | checkpoint | Visual Inspection
text | 4cee0b72-a705-593c-9b80-e7642218b662 |  | textbox | Test Link Connection Ref No.
checkpoint-status |  |  | checkpoint | Ductor Test Performed With Satisfactory Result
text | d011e761-2471-5704-9fd6-94f8af91d8e0 |  | textbox | Low Ohm Resistance Test Result - Ductor Test (Ohms)
select | 9fc27faa-647a-532b-b8a9-3e954706fc06 |  | dropdown | Test Equipment Used | Meggar DLRO10X
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 67041b37-b7be-566a-a0ca-6ec69c86eef3 |  | textbox | Tested By
text | 0c3b8bf9-035f-5514-98ef-4d2890268a5c |  | textbox | Witnessed By
text | 78a9075a-3e06-5b80-86ee-a0d178c42161 |  | textbox | Date
checklist-flat |  |  | checklist | Earth Bonding Test Script |  |  |  |  | Yes | Earth Bonding Test Script | 261ce6d4-0d7f-496b-b368-9cbbecef4398
checkpoint-status |  |  | checkpoint | Earth Bonding Test Script Has Been Completed And Attached To This Checkpoint If Required
checklist-flat |  |  | checklist | Temp Power Paperwork Attachment |  |  |  |  | Yes | Temp Power Paperwork Attachment | 2a5e56cb-3dfe-44ca-af7e-80102661ac66
checkpoint-status |  |  | checkpoint | Attach Paperwork For Switchboard To This Check
checklist-flat |  |  | checklist | Distribution Board Post-livening Check Sheet - PFC |  |  |  |  | Yes | Distribution Board Post-livening Check Sheet - PFC | 306c38be-b460-4b68-8d69-72fb57ff46e9
checkpoint-status |  |  | checkpoint | Confirm pre livening check is complete
checkpoint-status |  |  | checkpoint | Confirm the correct voltage is present
text | 88ea52a4-441d-5621-97ea-474fcb0d0873 |  | textbox | R-W |  |  | V
text | f5f22700-43f5-550c-92bc-3b70afa50ff2 |  | textbox | B-N |  |  | V
text | a74c655b-dd71-5199-8f0d-19ba57b96fc8 |  | textbox | R-B |  |  | V
text | be33dbcb-293f-5d4b-9d70-1109a3baa64b |  | textbox | R-E |  |  | V
text | bb5e4b62-2971-5500-8e37-f1e8a1b415d6 |  | textbox | W-B |  |  | V
text | 28da5923-0fde-5e7c-aa09-2af78025e5ad |  | textbox | W-E |  |  | V
text | d364e956-eaa3-58f8-bd64-bca2bb513dea |  | textbox | R-N |  |  | V
text | 013dba8e-fcd7-5014-a7ca-3613d295b296 |  | textbox | B-E |  |  | V
text | 8f722740-43a9-5da0-92e4-1eae6bddf9a1 |  | textbox | W-N |  |  | V
text | 3c97c3c9-82ec-5e65-9515-ccd8c916dfed |  | textbox | N-E |  |  | V
checkpoint-status |  |  | checkpoint | Confirm the correct polarity and phase rotation
text | 11864011-2c59-5f0c-83bb-a4359730dcaf |  | textbox | R
text | 8aa02573-7006-5d88-bcd3-a3ba70f0c248 |  | textbox | W
text | 5ddf53d5-2ca8-5ae4-9f72-eb1c67c8a4b6 |  | textbox | B
text | ed4f2f79-bfad-5e84-8c6f-abe0e21b3023 |  | textbox | N
checkpoint-status |  |  | checkpoint | Confirm the correct control voltage is present
checkpoint-status |  |  | checkpoint | Confirm all meters/monitoring devices are setup correctly and operational
checkpoint-status |  |  | checkpoint | Confirm the PFC controller is set up correctly and operational
checkpoint-status |  |  | checkpoint | Confirm all switching devices (ACB's, MCCB's, MCB's etc) are switching correctly
checkpoint-status |  |  | checkpoint | Confirm all auxiliaries are switching correctly
checkpoint-status |  |  | checkpoint | Confirm all adjustable circuit breaker settings are recorded and correct
checkpoint-status |  |  | checkpoint | Confirm switchboard is ready to be put into service
checkpoint-status |  |  | checkpoint | Special Conditions
text | 6b111a99-7d2f-5e38-a92e-b08a0156cceb |  | textbox | Conditions
checkpoint-status |  |  | checkpoint | Tested
text | a13b4562-7870-5f51-8d8f-3835a681cee8 |  | textbox | Tested By
checkpoint-status |  |  | checkpoint | Confirm Ready To Be Livened
holdpoint |  |  | signoff | Request Confirmation
checklist-flat |  |  | checklist | Transformer Post Livening |  |  |  |  | Yes | Transformer Post Livening | 349ae127-6812-40dc-afd4-2fde7a364ee0
checkpoint-status |  |  | checkpoint | Confirm Voltage Readings Taken At Primary And Secondary Sides Are Equal
checkpoint-status |  |  | checkpoint | Test And Record Voltage Readings Of Primary
text | 550fece3-b677-5401-b623-2827d8008b60 |  | textbox | Red To White
text | d1c61241-c673-56a4-a6f1-bce130a0637b |  | textbox | Red To Blue
text | c716fa0a-9b8f-573b-9abe-fa7f3a0e6881 |  | textbox | Red To Neutral
text | 415c6f63-4c04-5d17-83d9-a3be71ab8f75 |  | textbox | Red To Earth
text | f0abebec-562a-55d4-96fb-50d3737b4a62 |  | textbox | White To Blue
text | 0600e7f0-9d1a-554e-b329-afea75bb94c5 |  | textbox | White To Neutral
text | 6c17a9b9-7489-5441-9407-c539eed9e1e6 |  | textbox | White To Earth
text | a32ba9a7-61cc-5dcd-ac14-f489fa52866c |  | textbox | Blue To Neutral
text | 406a76e5-42b8-57b1-b4ed-e93599b52639 |  | textbox | Blue To Earth
text | 7db85d8b-fa68-5164-89b1-e6c694ebcc96 |  | textbox | Neutral To Earth
checkpoint-status |  |  | checkpoint | Test And Record Voltage Readings Of Secondary
text | ce8788e5-d9bf-5248-8c13-fb56752aed65 |  | textbox | Red To White
text | 2a481906-6487-504e-b372-850c6c3a5705 |  | textbox | Red To Blue
text | f9077049-d857-53e6-968d-a7eb50add059 |  | textbox | Red To Neutral
text | 05845d7c-c351-5440-8de1-d46bc88d2558 |  | textbox | Red To Earth
text | 19ba20c5-dfb3-5f91-ae54-6616700e5f54 |  | textbox | White To Blue
text | e17af6d1-2aa3-5367-b3f2-709015373b84 |  | textbox | White To Neutral
text | b4e8c651-2325-5d24-ae60-7c6ebc8494a5 |  | textbox | White To Earth
text | 422a9787-d22d-5d57-b416-808ad0e8a6e1 |  | textbox | Blue To Neutral
text | 470048f5-6589-59d9-ac77-cc881844c8f2 |  | textbox | Blue To Earth
text | 4cb7b076-12be-5c31-8811-881e7f6be87c |  | textbox | Neutral To Earth
checkpoint-status |  |  | checkpoint | Confirm Phase Rotation Is Correct
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
select | 68b66ca7-f6af-5b6d-8ec8-21a3d96f0fff |  | dropdown | Test Equipment Used | Fluke 1662, Fluke 1653B
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | cecdeb2c-cc41-564f-9864-cb0000bb6f55 |  | textbox | Tested By
text | f964dddc-a79c-50d3-a937-2d78668b4dd6 |  | textbox | Witnessed By
text | ebf9b147-a579-5d5e-bcce-9965e90a3d9f |  | textbox | Date
checklist-flat |  |  | checklist | Submain Pre Livening |  |  |  |  | Yes | Submain Pre Livening | 3aed368a-21ab-4759-a186-a5b5b09589b1
checkpoint-no-status |  |  | checkpoint | Details
select | 299b4a55-3a7b-5f6e-bd2c-0f0ba653703f |  | dropdown | Supply Cable Type | XLPE Cu,XLPE Fire Rated Cu
select | ff05808b-fac8-5115-a3f2-9d5459ac092b |  | dropdown | Single Core Or Multicore | Single Core, Multicore
text | 6fa8ac46-7e8c-5604-b7ac-c6d9589d2294 |  | textbox | Supply Cable Size
label | e010722b-018a-593e-99e3-7cbeb48b0f72 |  | note | Earth Cable Type - PVC
text | cda80589-e16c-5835-83c1-7f17c80dd7c3 |  | textbox | Earth Cable Size
text | 00824f80-d151-5faf-b716-2b2fc61aa81a |  | textbox | Number Of Parallel Sets Of L1, L2, L3
text | 70f69ae6-3260-5081-8364-5913873f5950 |  | textbox | Number Of Parallel Sets Of N
text | 4db80a40-340a-5573-a827-4d455e802d8f |  | textbox | Number Of Parallel Sets Of E
text | f4e86774-c7df-577a-b613-cb982dd5b96f |  | textbox | Breaker Size At Supply
checkpoint-status |  |  | checkpoint | Complete Visual Inspection Of Cable Installation
checkpoint-status |  |  | checkpoint | Cables Tied In Specified Arrangement
checkpoint-status |  |  | checkpoint | Bending Radius's Correct
checkpoint-status |  |  | checkpoint | No Physical Damage To Outer Sheaths
checkpoint-status |  |  | checkpoint | Phase Identification Is Fitted
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For Red Phase
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For White Phase
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For Blue Phase
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For Neutral
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For Earth
checkpoint-status |  |  | checkpoint | Perform Insulation Resistance At 1000VDC And Confirm All Results Above 100MOhm
text | 0841725b-d4d9-53ea-928d-fda346f3f93a |  | textbox | Red To White
text | 4b7992fa-222c-522f-bd6a-8be5765edc88 |  | textbox | Red To Blue
text | ef6cdd95-f93b-5aaa-aab3-968bdecff4a9 |  | textbox | Red To Neutral
text | a72c6ed6-ea64-50ce-80b5-f3a38f1654c0 |  | textbox | Red To Earth
text | 1df22167-0ed4-5f09-b58f-f197ba2c5048 |  | textbox | White To Blue
text | 2cba7d5a-998f-534c-a937-845c382b1465 |  | textbox | White To Neutral
text | 407be2c0-08b6-54fe-a846-33d18684aa39 |  | textbox | White To Earth
text | 037ea8bc-2973-5004-af5a-7a26f0ca63d3 |  | textbox | Blue To Neutral
text | c76fe67e-10cd-5016-ae51-f4795b88401e |  | textbox | Blue To Earth
text | 4fe91db8-b76d-5504-a133-e792147e3682 |  | textbox | Neutral To Earth
checkpoint-status |  |  | checkpoint | All Cables Torqued And Marked
checkpoint-status |  |  | checkpoint | Record Torque Value At Supply
text | d50dc172-2cc1-5521-9fc1-55f8a3a4ed7d |  | textbox | Red
text | a8f48333-1bcc-5a68-9218-17361395092e |  | textbox | White
text | 1c89902f-17ef-5b1c-a084-ad9f96dcc68a |  | textbox | Blue
text | b93c0d22-63a3-52a9-9f1c-aac99782ef3d |  | textbox | Neutral
text | 4a30f692-7d93-542d-83f6-a7df91a5b2c1 |  | textbox | Earth
checkpoint-status |  |  | checkpoint | Record Torque Value At Load
text | 823581cc-5f07-56b3-b147-e98ebd119c1a |  | textbox | Red
text | 905c4ad3-0134-5db1-b4a8-6cd923c0ff27 |  | textbox | White
text | 781ca33c-3fce-576f-9f51-ed9cb7820d1b |  | textbox | Blue
text | b3ee3b19-f569-58b9-b241-26141811d533 |  | textbox | Neutral
text | dce4ad51-2244-53d8-a9c1-ef58c88047df |  | textbox | Earth
checkpoint-status |  |  | checkpoint | Confirm Contact Resistance Testing Sheet Has Been Completed And Attached To This Checkpoint
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
label | 7f38b604-61d0-5047-be33-e746347f6eaa |  | note | Test Equipment Used - Megger MIT410/2, Megger DLRO10X
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | f721d81f-d377-5077-b066-65a80c8f3a39 |  | textbox | Tested By
text | 3f432d48-2ad7-5c71-befd-968cd22539ad |  | textbox | Witnessed By
text | faefb275-1845-5be9-add5-e0b7ddbca1b5 |  | textbox | Date
checklist-flat |  |  | checklist | Inground Earthing Script |  |  |  |  | Yes | Inground Earthing Script | 3b37d38a-8ba7-4e0a-a493-d5575a5fb8c8
checkpoint-status |  |  | checkpoint | Visual Inspection
text | 1fe84b85-85b7-52bc-ae1d-d826bcf23450 |  | textbox | Earth Connection Ref No.
select | 00fa24dd-062a-54af-8942-726d5f86e2b0 |  | dropdown | Connection Type | Cable To Cable, Cable To Earth Bar, Cable To Rebar, Rebar To Rebar
select | 8a022acf-8885-50b5-a432-7bfbb17fe7cb |  | dropdown | If Cable To Cable | 95mm to 95mm, 95mm to 120mm, 120mm to 120mm, N/A
select | 01fbeea8-bf16-5413-bcd3-b2d8d8d84073 |  | dropdown | Method | Crimp, Bolt, Clamp, Cad Welded
checkpoint-status |  |  | checkpoint | Confirm Status Of Test Result
text | 626c278a-cd72-5730-b134-faf743c27498 |  | textbox | Connection Point Tested to
text | ff4ea98c-2aa0-5114-92fa-7380293e35f0 |  | textbox | Low Ohm Resistance Test Result <0.5 Ohms
select | 29bcf1b2-9ca7-50bc-b190-e0c9dbc59dde |  | dropdown | Test Equipment Used | Fluke 1662, Fluke1653B
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | edfbadc2-2be0-5322-b8f2-ed72a30347a9 |  | textbox | Tested By
text | ee94199d-b156-5c8d-a5ea-cd7e298b83a0 |  | textbox | Witnessed By
text | e0465f6a-f573-5cbc-8f77-68d249c653bb |  | textbox | Date
checklist-flat |  |  | checklist | Subcircuit Installation Progression |  |  |  |  | Yes | Subcircuit Installation Progression | 40b31739-758d-4873-89a9-a96b0628134b
checkpoint-status |  |  | checkpoint | All Feeds, Control Wiring, Other Cabling Required Installed From Switchboard
select | 66864be1-1306-54b9-9044-5650983639a4 |  | dropdown | Status Of Above Check | 25%, 50%, 75%, 100%
text | 6cab41d4-3378-52da-b65c-3680ae750ee6 |  | textbox | Issues Holding Up The Progression Of Above Check. Number And Date Issues
text | 4a4c3d13-b1b7-5c61-8e0a-658407d6324c |  | textbox | Detail Actions Taken To Resolve Above Issues. State Issue Number
checkpoint-status |  |  | checkpoint | Issues Have Been Raised Formally On Aconex
checkpoint-status |  |  | checkpoint | All Field Cabling And Containment Has Been Installed Where Necessary
select | 27bcc034-2a7f-5e66-9eb6-a9ecbc38b10e |  | dropdown | Status Of Above Check | 25%, 50%, 75%, 100%
text | a1bc2783-8f70-5e03-bd58-22729aba8ea9 |  | textbox | Issues Holding Up The Progression Of Above Check. Number And Date Issues
text | 979b73a3-342f-5347-953b-b337b4a4a6bd |  | textbox | Detail Actions Taken To Resolve Above Issues. State Issue Number
checkpoint-status |  |  | checkpoint | Issues Have Been Raised Formally On Aconex
checkpoint-status |  |  | checkpoint | Switchboard Fit Off Is Complete
select | 149c838b-c12b-5eb3-b3b3-96cac17f6a1a |  | dropdown | Status Of Above Check | 25%, 50%, 75%, 100%
text | b90076c0-d992-597b-9bf2-dc611c2eb7c8 |  | textbox | Issues Holding Up The Progression Of Above Check. Number And Date Issues
text | c86e9fa8-ebe3-5736-86a1-980d1266b2b4 |  | textbox | Detail Actions Taken To Resolve Above Issues. State Issue Number
checkpoint-status |  |  | checkpoint | Issues Have Been Raised Formally On Aconex
checkpoint-status |  |  | checkpoint | All Field Cabling Fit Off Is Complete
select | 8a761c06-3982-52cb-80b8-13b33cea8233 |  | dropdown | Status Of Above Check | 25%, 50%, 75%, 100%
text | 3bfc17ec-147e-5b6e-9e93-bc551e2086bd |  | textbox | Issues Holding Up The Progression Of Above Check. Number And Date Issues
text | e309b799-dba7-5bf9-bdd3-b9d310932d98 |  | textbox | Detail Actions Taken To Resolve Above Issues. State Issue Number
checkpoint-status |  |  | checkpoint | Issues Have Been Raised Formally On Aconex
checkpoint-status |  |  | checkpoint | Sign off complete
text | 3fcc1b25-6b95-5b22-9a8d-55beec4bca62 |  | textbox | Supervisor Sign Off
text | bc5bd17a-0f42-515c-a5b5-484a64d7fd7b |  | textbox | Date
checklist-flat |  |  | checklist | LP Main Roof QA Script |  |  |  |  | Yes | LP Main Roof QA Script | 4b6fa048-fd8c-44d0-b389-29232ed30b53
checkpoint-status |  |  | checkpoint | Visually Inspect Entire Above Roof Lightning System, Maintain All Health And Safety Requirements
checkpoint-status |  |  | checkpoint | Confirm Above Roof Lightning Protection System Has Been Installed According To Latest IFC Drawings And Any Other Related Documents
checkpoint-status |  |  | checkpoint | Confirm That There Is No Visual Damage
checkpoint-status |  |  | checkpoint | All Fixings Seem Secure And In Their Original Positions
checkpoint-status |  |  | checkpoint | All Roof And Bonding Conductors Are Fixed With Copper To Copper Or Stainless Steel To Insulated Copper Saddles Similar To FURSE Or Approved Equivalent c/w Phosphor Bronze Screws At Intervals Not Exceeding 1m.
checkpoint-status |  |  | checkpoint | Air Terminals Are Securely Mounted, With Earth Connections Directly Routed Via The Shortest Route To Ground
checkpoint-status |  |  | checkpoint | All Copper Tape is full length Except Where Necessary To Accommodate 90 Degree Bends And T Joins
checkpoint-status |  |  | checkpoint | All Conductors Of Cable Type Are At Least 70mm2 In Size And Of Full Length
checkpoint-status |  |  | checkpoint | All Connections Are Welded And Where Not Feasible, Bolted. And Protected With Approved Sealant Or Anti Corrosion Paint
checkpoint-status |  |  | checkpoint | All Joins Overlap And By At Least 25mm
checkpoint-status |  |  | checkpoint | All Metallic Structures, Tanks, Equipment Ducts, Fans, AHUs, Cooling Towers, Pumps, Railings, All Metal Parts etc. Are Bonded To The Roof Conductors By Use Of Stainless Steel Clamps, Bolts And Nuts
checkpoint-status |  |  | checkpoint | Connection Points To Down Conductors Are No More Than 20m Apart, Have Been Left In A Suitably Accessible Place And Are Ready For Down Conductor Connections
checkpoint-status |  |  | checkpoint | Confirm Ductor Test Across All Joints Has Taken Place And Satisfactory Results Have Been Recorded
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 8aa3a952-4ea3-5480-b7b8-14f045b5b223 |  | textbox | Tested By
text | 830ebfbb-725b-51fe-baf4-294c910594c1 |  | textbox | Witnessed By
text | 005ec06c-9018-5282-b990-b128d52475fb |  | textbox | Date
checklist-flat |  |  | checklist | Earth Bar QA One Incomer |  |  |  |  | Yes | Earth Bar QA One Incomer | 530ffd93-9a9c-4c2a-811f-e39782256104
checkpoint-no-status |  |  | checkpoint | Earth Bar QA One Incomer
text | ee9b629f-5179-5a01-9f28-9e9c872f503e |  | textbox | Earth Bar Identifier
checkpoint-status |  |  | checkpoint | Earth Bar note Attached
checkpoint-status |  |  | checkpoint | Supply Earth noteled
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Incoming Earth Cable Torqued
select | 264fb45a-4e22-514f-bfa3-f537a7ca534f |  | dropdown | Incoming Earth Cable Type | Insulated PVC
select | 2c292b87-015d-5e86-80f8-b79bdad6c24c |  | dropdown | Incoming Earth Cable Size | 95mm, 120mm
checkpoint-status |  |  | checkpoint | Correct Incoming Earth Size Per Single Line Diagram
checkpoint-status |  |  | checkpoint | Earth Bar Securely Attached With Insulated Spacers
checkpoint-status |  |  | checkpoint | All Outgoing Earths Have Destination noteled At Earth Bar
checkpoint-status |  |  | checkpoint | All Outgoing Earths Are Torqued
checkpoint-status |  |  | checkpoint | Photo Reference
text | 629b2b3c-d814-5606-885f-f5d29922f8f5 |  | textbox | Comment
text | 42ce1963-15bd-5137-891a-be93842c014c |  | textbox | Date
text | 5a2170e7-7f03-57d1-9e15-8c2d3a88079e |  | textbox | Comment
text | 018a9864-c3e1-5140-8dd3-08aea75a09f6 |  | textbox | Date
text | 891e315e-eb27-58ab-80de-69045c2e39a4 |  | textbox | Tested By
text | 62fe6e04-e55c-526e-9044-96023e0c03ab |  | textbox | Witnessed By
text | 38869c9b-333c-5075-9cda-19db42fd563c |  | textbox | Date
checklist-flat |  |  | checklist | Submain Pre Livening Temp |  |  |  |  | Yes | Submain Pre Livening Temp | 5388d783-58d4-45be-82fe-21173c50553b
checkpoint-no-status |  |  | checkpoint | Submain Pre Livening Temp
text | da53b3cd-d470-5ade-8ebb-5fcea901a037 |  | textbox | Submain Supplied From
text | 1ec13b88-5fc5-5452-bca1-eb6f7edc3fe8 |  | textbox | Submain Supply Run To
select | 3248c6fe-c920-5623-b9f7-33b26231e339 |  | dropdown | Supply Cable Type | XLPE Cu, XLPE Fire Rated Cu
select | 435c15b0-31b5-5ca1-9efd-2e4a287a374d |  | dropdown | Single Core Or Multicore | Single Core, Multicore
text | 9fb7d649-1d7e-5fb6-a498-dc99bc8e1ce9 |  | textbox | Supply Cable Size
label | ea0fcfb2-e889-509f-9e10-8693de23be21 |  | note | Earth Cable Type - PVC
text | fc426e47-89c7-518e-baff-bfd8d71a7992 |  | textbox | Earth Cable Size
text | ef358100-6d5f-55c3-aeec-ec2d8473a12b |  | textbox | Number Of Parallel Sets Of L1, L2, L3
text | 8d798c10-3ea9-5c15-9c98-84ae733a322c |  | textbox | Number Of Parallel Sets Of N
text | 52972e84-5919-57be-92b6-90ce3a913f74 |  | textbox | Number Of Parallel Sets Of E
text | 530fc7b9-3431-5660-9af8-1cef37a1452e |  | textbox | Breaker Size At Supply
checkpoint-status |  |  | checkpoint | Complete Visual Inspection Of Cable Installation
checkpoint-status |  |  | checkpoint | Cables Tied In Specified Arrangement
checkpoint-status |  |  | checkpoint | Bending Radius's Correct
checkpoint-status |  |  | checkpoint | No Physical Damage To Outer Sheaths
checkpoint-status |  |  | checkpoint | Phase Identification Is Fitted
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For Red Phase
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For White Phase
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For Blue Phase
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For Neutral
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For Earth
checkpoint-status |  |  | checkpoint | Perform Insulation Resistance At 500VDC And Confirm All Results Above 100MOhm
text | 7a2c9d0f-014c-5118-a623-110bafee73d5 |  | textbox | Red To White
text | 1342c92e-d028-55e1-9b19-047d5017f71d |  | textbox | Red To Blue
text | a39f1499-4d30-543f-8a08-30c2ea68c865 |  | textbox | Red To Neutral
text | 5fc52541-ecdc-5521-842d-a0846efe509e |  | textbox | Red To Earth
text | eacd5554-f73e-52c4-ad39-ed49b7ec06b9 |  | textbox | White To Blue
text | 1f7ff49b-e6b0-5a60-994d-a5dbf27c8fa6 |  | textbox | White To Neutral
text | b479e662-7e81-5939-8afa-ea852819b43f |  | textbox | White To Earth
text | 4eaa3650-704e-5feb-9cb7-0b1a98f3f664 |  | textbox | Blue To Neutral
text | c4edf50f-64bb-505c-86a2-de253012db74 |  | textbox | Blue To Earth
text | dbf0d15d-e75a-5b2a-b55e-c511fe7b6e72 |  | textbox | Neutral To Earth
checkpoint-status |  |  | checkpoint | All Cables Torqued And Marked
checkpoint-status |  |  | checkpoint | Record Torque Value At Supply
text | 4bbef02e-5b69-5f38-b5ff-c82f0ec3654c |  | textbox | Red
text | 24924aea-14dd-51ec-b501-f7b92a37660b |  | textbox | White
text | be5f90b6-cdd1-52c6-9b91-01b3d67c4e68 |  | textbox | Blue
text | 8211a62a-1bc7-5d8e-92ca-595ac90ae1e1 |  | textbox | Neutral
text | ff2696c5-5897-5243-b4ba-a7345b143de4 |  | textbox | Earth
checkpoint-status |  |  | checkpoint | Record Torque Value At Load
text | 141a8a48-1201-5a62-94f4-6dfd753f8c6c |  | textbox | Red
text | 02e5a775-30c1-57b6-8616-886aa02e931f |  | textbox | White
text | f1e5c00c-de36-59e4-a385-353e7a16a25e |  | textbox | Blue
text | a887968a-d53b-5608-9969-e4fb9f1b3fdd |  | textbox | Neutral
text | 09fca171-5dfd-5c96-b90b-661627c202f4 |  | textbox | Earth
label | 739dc7a3-403c-5900-89a5-0dbe53e234a5 |  | note | Test Equipment Used: Megger MIT410/2
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | b8943976-ce2b-5f51-b712-c91831cb168c |  | textbox | Tested By
text | b514c54c-869a-5959-b20a-b7ebacd87cf1 |  | textbox | Witnessed By
text | 910d65b0-f0ab-5c2c-9f39-63203d8968cb |  | textbox | Date
checklist-flat |  |  | checklist | Submain Post Livening |  |  |  |  | Yes | Submain Post Livening | 6695209b-9109-4a86-aa24-212de6e2e571
checkpoint-no-status |  |  | checkpoint | Details
select | ed26e988-c86c-59da-b5b5-d283c81deda9 |  | dropdown | Supply Cable Type | XLPE Cu, XLPE Fire Rated Cu
text | 62c47092-bba0-5c7a-aaf9-6997e364269b |  | textbox | Supply Cable Size
select | 38ef1b64-014d-5765-9793-7187d2c3281a |  | dropdown | Earth Cable Type | PVC
text | 8b000579-56e0-57ae-b084-771cec39b6b8 |  | textbox | Earth Cable Size
select | d8f2b1f8-bd81-5023-9371-e0feda094d18 |  | dropdown | Single Core Or Multicore | Single Core, Multicore
text | e07085f5-beb0-57d4-b08b-75f215106526 |  | textbox | Number Of Parallel Sets Of L1, L2, L3
text | 7add28ae-57f6-5e78-864f-97a3d8c38c0b |  | textbox | Number Of Parallel Sets Of N
text | f5b8cac3-702e-5327-a92f-dfd3ef41b853 |  | textbox | Number Of Parallel Sets Of E
text | 649041ee-14b4-51ea-98bd-4c2116a5e79d |  | textbox | Breaker Size At Switchboard
text | 3d417205-698b-571a-b6cd-f4bff2055dd6 |  | textbox | Record Size Breaker Is Set To
text | d45a7569-ef40-5d4c-92d9-05d769ec4eb0 |  | textbox | Record KA Rating Of Breaker
checkpoint-status |  |  | checkpoint | Test And Record Voltage Readings
text | c0eac3f9-78b7-57b1-9c42-1a96377e5154 |  | textbox | Red To White
text | 183d2cc2-2dd2-5a76-9be9-378e4cf027cc |  | textbox | Red To Blue
text | 1750ab89-68e3-56ed-b7b3-ab6f0602a45e |  | textbox | Red To Neutral
text | 9e529da4-9db9-5836-90ed-ecf97af4a680 |  | textbox | Red To Earth
text | 43f2092c-f66e-570b-b3cd-a0ab9392536a |  | textbox | White To Blue
text | b2ee281e-cc3d-565d-a666-3dd4a520d4e0 |  | textbox | White To Neutral
text | 6c3ed57d-8578-5d0b-aac1-f4cf560a8c63 |  | textbox | White To Earth
text | 15de55aa-f20f-5a5b-8b39-ed9e0b9bb416 |  | textbox | Blue To Neutral
text | 53fdce81-6c40-56fd-ae8d-1ab2abd48cd2 |  | textbox | Blue To Earth
text | a3c2734b-d214-5bff-bab8-e92f5c695ac8 |  | textbox | Neutral To Earth
checkpoint-status |  |  | checkpoint | Confirm Phase Rotation Is Correct
checkpoint-status |  |  | checkpoint | Perform and Record The Following
text | ca3bac79-9b9e-5d71-bb4d-716e283471f2 |  | textbox | Red To Earth EFLI
text | bbdb8e88-d751-5b2b-9caa-c6e54d365e23 |  | textbox | Red To Earth PFC
text | 0fb00b98-9acc-5a1c-90c9-dbedc5ee1a6f |  | textbox | White To Earth EFLI
text | be429912-220f-56c5-9694-1ea912bf4197 |  | textbox | White To Earth PFC
text | b6236e6b-2acf-565d-b77f-430e8928fe7a |  | textbox | Blue To Earth EFLI
text | 6af2d534-8e3f-5e4e-ac90-f5bac4b9939b |  | textbox | Blue To Earth PFC
text | 218b6071-5e6f-5184-88b2-a3502936849b |  | textbox | Red To Neutral EFLI
text | 3d59387a-6bc3-5cc7-943d-8c274703cfd9 |  | textbox | Red To Neutral PFC
text | c37acd61-eafe-5022-976d-0c4e61e2432f |  | textbox | White To Neutral EFLI
text | 7ebeeee9-140b-5ddf-adee-ec4df19965ae |  | textbox | White To Neutral PFC
text | 7671c4ea-50e3-5af7-af0b-6232ae0cbb29 |  | textbox | Blue To Neutral EFLI
text | 48c79f5f-fad8-59c4-8a3a-f1c2ad2ac89d |  | textbox | Blue To Neutral PFC
checkpoint-status |  |  | checkpoint | Perform and Record The Following
text | 42256987-4fd1-58a3-bab4-b9854d10457d |  | textbox | Red To White Loop Impedance
text | e8b34101-5f36-5bd9-9b25-e3cee94f7eb7 |  | textbox | Red To White PSCC
text | 229b8e5d-ab10-5ffe-a9b9-be6fe11dc87f |  | textbox | Red To Blue Loop Impedance
text | d3fb9f29-4989-5cd1-8d5a-8d40c2478261 |  | textbox | Red to Blue PFC
text | ae77b00b-20fb-5143-9bf0-39e87f8f3713 |  | textbox | White To Blue Loop Impedance
text | 60868d16-f998-5166-9aea-f2122e9edbef |  | textbox | White To Blue PFC
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
select | 410f404f-c578-51e1-80a6-b1f66fb3a60b |  | dropdown | Test Equipment Used | Fluke 1662, Fluke 1653B
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | bc39f37d-71bf-5bca-ba45-3cd6ee42b94f |  | textbox | Tested By
text | 1e728fbe-f1c0-5142-98ec-8f5d392f5466 |  | textbox | Witnessed By
text | ad8e58bf-4669-580e-a928-c66140a6df11 |  | textbox | Date
checklist-flat |  |  | checklist | E For M Submain Post Livening |  |  |  |  | Yes | E For M Submain Post Livening | 66fbfa8f-4c75-45c9-b205-1405e3df5408
checkpoint-status |  |  | checkpoint | Submain Post Livening Test/s Have Been Completed And Attached To This Checkpoint If Required
checklist-flat |  |  | checklist | Bus Duct Pre Livening |  |  |  |  | Yes | Bus Duct Pre Livening | 68004c7b-2e06-4060-b5ef-751695e01ec4
checkpoint-status |  |  | checkpoint | Verify Area Is Clean Of Debris And Foreign Objects
checkpoint-status |  |  | checkpoint | All Packaging, Rubbish And Trash Has Been Removed From Installation Site
checkpoint-status |  |  | checkpoint | Confirm Adequate Lighting Has Been Provided
checkpoint-status |  |  | checkpoint | Confirm End Feed Unit Location Complies With AS/NZS3000 Minimum Safe Distances And Clearances
checkpoint-status |  |  | checkpoint | Verify Barriers/Masking Panels Are Present And Installed Correctly
checkpoint-status |  |  | checkpoint | Inspect Bus Insulators Of End Feed Unit
checkpoint-status |  |  | checkpoint | Inspect Power Cables In End Feed Unit And Tap Off unit
checkpoint-status |  |  | checkpoint | Inspect Doors, Covers, Gaskets
checkpoint-status |  |  | checkpoint | Inspect Phase Barriers (When Applicable)
checkpoint-status |  |  | checkpoint | Confirm Grounding At End Feed Unit And All Tap Off Units
checkpoint-status |  |  | checkpoint | Tap Off unit Components - Verify All Electrical Components Are Correctly Mounted And Fixed Securely
checkpoint-status |  |  | checkpoint | Inspect Wiring Inside All Tap Off Units - Pull Test On Wire Connections
checkpoint-status |  |  | checkpoint | Verify All Panels And Covers Are Fixed. Doors Function Smoothly
checkpoint-status |  |  | checkpoint | Confirm Circuit Identification Is Visible On Masking Panel Or Front Of Tap Off Unit
checkpoint-status |  |  | checkpoint | Verify/Inspect Breakers For Damage At End Feed Unit And All Tap Off Units
checkpoint-status |  |  | checkpoint | Verify Breaker Type, Sizes And KA Rating Against Approved Circuit Schedule For End Feed Unit And All Tap Off Units
checkpoint-status |  |  | checkpoint | Operate Breakers/Isolators At End Feed Unit And All Tap Off Units And Check For Smooth Operation
checkpoint-status |  |  | checkpoint | Confirm All Required Switchboard Blanks Have Been Installed Inside Tap Off Units
checkpoint-status |  |  | checkpoint | Confirm All Sections Are Clean And Free Of Objects/Debris/Swarf
checkpoint-status |  |  | checkpoint | Confirm Exterior Is Free From Scratches. Dents, Tape Marks And Physical Damage
checkpoint-status |  |  | checkpoint | Confirm Equipment Is Installed According To Shop Drawings And Specifications
checkpoint-status |  |  | checkpoint | Confirm The Bus Duct Has An Identification Label Matching The Single Line Diagram
checkpoint-status |  |  | checkpoint | Confirm The Required Number Of Tap Off Boxes Have Been Installed As Per Requirements
checkpoint-status |  |  | checkpoint | Confirm Colour Banding Is Installed Per Specifications And Can Be Clearly Identified From The Floor
checkpoint-status |  |  | checkpoint | Confirm That End Feed Unit Supply Cables Have Phase Identification Fitted
checkpoint-status |  |  | checkpoint | Confirm That End Feed Unit Is LOTO Or Tagged Prior To Energizing Submains
checkpoint-status |  |  | checkpoint | Confirm All Gland Plates Are Secure With All Bolts Installed
checkpoint-status |  |  | checkpoint | Confirm All Gland Plates Are Earthed
checkpoint-status |  |  | checkpoint | Confirm All Glands are Tight Allowing No Movement Of Cable Within Gland
checkpoint-status |  |  | checkpoint | To Be Performed With Tap Off Boxes Installed -Perform Insulation Resistance At 1000VDC On All Parts Of Bus Duct Bus Bar Accessed During Installation Process, Consider Load Sides Of Breakers Not Connected When Breakers Open And Any Breaks In The Busbar Through Design. Refer To Shop Drawings And Single Line Diagrams. Rack out/switch off all breakers, remove all control fuses, fault current limiters and disconnect neutral and earth at surge diverters. Remove all RCD Earth and neutral tails. Confirm All Results Above 100MOhm
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
label | a9cb1412-41df-5ee3-b8f2-f9b93cedc8c2 |  | note | Test Equipment Used - Meggar MIT410/2
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | a761f65b-45c9-57e2-bbf0-54b1a42c1a20 |  | textbox | Tested By
text | da14c5a1-8dd1-58d7-b7b3-f1a774132555 |  | textbox | Witnessed By
text | 3628392d-247e-5278-95c2-ab8251bb4710 |  | textbox | Date
checklist-flat |  |  | checklist | E For M Submain Pre Livening |  |  |  |  | Yes | E For M Submain Pre Livening | 6b501ab5-b44b-487c-b143-521a6e355e70
checkpoint-status |  |  | checkpoint | Submain Pre Livening Test/s Have Been Completed And Attached To This Checkpoint If Required
checklist-flat |  |  | checklist | Switchboard Post Livening |  |  |  |  | Yes | Switchboard Post Livening | 6cd7135e-2790-402c-b21d-42c9806ff1fa
checkpoint-status |  |  | checkpoint | Confirm Correct Voltage Readings At Bus Bar
checkpoint-status |  |  | checkpoint | Confirm Polarity And Phase Rotation
checkpoint-status |  |  | checkpoint | Confirm Correct Control Voltage Is Present
checkpoint-status |  |  | checkpoint | Confirm All Switching Devices Are Switching Correctly
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
select | 556e33a8-da2e-5095-a934-ed78aa2000f4 |  | dropdown | Test Equipment Used | Fluke 1662, Fluke 1653B
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 24b9d34e-17f3-5e16-9f2b-b99e1adc61a7 |  | textbox | Tested By
text | 0b9fbdaf-b5c4-5d75-b71b-55afaf298a00 |  | textbox | Witnessed By
text | 0e58f391-e4ca-5b78-87b1-b444e49dc8b9 |  | textbox | Date
checklist-flat |  |  | checklist | Switchboard Pre Livening |  |  |  |  | Yes | Switchboard Pre Livening | 6d71dc81-d6bb-49a5-91ed-54394fdc7c4d
checkpoint-status |  |  | checkpoint | Confirm The Switchboard Is Securely Fastened In Accordance With The Installation Manual And Specifications
checkpoint-status |  |  | checkpoint | Confirm That The Switchboard Has An Identification Label Matching The Single Line Diagram
checkpoint-status |  |  | checkpoint | Confirm There Is No Link Between The Earth And Neutral Bars
checkpoint-status |  |  | checkpoint | Confirm That There Is An Earth Bond To The Case Of The Switchboard
checkpoint-status |  |  | checkpoint | Confirm That The Metal Work Is Undamaged And Free Of Corrosion
checkpoint-status |  |  | checkpoint | Confirm That The MCB/Isolator Ratings Match The Switchboard Schedules/SLD
checkpoint-status |  |  | checkpoint | Confirm That All Circuit Terminations Have Phase Identification Fitted
checkpoint-status |  |  | checkpoint | Confirm That All Circuit Schedules Have Been Fitted
checkpoint-status |  |  | checkpoint | Confirm That All Out Going Circuit Breakers Are LOTO Or Tagged Prior To Energizing Submains
checkpoint-status |  |  | checkpoint | Confirm All Gland Plates Are Secure With All Bolts Installed
checkpoint-status |  |  | checkpoint | Confirm All Gland Plates Are Earthed
checkpoint-status |  |  | checkpoint | Confirm All Glands are Tight Allowing No Movement Of Cable Within Gland
checkpoint-status |  |  | checkpoint | Confirm All Bushes Are Sealed If Used As A Wireway To Install Field Cabling
checkpoint-status |  |  | checkpoint | Perform Insulation Resistance At 1000VDC On All Parts Of The Bus Bar Accessed During Installation Process, Consider Load Sides Of Breakers Not Connected When Breakers Open And Any Breaks In The Busbar Through Design. Refer To Shop Drawings And Single Line Diagrams. Rack out/switch off all breakers, remove all control fuses, fault current limiters and disconnect neutral and earth at surge diverters. Remove all RCD Earth and neutral tails. Confirm All Results Above 100MOhm
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
label | 32124c19-959e-5ca5-a972-a184b5d05f47 |  | note | Test Equipment Used - Megger MIT410/2
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | b2e612e5-a5eb-5ce3-98e9-218c0abd7c66 |  | textbox | Tested By
text | e82b2cd4-01eb-50b5-8b59-88115a8b5d2a |  | textbox | Witnessed By
text | b8a59056-eded-56df-b921-b99de0db5d92 |  | textbox | Date
checklist-flat |  |  | checklist | Distribution Board Post-livening Check Sheet - Single Phase DB |  |  |  |  | Yes | Distribution Board Post-livening Check Sheet - Single Phase DB | 6e7b8065-bcf9-4860-bc65-dcaab2d286b2
checkpoint-status |  |  | checkpoint | Confirm pre livening check is complete
checkpoint-status |  |  | checkpoint | Confirm the correct voltage is present
text | 00931431-deff-5f08-a7bb-216043caa2d8 |  | textbox | P-N |  |  | V
text | 27b385bd-8403-51c9-82a4-65797291d252 |  | textbox | P-E |  |  | V
text | a32063db-65b1-5ad9-9271-c42806a19e43 |  | textbox | N-E |  |  | V
checkpoint-status |  |  | checkpoint | Confirm the correct polarity
text | fe61080c-5a4f-5367-9730-8ed59462c278 |  | textbox | P
text | c00f2836-6ad4-56ac-a447-c6a8fc869eb2 |  | textbox | N
checkpoint-status |  |  | checkpoint | Confirm the correct control voltage is present
checkpoint-status |  |  | checkpoint | Confirm all meters/monitoring devices are setup correctly and operational
checkpoint-status |  |  | checkpoint | Confirm control contractors and devices are operating correctly
checkpoint-status |  |  | checkpoint | Confirm all switching devices (ACB's, MCCB's, MCB's etc) are switching correctly
checkpoint-status |  |  | checkpoint | Confirm all auxiliaries are switching correctly
checkpoint-status |  |  | checkpoint | Confirm all adjustable circuit breaker settings are recorded and correct
checkpoint-status |  |  | checkpoint | Confirm switchboard is ready to be put into service
checkpoint-status |  |  | checkpoint | Special Conditions
text | d9157884-5207-58dd-8eca-84c7e6465e85 |  | textbox | Conditions
checkpoint-status |  |  | checkpoint | Tested
text | c0351c19-76de-5d77-86c9-50a361057fcd |  | textbox | Tested By
checkpoint-status |  |  | checkpoint | Confirm Ready To Be Livened
holdpoint |  |  | signoff | Request Confirmation
checklist-flat |  |  | checklist | LP DC QA Script |  |  |  |  | Yes | LP DC QA Script | 78cb51ee-a29b-4443-aac9-ddab1e3d7a25
checkpoint-status |  |  | checkpoint | Visually Inspect All Down Conductors
checkpoint-status |  |  | checkpoint | Confirm Down Conductors Have Been Installed According To Latest IFC Drawings And Any Other Related Documents
checkpoint-status |  |  | checkpoint | Confirm There Is No Visual Damage
checkpoint-status |  |  | checkpoint | All Fixings Seem Secure And Are In Their Original Positions
checkpoint-status |  |  | checkpoint | All Down Conductors Are Fixed With Copper To Copper Or Stainless Steel To Insulated Copper Saddles Similar To FURSE Or Approved Equivalent c/w Phosphor Bronze Screws At Intervals Not Exceeding 1m.
checkpoint-status |  |  | checkpoint | All Down Conductors Are At Least 70mm2 In Size And Are Of Full Length Except For Test Joint Locations
checkpoint-status |  |  | checkpoint | All Connections Are Welded And Where Not Feasible, Bolted. And Protected With Approved Sealant Or Anti Corrosion Paint
checkpoint-status |  |  | checkpoint | All Connections Overlap By At Least 25mm
checkpoint-status |  |  | checkpoint | Confirm Ductor Test Across All Joints Has Taken Place And Satisfactory Results Have Been Recorded
checkpoint-status |  |  | checkpoint | Confirm Resistance To Ground At Each Specified Connection To The Earth Electrode - Measured Via The 'Three Point - Fall Of Potential' Method Has Been Performed And Results Recorded < 1 Ohm
checkpoint-status |  |  | checkpoint | All Test Links Have Been Re - Installed With Continuity Proved Across Link
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | d0966f7c-60b1-5388-a7e7-d8466dc3646c |  | textbox | Tested By
text | 22d25328-9d31-595b-baf3-65897192d67d |  | textbox | Witnessed By
text | fee0b985-c988-57c1-8ad1-048ed11c313a |  | textbox | Date
checklist-flat |  |  | checklist | Switchboard Pre Livening MEN |  |  |  |  | Yes | Switchboard Pre Livening MEN | 91b74e57-f33d-452a-b0c3-f354b2b250bf
checkpoint-status |  |  | checkpoint | Confirm The Switchboard Is Securely Fastened In Accordance With The Installation Manual And Specifications
checkpoint-status |  |  | checkpoint | Confirm That The Switchboard Has An Identification Label Matching The Single Line Diagram
checkpoint-status |  |  | checkpoint | Confirm There Is A Link Between The Earth And Neutral Bars
checkpoint-status |  |  | checkpoint | Confirm That There Is An Earth Bond To The Case Of The Switchboard
checkpoint-status |  |  | checkpoint | Confirm That The Metal Work Is Undamaged And Free Of Corrosion
checkpoint-status |  |  | checkpoint | Confirm That The MCB/Isolator Ratings Match The Switchboard Schedules/SLD
checkpoint-status |  |  | checkpoint | Confirm That All Circuit Terminations Have Phase Identification Fitted
checkpoint-status |  |  | checkpoint | Confirm That All Circuit Schedules Have Been Fitted
checkpoint-status |  |  | checkpoint | Confirm That All Out Going Circuit Breakers Are LOTO Or Tagged Prior To Energizing Submains
checkpoint-status |  |  | checkpoint | Confirm All Gland Plates Are Secure With All Bolts Installed
checkpoint-status |  |  | checkpoint | Confirm All Gland Plates Are Earthed
checkpoint-status |  |  | checkpoint | Confirm All Glands are Tight Allowing No Movement Of Cable Within Gland
checkpoint-status |  |  | checkpoint | Confirm All Bushes Are Sealed If Used As A Wireway To Install Field Cabling
checkpoint-status |  |  | checkpoint | Perform Insulation Resistance At 1000VDC On All Parts Of The Bus Bar Accessed During Installation Process, Consider Load Sides Of Breakers Not Connected When Breakers Open And Any Breaks In The Busbar Through Design. Refer To Shop Drawings And Single Line Diagrams. Rack out/switch off all breakers, remove all control fuses, fault current limiters and disconnect neutral and earth at surge diverters. Remove all RCD Earth and neutral tails. Confirm All Results Above 100MOhm
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
label | 668a1da6-89de-59ef-b6a0-bd55df2781e9 |  | note | Test Equipment Used - Megger MIT410/2
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 95ae914b-8287-5e66-8791-83bab5021eb7 |  | textbox | Tested By
text | 55be9208-648b-5fba-98ca-c9e45e6a5c29 |  | textbox | Witnessed By
text | efd33161-1452-5806-a091-f45a9daa920f |  | textbox | Date
checklist-flat |  |  | checklist | Second Fix |  |  |  |  | Yes | Second Fix | a02ca4be-2983-4369-984e-bc1f5f6f7555
checkpoint-status |  |  | checkpoint | Light fittings installed as per luminaire schedule
checkpoint-status |  |  | checkpoint | Light fittings seismically restrained as per design
checkpoint-status |  |  | checkpoint | All power points installed and cover plates fitted
checkpoint-status |  |  | checkpoint | All Light Switching installed and cover plates fitted
checkpoint-status |  |  | checkpoint | Socket Outlets & Switches, all square and labelled
checkpoint-status |  |  | checkpoint | Lighting Control devices installed
checkpoint-status |  |  | checkpoint | Emergency Lighting, correct lumnaires as per schedule, all fittings individually identified
checkpoint-status |  |  | checkpoint | All equipment isolators installed and cover plates fitted
checkpoint-status |  |  | checkpoint | Complete Earth bonding to sinks, benches etc.
checkpoint-status |  |  | checkpoint | Complete Permanent Connections & final connections to equipment
checkpoint-status |  |  | checkpoint | Ensure circuit labels & signage are fitted
checkpoint-status |  |  | checkpoint | Liaise with testing team to confirm all mandatory electrical tests are completed in this area. (Test results to be record in "COMPASS")
checkpoint-status |  |  | checkpoint | Mark up As Built drawings for completed area
checkpoint-status |  |  | checkpoint | Record Photos (walls & ceiling)
checklist-flat |  |  | checklist | Submain Post Livening Temp |  |  |  |  | Yes | Submain Post Livening Temp | b2824b31-0c72-4546-91e0-d7d021017cac
checkpoint-no-status |  |  | checkpoint | Submain Post Livening Temp
text | f7ada621-39c7-52df-a7bd-63fee8475edd |  | textbox | Submain Supplied From
text | f8e169cc-5e6b-5f83-8700-5ec8ce05d2fc |  | textbox | Submain Supply Run To
select | 8d665a7c-bcb3-5fa8-956a-b05b9949736f |  | dropdown | Supply Cable Type | XLPE Cu, XLPE Fire Rated Cu
text | 1ce58409-adc0-5f76-a747-1651b5b2f4d4 |  | textbox | Supply Cable Size
select | 264edd22-d849-5ce9-9988-3e150a2f2366 |  | dropdown | Earth Cable Type | PVC
text | 31e8aa11-5dd5-5cf0-821e-642afe64f1a5 |  | textbox | Earth Cable Size
select | 5ab17254-7e03-5ac3-9006-4edd97656007 |  | dropdown | Single Core Or Multicore | Single Core, Multicore
text | df2a3274-88f4-5d83-9e33-6b6721f84d15 |  | textbox | Number Of Parallel Sets Of L1, L2, L3
text | 42986376-6981-59fe-aa54-cddb5f576285 |  | textbox | Number Of Parallel Sets Of N
text | 303ce15b-a7f1-5c86-adaf-88e051a5605c |  | textbox | Number Of Parallel Sets Of E
text | 5fb3f278-8820-5c21-9fde-c5ae7f958483 |  | textbox | Breaker Size At MSB
text | 6516a0b4-5eb5-5a41-bbcf-d66e98bb5366 |  | textbox | Record Size Breaker Is Set To
text | d796fde6-6873-5121-a451-e1078ee29609 |  | textbox | Record KA Rating Of Breaker
text | 9a4c5985-f00f-5d06-a28a-1f3ba6c8c68b |  | textbox | Test And Record Voltage Readings - Red To White
text | 4a2c0f2b-04f3-549f-9fd6-9f1d8a17e07e |  | textbox | Red To Blue
text | 7363ff6e-d5fc-5411-8f34-5b3ad879f35b |  | textbox | Red To Neutral
text | ea9e2849-5da9-59e1-8d5a-e56d80e8c280 |  | textbox | Red To Earth
text | ea1a1242-d280-579b-b760-f3eccf212a99 |  | textbox | White To Blue
text | 0b5d1dab-b116-59ff-984e-73462e987f20 |  | textbox | White To Neutral
text | 69c212a2-2cee-57be-9c2d-5a722ef6b8ba |  | textbox | White To Earth
text | 37408ccc-ae94-5017-8ed6-4ba627bcc178 |  | textbox | Blue To Neutral
text | ecd17846-ffe6-52f4-a0f9-3cffb0503ed5 |  | textbox | Blue To Earth
text | 06de7a2b-2977-5e5f-a3e2-3799211c2592 |  | textbox | Neutral To Earth
checkpoint-status |  |  | checkpoint | Confirm Phase Rotation Is Correct
checkpoint-status |  |  | checkpoint | Perform and Record The Following
text | b8b9496b-9e34-5324-a0df-218cb20943f8 |  | textbox | Red To Earth EFLI
text | bb6c65e6-9c69-5fa1-9967-fe297f84a26a |  | textbox | Red To Earth PFC
text | 52ce086b-3887-59b0-9852-4aa845c910e3 |  | textbox | White To Earth EFLI
text | e1f29ba5-b3d9-5fd4-8e01-246c066d0b7b |  | textbox | White To Earth PFC
text | b6784484-b2c9-5442-bea0-fc4470a4d9b0 |  | textbox | Blue To Earth EFLI
text | 555baabf-fc68-57b4-a799-06ce30e9af2c |  | textbox | Blue To Earth PFC
text | 1a47b007-3ac8-568f-9e9c-9bbc6c301b62 |  | textbox | Red To Neutral EFLI
text | 93b55753-3e02-5b79-8af1-8d3649fe55a8 |  | textbox | Red To Neutral PFC
text | 24cb20f0-a6fe-5f1b-a09f-ee6e4fcf4b0a |  | textbox | White To Neutral EFLI
text | 2f99859e-9cf5-512e-bb1f-a73834ab51de |  | textbox | White To Neutral PFC
text | c8487bd3-a640-5538-bda9-77ac10319d00 |  | textbox | Blue To Neutral EFLI
text | 1073c3cd-9f7b-537b-8220-0b7121f89b86 |  | textbox | Blue To Neutral PFC
checkpoint-status |  |  | checkpoint | Perform and Record The Following
text | fb34a7eb-4b98-5e5d-9ae5-ab04f448a2f5 |  | textbox | Red To White Loop Impedance
text | e3b41299-ad6d-5e1c-99e6-4519ea266df2 |  | textbox | Red To White PSCC
text | 22d49735-5cbd-56d4-b227-0786d2841f03 |  | textbox | Red To Blue Loop Impedance
text | 4ee91e5c-a8ab-5f2d-862d-11f28ec7a35d |  | textbox | Red to Blue PSCC
text | 24caceb6-36f2-5ff8-8beb-e6a074e46210 |  | textbox | White To Blue Loop Impedance
text | ce03faca-42b4-523b-abbc-2f6cb301022a |  | textbox | White To Blue PSCC
select | 89b287d1-c350-5edb-8f16-e6d053e31616 |  | dropdown | Test Equipment Used | Fluke 1662, Fluke 1653B
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 7db78efc-cf5c-5d36-b7f7-8f29143ca38c |  | textbox | Tested By
text | c11bc49a-c765-5880-9c5d-5c5c3d2c32f7 |  | textbox | Witnessed By
text | 10070606-363d-5beb-95ae-bb3f7a6cc4ae |  | textbox | Date
checklist-flat |  |  | checklist | Subcircuit Post Livening |  |  |  |  | Yes | Subcircuit Post Livening | b2d13989-ae33-4a8a-a785-34b4f6121fff
checkpoint-status |  |  | checkpoint | Subcircuit Post Livening Test/s Have Been Completed And Attached To This Checkpoint If Required
checkpoint-status |  |  | checkpoint | All results on uploaded document pass AS/NZS 3000 and NETA ATS specifications
checklist-flat |  |  | checklist | Bus Duct Post Livening |  |  |  |  | Yes | Bus Duct Post Livening | b6e57bc2-5772-4918-83f4-c14483c5ba6e
checkpoint-status |  |  | checkpoint | Confirm Correct Voltage Readings, Polarity And Phase Rotation At All Tap Off Boxes And End Feed Unit
text | 4607625a-2fa1-531c-a613-d09b8e49ea18 |  | textbox | Test And Record Voltage Readings At End Of Bus Duct - Tap Off Box - Red To White
text | 7cc7f9bb-68ad-5c14-a751-0b23ee406095 |  | textbox | Red To Blue
text | 693518fb-5861-52fe-973e-685505eecaa6 |  | textbox | Red To Neutral
text | f34de00a-555c-5818-9f93-8a5d2a16bae0 |  | textbox | Red To Earth
text | ef27132c-8992-51a4-9fde-44badb360a32 |  | textbox | White To Blue
text | 35f2e336-d8c3-5f87-8613-eeb88f6d150b |  | textbox | White To Neutral
text | 75fe71c2-37ed-565e-aecc-ad982bca3a3e |  | textbox | White To Earth
text | 36bb0dbe-4f27-5779-9004-9cb8967a65cf |  | textbox | Blue To Neutral
text | 016237dc-f808-54b5-9624-229defcf8a79 |  | textbox | Blue To Earth
text | bf5843bb-ea0c-52d7-906f-e2429ed91c62 |  | textbox | Neutral To Earth
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
select | d9af3684-cc03-5c81-a95d-f831ce7d1149 |  | dropdown | Test Equipment Used | Fluke 1662, Fluke 1653B
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 84b8b587-e5f0-5d82-bfab-969fac293dcd |  | textbox | Tested By
text | 361a6992-6ff3-5eca-a8f5-77b7f8b91924 |  | textbox | Witnessed By
text | adc779b1-c7e6-56cd-8ce3-231893eafc6a |  | textbox | Date
checklist-flat |  |  | checklist | Date: |  |  |  |  | Yes | Site Diary 1 | bd564c65-36a8-416e-a794-1f6e759a99d4
checkpoint-status |  |  | checkpoint | Details
text | c8f1ae83-0dbb-5d81-97c6-0e72f690fd4a |  | textbox | Name of person taking toolbox
button | a3aae53d-45da-5a4a-aaf5-5665077fd1fe |  | button | Any safety concerns raised from previous days work? (If Yes please detail) | Yes, No
checkpoint-status |  |  | checkpoint | Attendees: list or take photo
checkpoint-status |  |  | checkpoint | Todays Work:
checkpoint-status |  |  | checkpoint | Hazards & Controls
label | d67f4092-ca8e-56c1-b3c8-a25bad9ac531 |  | note | Please select relevant hazard and control, or list others
boolean | 88cad34b-74b8-5b16-b111-66656989143e |  | tickbox | Hazard - EWP
boolean | d0ca61c4-2c37-59d7-aa87-8ca57a6ec9a3 |  | tickbox | Control - Have a spotter; Cordon area off below
boolean | a13dd517-376c-56e7-a6bd-c07e70902bc6 |  | tickbox | Hazard - Live Power
boolean | aaa24036-2fdf-5680-a486-f3f9c60d876f |  | tickbox | Control - Isolate where possible; Test - (Prove-Test-Prove)
boolean | f9a91d32-fddd-5e45-8b09-1c2531a92113 |  | tickbox | Hazard - Objects dropping from above
boolean | 4664efaf-d9eb-5881-933a-31aedbcbd1cc |  | tickbox | Control - Codon off area; Be aware of works above
boolean | 4776055a-e0d8-516b-bbd7-b7f9be92b205 |  | tickbox | Hazard - Cranes working above
boolean | 2c2123a4-5142-5bf5-b08f-b4dd61e92dd4 |  | tickbox | Control - Look up; Do not enter lift areas during lifts; Follow Dog-Mens instructions
boolean | 50f345c7-0344-5287-bd5e-a53496def774 |  | tickbox | Hazard - Noise
boolean | 3ebfac40-05c0-56e6-a810-7a9e6b95f66f |  | tickbox | Control - PPE - Earmuffs/Plugs
boolean | 1c9a4544-d94b-53e8-ad6c-7764f4b9994e |  | tickbox | Hazard - Dust
boolean | 73838533-9245-53b4-8c61-3487d2192f5e |  | tickbox | Control - PPE - Dustmaks/Respirator
boolean | 9911122d-b964-5522-84b0-897dea73274c |  | tickbox | Hazard - Trip Hazards
boolean | b8f31236-87e3-5c0c-827a-44701a5db41a |  | tickbox | Control - Be aware; Clean up after yourself; Report
text | 1dc2cb00-03d5-5e0d-84ac-f83c09a00e03 |  | textbox | List others:
checkpoint-status |  |  | checkpoint | Scope of work understood by all
checkpoint-status |  |  | checkpoint | PPE in good condition
checkpoint-status |  |  | checkpoint | Plant & equipment in good condition & tagged (as required)
checkpoint-status |  |  | checkpoint | Access equipment in good condition & safe to use
checkpoint-status |  |  | checkpoint | List any other concerns
checklist-flat |  |  | checklist | EM Lighting Commissioning |  |  |  |  | Yes | EM Lighting Commissioning v2 | c275929c-d793-4d45-8fcd-9577499d6d11
checkpoint-status |  |  | checkpoint | Emergency Lighting Commissioning Test sheet Has Been Completed And Attached To This Checkpoint
checkpoint-status |  |  | checkpoint | All results on uploaded document pass AS/NZS 3000 and NETA ATS specifications
checklist-flat |  |  | checklist | PanelBoard L2 Vendor |  |  |  |  | Yes | PanelBoard L2 Vendor | c6c99d49-b1da-424a-95ff-76ec8e22889e
checkpoint-status |  |  | checkpoint | Confirm Switchboard Location Complies With AS/NZS3000 Minimum Safe Distances And Clearances
checkpoint-status |  |  | checkpoint | Verify Area Is Clean Of Debris And Foreign Objects
checkpoint-status |  |  | checkpoint | All Packaging, Rubbish And Trash Has Been Removed From Installation Site
checkpoint-status |  |  | checkpoint | Confirm Adequate Lighting Has Been Provided
checkpoint-status |  |  | checkpoint | Confirm Door/Swing Out Compartments Are Level, No Missing Pieces
checkpoint-status |  |  | checkpoint | Verify Fuses Installed Are Correct Sizes
checkpoint-status |  |  | checkpoint | Verify Barriers/Masking Panels Are Present And Installed Correctly
checkpoint-status |  |  | checkpoint | Inspect Bus Insulators
checkpoint-status |  |  | checkpoint | Inspect Power Cables
checkpoint-status |  |  | checkpoint | Inspect Doors, Covers, Gaskets
checkpoint-status |  |  | checkpoint | Inspect Phase Barriers (When Applicable)
checkpoint-status |  |  | checkpoint | Confirm Grounding
checkpoint-status |  |  | checkpoint | Switchboard Components - Verify All Electrical Components Are Correctly Mounted And Fixed Securely
checkpoint-status |  |  | checkpoint | Inspect Indicator Lamps
checkpoint-status |  |  | checkpoint | Inspect Sub Circuit And Control Wiring - Pull Test On Wire Connections
checkpoint-status |  |  | checkpoint | Verify All Panels And Covers Are Fixed. Doors Function Smoothly
checkpoint-status |  |  | checkpoint | Confirm Circuit Identification Is Visible On Masking Panel Or Front Of Switchboard
checkpoint-status |  |  | checkpoint | Verify/Inspect Breakers For Damage
checkpoint-status |  |  | checkpoint | Verify Breaker Type, Sizes And KA Rating Against Approved Circuit Schedule
checkpoint-status |  |  | checkpoint | Operate Breakers/Isolators And Check For Smooth Operation
checkpoint-status |  |  | checkpoint | Confirm All Required Switchboard Blanks Have Been Installed
checkpoint-status |  |  | checkpoint | Tested By
text | 0ce0abeb-18d8-5b7f-ad7f-61ed7574ff64 |  | textbox | Tested By
text | 6d2b1a00-fa71-5c6b-8963-f57930cac8c3 |  | textbox | Witnessed By
text | 4cfce42d-105a-555b-8721-94c0d3fbda40 |  | textbox | Date
checklist-flat |  |  | checklist | ATS Pre Livening |  |  |  |  | Yes | ATS Pre Livening | d7414c71-9e3a-45d1-9674-f9a2e8cbe694
checkpoint-status |  |  | checkpoint | Confirm The ATS Is Securely Fastened In Accordance With The Installation Manual And Specifications
checkpoint-status |  |  | checkpoint | Confirm That The ATS Has An Identification Label Matching The Single Line Diagram
checkpoint-status |  |  | checkpoint | Confirm There Is No Link Between The Earth And Neutral Bars
checkpoint-status |  |  | checkpoint | Confirm That There Is An Earth Bond To The Case Of The ATS
checkpoint-status |  |  | checkpoint | Confirm That The Metal Work Is Undamaged And Free Of Corrosion
checkpoint-status |  |  | checkpoint | Confirm That The MCB/Isolator Ratings Match The Switchboard Schedules/SLD
checkpoint-status |  |  | checkpoint | Confirm That All Circuit Terminations Have Phase Identification Fitted
checkpoint-status |  |  | checkpoint | Confirm That All Circuit Schedules Have Been Fitted
checkpoint-status |  |  | checkpoint | Confirm That All Out Going Circuit Breakers Are LOTO Or Tagged Prior To Energizing Submains
checkpoint-status |  |  | checkpoint | Confirm All Gland Plates Are Secure With All Bolts Installed
checkpoint-status |  |  | checkpoint | Confirm All Gland Plates Are Earthed
checkpoint-status |  |  | checkpoint | Confirm All Glands are Tight Allowing No Movement Of Cable Within Gland
checkpoint-status |  |  | checkpoint | Confirm All Bushes Are Sealed If Used As A Wireway To Install Field Cabling
checkpoint-status |  |  | checkpoint | Perform Insulation Resistance At 500VDC On The ATS With The Switch Closed On Normal To Load. Confirm All Results Above 100MOhm
checkpoint-status |  |  | checkpoint | Perform Insulation Resistance At 500VDC On The ATS With The Switch Closed On Emergency To Load. Confirm All Results Above 100MOhm
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
label | d41132c9-0edc-5724-bdba-162229d2f621 |  | note | Test Equipment Used - Megger MIT410/2
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 4bb5ed61-c874-55b3-897f-a2016f0106e6 |  | textbox | Tested By
text | 1adb80f4-b86e-5e2a-a018-36d58d484684 |  | textbox | Witnessed By
text | 9ae4e7e5-b0e3-5fa0-a152-9a53913b8a88 |  | textbox | Date
checklist-flat |  |  | checklist | EM Lighting Commissioning |  |  |  |  | Yes | EM Lighting Commissioning | dabb3d99-a6b3-4711-be9a-311878dd17a7
checkpoint-status |  |  | checkpoint | Emergency Lighting Commissioning Test sheet Has Been Completed And Attached To This Checkpoint
checklist-flat |  |  | checklist | Main Switchboard Pre Livening |  |  |  |  | Yes | Main Switchboard Pre Livening | db86e1af-937b-40e8-9934-191dba9756b1
checkpoint-status |  |  | checkpoint | Confirm MSB Is Securely Fastened In Accordance With The Installation Manual And Specifications
checkpoint-status |  |  | checkpoint | Confirm The MEN Link Is Installed
checkpoint-status |  |  | checkpoint | Confirm That The MSB Has An Identification note Matching The Single Line Diagram
checkpoint-status |  |  | checkpoint | Confirm That There Is An Earth Bond To The Case Of The Switchboard
checkpoint-status |  |  | checkpoint | Confirm That All Hinged Doors Are Earthed
checkpoint-status |  |  | checkpoint | Confirm That The Metal Work Is Undamaged And Free Of Corrosion
checkpoint-status |  |  | checkpoint | Confirm That The MCB/Isolator Ratings Match The Switchboard Schedules/SLD
checkpoint-status |  |  | checkpoint | Confirm That All Circuit Terminations Have Phase Identification Fitted
checkpoint-status |  |  | checkpoint | Confirm That All Circuit Schedules Have Been Fitted
checkpoint-status |  |  | checkpoint | Confirm That All Out Going Circuit Breakers Are LOTO Or Tagged Prior To Energizing Submains
checkpoint-status |  |  | checkpoint | Confirm All Gland Plates Are Secure With All Bolts Installed
checkpoint-status |  |  | checkpoint | Confirm All Gland Plates Are Earthed
checkpoint-status |  |  | checkpoint | Confirm All Glands are Tight Allowing No Movement Of Cable Within Gland
checkpoint-status |  |  | checkpoint | Perform Insulation Resistance At 1000VDC On All Parts Of MSB Bus Bar Accessed During Installation Process, Consider Load Sides Of Breakers Not Connected When Breakers Open And Any Breaks In The Busbar Through Design. Refer To Shop Drawings And Single Line Diagrams. Rack out/switch off all breakers, remove all control fuses, fault current limiters and disconnect neutral and earth at surge diverters. Remove all RCD Earth and neutral tails. Confirm All Results Above 100MOhm
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
label | 71d2bb78-97be-5337-a9a6-f6810582c072 |  | note | Test Equipment Used: Megger MIT410/2
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | a585b41a-aacb-5740-a2bf-6f987c68881d |  | textbox | Tested By
text | ca15e850-7d54-5d40-9b64-ebe30a7be43d |  | textbox | Witnessed By
text | 7295ed44-c800-51c4-a1bb-70974f31b9aa |  | textbox | Date
checklist-flat |  |  | checklist | XFM Pre Livening |  |  |  |  | Yes | XFM Pre Livening | dc673a39-2061-4c72-9291-0a14bbc2584b
checkpoint-status |  |  | checkpoint | Checks At MSB - Confirm Mains Supply Gland Plate is Secure With All Bolts Installed
checkpoint-status |  |  | checkpoint | Confirm Mains Supply Gland Plate is Earthed
checkpoint-status |  |  | checkpoint | Confirm Mains Supply Glands are Tight Allowing No Movement Of Cable Within Gland
checkpoint-status |  |  | checkpoint | Confirm Mains Supply Cables Are Secured Within Wireway To Bus Bar
checkpoint-status |  |  | checkpoint | Confirm There Is An Earth To The Body Of The Switchboard
checkpoint-status |  |  | checkpoint | Confirm The Main Earth Has Been Tested At The MSB And That It Has Shown A Result >1 Ohm
checkpoint-status |  |  | checkpoint | Confirm The Main Earth Is noteled
checkpoint-status |  |  | checkpoint | Confirm Phase Identification Is Fitted
checkpoint-status |  |  | checkpoint | Confirm The MEN Link Is Installed
checkpoint-status |  |  | checkpoint | Confirm The Main Breaker Compartment Is Clean And Free Of Dust, Debris And Swarf
checkpoint-status |  |  | checkpoint | Confirm All Out Going Breakers Of The MSB Are LOTO
checkpoint-status |  |  | checkpoint | Perform Insulation Resistance At 1000VDC On All Parts Of MSB Bus Bar Accessed During Installation Process Of The XFM Mains Supply, Consider Load Sides Of Breakers Not Connected When Breakers Open And Any Breaks In The Busbar Through Design. Refer To Shop Drawings And Single Line Diagrams. Rack out/switch off all breakers, remove all control fuses, fault current limiters and disconnect neutral and earth at surge diverters. Remove all RCD Earth and neutral tails. Confirm All Results Above 100MOhm
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
label | f5bfd9c2-5652-5554-a754-0534069c5d9f |  | note | Test Equipment Used - Megger MIT410/2
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 114678bf-db22-5366-90f2-16b6c23b045e |  | textbox | Tested By
text | c6d008ee-aa13-5da2-9cd5-b59d6e31fbb2 |  | textbox | Witnessed By
text | 7aa97f7b-1ac6-5c1b-bb26-7f81d825aacc |  | textbox | Date
checklist-flat |  |  | checklist | Switchboard Post Livening Temp |  |  |  |  | Yes | Switchboard Post Livening Temp | e0137e3b-f603-465c-91aa-cae60ec2ccea
checkpoint-no-status |  |  | checkpoint | Switchboard Post Livening Temp
text | 8abdb668-8a1c-52e9-9e83-405dd0735011 |  | textbox | Switchboard ID
text | 7b15d72b-aa11-5ea8-b11c-3506bece8e85 |  | textbox | Switchboard Location
checkpoint-status |  |  | checkpoint | Confirm Correct Voltage Readings At Bus Bar
checkpoint-status |  |  | checkpoint | Confirm Polarity And Phase Rotation
checkpoint-status |  |  | checkpoint | Confirm Correct Control Voltage Is Present
checkpoint-status |  |  | checkpoint | Confirm All Switching Devices Are Switching Correctly
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
select | 8538aab2-e489-5bda-9dcd-a025e216ba95 |  | dropdown | Test Equipment Used | Fluke 1662, Fluke 1653B
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 0a597b79-3fc9-5b0f-a9a1-e94adf2ad0e0 |  | textbox | Tested By
text | 1dbd84da-7fb8-5a6e-ac44-3673c0700c41 |  | textbox | Witnessed By
text | e914ee13-52d3-5eb4-82b0-17c4635eed51 |  | textbox | Date
checklist-flat |  |  | checklist | Electrical Checks - Site Diary |  |  |  |  | Yes | Electrical Checks - Site Diary | e1a4ce9f-f1ef-47af-aa61-f7088d2d5df1
checkpoint-status |  |  | checkpoint | Site Information
text | 61151e3b-ef7c-5e29-9657-b22b618c5577 |  | textbox | Diary Ref No. "SD"
text | e4ae522a-1361-5e5d-ac9d-81786a74eb81 |  | textbox | Date
select | 0421a587-8300-5d89-8d75-af5320c50f94 |  | dropdown | Area | Cell 1, Cell 2, Cell 3, Cell 4, Admin GF, Admin L1, Fuel Farm, Pump house, Exterior N, Exterior S, Exterior E, Exterior W
select | 41094d31-f30e-5f0b-8c54-7af4d108fbdc |  | dropdown | Location | Cell, MSB Rm, Transformer, Generator, Mech Gallery, Spine
checkpoint-status |  |  | checkpoint | Safety Issues
button | ec5e1390-36bd-5775-b52a-31fd83d825de |  | button | Safety Issues | Nothing to report, Refer comments below
text | f0f7b7d4-10d0-5ce3-8170-512f1bcbbbcd |  | textbox | Safety Comments
checkpoint-status |  |  | checkpoint | Conditions
button | 87adba04-4f83-5020-8982-05c32dfb683c |  | button | Conditions | Clean, Clean & Dry, Suitable to commence work, Action required
text | 7d3dc217-597c-5c08-afba-9411b4478c66 |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Program
button | cbbbee33-29af-58e4-8fcd-469234ea6cb6 |  | button | Status | Not Ready,Ready to Start, WIP, Refer Issues
text | 09c1da0c-123d-5e60-ab38-4c58db29518f |  | textbox | Program ID
text | 3f776330-e411-5492-a873-8cee8f480c5e |  | textbox | Program Start Date
text | be1c473c-1bbb-5fb4-b4fd-d727a6f0f479 |  | textbox | Program Duration
text | b27dd563-da5b-5892-861f-d99d084a00b8 |  | textbox | Program Completion Date
text | acd56ed7-fb41-5a48-8c6a-9b9414791137 |  | textbox | Comments
checklist-flat |  |  | checklist | Equipment Installed Script |  |  |  |  | Yes | Equipment Installed Script | e483c96b-4c7d-4c25-8f7d-e0621e0a5bfc
checkpoint-status |  |  | checkpoint | Confirm That Equipment Is Installed According To Installation Manual And Is Ready For Red Tag Sign Off
text | ca4bc80c-c8d2-5ec1-9d1c-a581c9c6aeed |  | textbox | Comment
text | f563a9e7-2ebf-5575-8a55-6d946d40f22d |  | textbox | Date
text | 50016b9c-fe02-52d4-845d-65cfa081550b |  | textbox | Comment
text | e5733e08-9848-5496-8a18-bfd9a24fbb76 |  | textbox | Date
text | 90745295-04f0-5707-9891-35e9599603cb |  | textbox | Confirmed By
text | ca12129a-e4e3-51f5-b612-61efc8b6470b |  | textbox | Date
checklist-flat |  |  | checklist | Mains/Submain Installation Check Sheet |  |  |  |  | Yes | Mains/Submain Installation Check Sheet | e4d9fa81-6480-4287-8165-060190b545e3
checkpoint-no-status |  |  | checkpoint | Cable Ref
text | 42d5e370-ee4d-549a-aa5d-c3bcde046c8a |  | textbox | Cable Ref. No.
text | 42c03983-db41-5870-a9fd-ab9b45592d31 |  | textbox | Cable From
text | 334832df-897a-5936-a76f-0f9df01c75ff |  | textbox | Cable To
select | f04a3055-88c4-5d5e-bc72-63870cfd81d8 |  | dropdown | Conductor size mm2 | 16, 25, 35, 50, 70, 95, 120, 150, 185, 240, 300, 400
select | 7081c43c-313f-5a84-bc40-5364fb68d81b |  | dropdown | Single Core Or Multicore | Single Core, Multi Core
select | 3e3b4771-0402-5d42-94c2-cb63c69e8907 |  | dropdown | Conductor Material | CU, Al
select | 72e8d36c-78ef-5335-a591-2fc4d2ac5073 |  | dropdown | Cable Type | XLPE,XLPE Fire Rated, XLPE PVC
text | 2b766693-99ce-5509-80d0-be718d1aa7fa |  | textbox | No Of Parallel Sets Of L1, L2, L3
text | b9bde8ff-f61c-56bb-b874-1e1ae0b05bfd |  | textbox | No Of Parallel Sets Of N
select | 922ff684-30aa-5769-b332-214106a6914c |  | dropdown | Earth Cable size mm2 | 16, 25, 35, 50, 70, 95, 120, 150
select | af2bb17f-7a84-5d2d-8a4b-31e0f2b0b563 |  | dropdown | Cable Type | PVC
text | 39549595-b9ae-5de4-9ad5-5182429c09f1 |  | textbox | No. Cable Runs
select | 035ff0af-6e29-53dd-9ec3-1924793ed401 |  | dropdown | Cable Installation Progress | 25%, 50%, 75%, 100%
boolean | e56736d5-58f9-573b-a71d-13782d611f78 |  | tickbox | Cable (Source) Labels Fitted
boolean | 1a0b39b3-b1d0-5a3e-a6ca-da2dbb875370 |  | tickbox | Cable (Destination) Labels Fitted
checkpoint-status |  |  | checkpoint | Cable Installation Complete
checkpoint-status |  |  | checkpoint | Cable Termination Complete - Ready For Testing
text | 50874ade-cfaf-5e20-b788-347bb21f3a42 |  | textbox | Checked by
text | 6d837a24-b19d-5fc3-8631-bd2ca0cb825e |  | textbox | Date
boolean | 11625426-4dbc-5e74-a29d-985c8c395798 |  | tickbox | Photo reference
checklist-flat |  |  | checklist | LP DC To Ground Test Script |  |  |  |  | Yes | LP DC To Ground Test Script | e4f246b9-c6ef-4675-b623-ea322cdcface
checkpoint-status |  |  | checkpoint | Visual Inspection
text | fa9e5eec-2cc7-5a2f-bc35-095a1e193c30 |  | textbox | Down Conductor Connection Ref No.
text | c4a7f1da-ac2f-5bde-b2e5-6ad502a7c114 |  | textbox | Comments
select | a7ecbac0-a555-58a9-9dfc-2d606d57dc37 |  | dropdown | Ambient Air Condition | Dry, Humid
select | e908d20e-502a-57fc-8987-1f24431b57b7 |  | dropdown | Ground Condition | Dry,Wet
select | dc83cb8a-1512-5136-a6f9-de7f664ebaae |  | dropdown | Confirm No Rainfall In Past 48 Hours | Yes, No
text | 8b1cacc8-b405-55d3-bf13-c2cb0e67e40a |  | textbox | Other Conditions Or Circumstances To Note At Time Of Test
text | 873f2cd5-06f8-51c8-93f5-477fad2073a2 |  | textbox | Type of Earth Electrode And Type Of Connection Of Down Conductor To It
text | 4bceca04-8ae0-5e24-bf88-ffcca0e01ce4 |  | textbox | Record The Size And Type Of Conductor Installed As The Earth Lead From The Main Earth Electrode To The Down Conductor Test Link And Describe Its Route
checkpoint-status |  |  | checkpoint | Test Performed With Satisfactory Results
text | c2c8bfe2-eb35-5178-b211-3dcbb1208c28 |  | textbox | 3 Point-Fall Of Potential Test, conducted a minimum of three times - Test Results < 1 Ohm
text | ccfe5875-20b3-500f-80cf-2c58f85d7ca9 |  | textbox | Average Of Test Results To Three Decimal Places < 1 Ohm
select | 5469e947-863d-5a0d-9dff-5877044ea301 |  | dropdown | Test Equipment Used | Fluke 1662, Fluke1653B
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 788b2e88-35b7-5770-99b9-8d52b80824d4 |  | textbox | Tested By
text | 8506813a-2699-5f26-b3a4-6e4ac876cc53 |  | textbox | Witnessed By
text | bd416f6a-fd41-5bdf-bc67-481a340d93d4 |  | textbox | Date
checklist-flat |  |  | checklist | Verification Of Cable Size Attachments |  |  |  |  | Yes | Verification Of Cable Size Attachments | e6cd9493-7344-4473-99b5-aeb1743c0c1b
checkpoint-status |  |  | checkpoint | Photo 1
checkpoint-status |  |  | checkpoint | Photo 2
checkpoint-status |  |  | checkpoint | Photo 3
checkpoint-status |  |  | checkpoint | Photo 4
checkpoint-status |  |  | checkpoint | Photo 5
checkpoint-status |  |  | checkpoint | Photo 6
checkpoint-status |  |  | checkpoint | Photo 7
checkpoint-status |  |  | checkpoint | Photo 8
checklist-flat |  |  | checklist | Subcircuit Pre Livening |  |  |  |  | Yes | Subcircuit Pre Livening | e7726cc1-6bce-49f1-97ca-1c2284fdf36d
checkpoint-status |  |  | checkpoint | Subcircuit Pre Livening Test/s Have Been Completed And Attached To This Checkpoint If Required
checkpoint-status |  |  | checkpoint | All results on uploaded document pass AS/NZS 3000 and NETA ATS specifications
checklist-flat |  |  | checklist | Main Earth Bar Script MSB |  |  |  |  | Yes | Main Earth Bar Script MSB | ea0327eb-7a42-4193-b152-e29b7a052f93
checkpoint-status |  |  | checkpoint | Main Earth Bar Label Attached
checkpoint-status |  |  | checkpoint | Both Main Earths Labelled
checkpoint-status |  |  | checkpoint | Visual Inspection
text | fd5480a3-0764-5b97-bbbf-e6f3119cbf6f |  | textbox | Main Earth Bar Identifier
select | 8bbdb066-5a7d-5e49-8b21-5f5baa27bd6e |  | dropdown | Ambient Air Condition | Dry, Humid
select | b3955542-3303-5496-8082-a35a3d06ebbc |  | dropdown | Ground Condition | Dry,Wet
checkpoint-status |  |  | checkpoint | Confirm No Rainfall In Past 48 Hours
text | 902f65ec-1337-55e7-b705-095685879ae5 |  | textbox | Other Conditions Or Circumstances To Note At Time Of Test
text | 6f73e900-afb2-5ae3-a0a8-097336a38e35 |  | textbox | Type of Earth Electrode And Type Of Connections Of Main Earth Leads To It
text | 0a2c5b40-4d9f-54e8-be33-2774834ee56a |  | textbox | Record The Size And Type Of Conductors Installed As The Main Earth Leads From The Main Earth Electrode To The Main Earth Bar And Describe Their Route
checkpoint-status |  |  | checkpoint | Ground Earth Test 1
text | ad9d0a99-be8f-50ba-ad2b-bd4a568515d8 |  | textbox | Main Earth Cable 1 Identifier
text | 6c3f5903-a8e5-5721-86f2-5d2e4eb46175 |  | textbox | 3 Point-Fall Of Potential Test, conducted a minimum of three times - Test Results < 0.5 Ohm - Test 1
text | f4b2ead8-1030-5fc2-8452-62f88b345a9b |  | textbox | Test 2
text | d0b86564-28f9-5396-b196-f8bbe0cfe4a3 |  | textbox | Test 3
text | 5b873c3a-4656-527c-8222-ed55772fae0e |  | textbox | Test 4
text | 38d90906-62d5-5eea-aa58-8dbc7445b151 |  | textbox | Test 5
text | 2d103f1a-8d40-58d5-8e0c-b9319fa3b1aa |  | textbox | Average Of Test Results To Three Decimal Places < 0.5 Ohm
checkpoint-status |  |  | checkpoint | Ground Earth Test 2
text | fc4b17e2-1240-5b68-bce4-d66d60c7b0b3 |  | textbox | Main Earth Cable 2 Identifier
text | e4330bee-4725-51ad-9a64-3175ab3d7c46 |  | textbox | 3 Point-Fall Of Potential Test, conducted a minimum of three times - Test Results < 0.5 Ohm - Test 1
text | d82be397-836d-53c0-bdc0-188deefb329c |  | textbox | Test 2
text | 50ba987f-9adc-5062-b371-e0a3cc7cf1e6 |  | textbox | Test 3
text | aed4807c-adf6-5e45-ba2e-d94615c99e50 |  | textbox | Test 4
text | 0899b079-9aed-5403-9e3e-ba3f764daf69 |  | textbox | Test 5
text | 9f8acc25-1b1c-5e51-89d5-bb894146210d |  | textbox | Average Of Test Results To Three Decimal Places < 0.5 Ohm
checkpoint-status |  |  | checkpoint | Main Earths Torqued at Main Earth Bar
checkpoint-status |  |  | checkpoint | Main Earth Lead Resistance Test
text | 54511c03-5057-5488-9dcf-cfcfd6e7b5f6 |  | textbox | Resistance - Main Earth Lead at MEN to Main Earth Bar < 0.5 Ohms
select | 60b8d56b-5f10-5684-b073-1e076f3fb1ae |  | dropdown | Test Equipment Used | Fluke 1662, Fluke1653B
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 1ee2381c-584e-597a-a4ef-ff33562fd4d2 |  | textbox | Tested By
text | 14eb7ff0-199b-5f1a-9e10-70691e722399 |  | textbox | Witnessed By
text | 6f274de2-5a54-5fb8-81d2-1d4dfc8c1185 |  | textbox | Date
checklist-flat |  |  | checklist | Switchboard L2 Vendor |  |  |  |  | Yes | Switchboard L2 Vendor | ee619373-4ead-4b88-81fa-49f271d24f77
checkpoint-status |  |  | checkpoint | Confirm Switchboard Location Complies With AS/NZS3000 Minimum Safe Distances And Clearances
checkpoint-status |  |  | checkpoint | Verify Area Is Clean Of Debris And Foreign Objects
checkpoint-status |  |  | checkpoint | All Packaging, Rubbish And Trash Has Been Removed From Installation Site
checkpoint-status |  |  | checkpoint | Confirm Adequate Lighting Has Been Provided
checkpoint-status |  |  | checkpoint | Confirm Door/Swing Out Compartments Are Level, No Missing Pieces
checkpoint-status |  |  | checkpoint | Verify Fuses Installed Are Correct Sizes
checkpoint-status |  |  | checkpoint | Verify Barriers/Masking Panels Are Present And Installed Correctly
checkpoint-status |  |  | checkpoint | Inspect Bus Insulators
checkpoint-status |  |  | checkpoint | Inspect Power Cables
checkpoint-status |  |  | checkpoint | Inspect Doors, Covers, Gaskets
checkpoint-status |  |  | checkpoint | Inspect Phase Barriers (When Applicable)
checkpoint-status |  |  | checkpoint | Confirm Grounding
checkpoint-status |  |  | checkpoint | Inspect Indicator Lamps
checkpoint-status |  |  | checkpoint | Switchboard Components - Verify All Electrical Components Are Correctly Mounted And Fixed Securely
checkpoint-status |  |  | checkpoint | Inspect Sub Circuit And Control Wiring - Pull Test On Wire Connections
checkpoint-status |  |  | checkpoint | Verify All Panels And Covers Are Fixed. Doors Function Smoothly
checkpoint-status |  |  | checkpoint | Confirm Circuit Identification Is Visible On Masking Panel Or Front Of Switchboard
checkpoint-status |  |  | checkpoint | Verify/Inspect Breakers For Damage
checkpoint-status |  |  | checkpoint | Verify Breaker Type, Sizes And KA Rating Against Approved Circuit Schedule
checkpoint-status |  |  | checkpoint | Operate Breakers/Isolators And Check For Smooth Operation
checkpoint-status |  |  | checkpoint | Inspect/Verify Surge Protection Device Wiring Is Correct And Connected
checkpoint-status |  |  | checkpoint | Inspect CT's For Correct Location, Orientation And Connections
checkpoint-status |  |  | checkpoint | Inspect Control Power Transformer Circuit And Confirm Correct Wiring
checkpoint-status |  |  | checkpoint | Inspect Key Mech And Interlocks
checkpoint-status |  |  | checkpoint | Verify Correct Install Of Cable Thermal Sensors
checkpoint-status |  |  | checkpoint | Tested By
text | 810b7ac1-2a32-51e2-a8f5-2dc23657da58 |  | textbox | Tested By
text | 98f03098-b400-56a7-a671-dd13135eed45 |  | textbox | Witnessed By
text | 1e1ccf23-5f2c-5281-911e-a707c978a2ea |  | textbox | Date
checklist-flat |  |  | checklist | Downstream Earth Bar and Test Link Script |  |  |  |  | Yes | Downstream Earth Bar and Test Link Script | ef89de61-0296-4bc3-8f40-981bf4774f52
checkpoint-status |  |  | checkpoint | All Fields Complete With Satisfactory Results
text | 59b7a207-2c60-5c83-8a9e-99a762779b6d |  | textbox | Earth Bar or Test Link Ref Source
text | 5aee9cf9-fa77-597c-96c3-cddf6ce14de1 |  | textbox | Earth Bar or Test Link Ref Field
select | 80a3b709-b956-5737-9f53-2584071ff970 |  | dropdown | Cable Size | 16mm, 25mm, 35mm, 50mm, 70mm, 95mm, 120mm
text | 7a063872-baee-500a-82ce-90df8aca4a42 |  | textbox | Low Ohm Resistance Test Result
select | 4d465c30-c65f-5b78-b8c5-e714a04d19a4 |  | dropdown | Connection Type Source | cable to cable, cable to earth bar, cable to test link
select | 0415d034-0ded-5a4f-8fc3-a55b7558b645 |  | dropdown | Method | Crimp, Bolt, Clamp, Cad Welded
select | ba725a92-7e6a-527d-a23b-cabac788656c |  | dropdown | Bolt Size | 6mm, 8mm, 10mm, 12mm, N/A
select | beac9650-efb6-5eb1-a89c-61b92997d760 |  | dropdown | Torque Confirmed Source | Pass, Fail, N/A
select | c30586ee-093d-5a59-8f5c-7570d252eced |  | dropdown | Connection Type Field | cable to earth bar, cable to test link
select | 3e747ed9-bcc6-53dd-81b1-aca0fa2aad14 |  | dropdown | Method | Crimp, Bolt, Clamp, Cad Welded
select | 22767795-0954-553d-8214-da636932bc6c |  | dropdown | Bolt Size | 6mm, 8mm, 10mm, 12mm
select | bd5537ad-b8de-52bb-8151-92ef236920c4 |  | dropdown | Torque Confirmed | Pass, Fail, N/A
select | fb420f09-4514-5ca6-98dd-262df1ab5d3a |  | dropdown | Test Equipment Used | Fluke 1662, Fluke1653B
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 04dda4c2-d620-5818-b6df-e8cdea7f15a6 |  | textbox | Tested By
text | dcfcc7b4-ba26-5af7-bbac-5a0ac0d01f3c |  | textbox | Witnessed By
text | cd94c454-6be7-54fc-963e-408072ac5179 |  | textbox | Date
checklist-flat |  |  | checklist | Transformer Pre Livening |  |  |  |  | Yes | Transformer Pre Livening | f5c4c76f-fddb-4fa0-b693-49c6926c7bdc
checkpoint-status |  |  | checkpoint | Confirm The Transformer Is Securely Fastened In Accordance With The Installation Manual And Specifications
checkpoint-status |  |  | checkpoint | Confirm That The Transformer Has An Identification Label Matching The Single Line Diagram
checkpoint-status |  |  | checkpoint | Confirm That There Is An Earth Bond To The Case Of The Transformer
checkpoint-status |  |  | checkpoint | Confirm That The Metal Work Is Undamaged And Free Of Corrosion
checkpoint-status |  |  | checkpoint | Confirm That All Circuit Terminations Have Phase Identification Fitted
checkpoint-status |  |  | checkpoint | Confirm That All Outgoing Circuit Breakers Are LOTO Or Tagged Prior To Energizing Submains
checkpoint-status |  |  | checkpoint | Confirm All Gland Plates Are Secure With All Bolts Installed
checkpoint-status |  |  | checkpoint | Confirm All Gland Plates Are Earthed
checkpoint-status |  |  | checkpoint | Confirm All Glands are Tight Allowing No Movement Of Cable Within Gland
checkpoint-status |  |  | checkpoint | Confirm All Bushes Are Sealed If Used As A Wireway To Install Field Cabling
checkpoint-status |  |  | checkpoint | The Transformer Surroundings And The Accessible Parts Of The Windings Shall Be Vacuum Cleaned
checkpoint-status |  |  | checkpoint | It Shall Then Be Blown Down Using Dry Compressed Air On All The Ventilating Channels
checkpoint-status |  |  | checkpoint | A Further Vacuum Cleaning Shall Be Done To Pick Up All The Loose Dirt
checkpoint-status |  |  | checkpoint | A Lint-Free Cloth Shall Be Used To Clean Up The Winding Surfaces
checkpoint-status |  |  | checkpoint | Hot Dry Air Shall Then Be Blown Into The Core And Winding Assembly Over Several Hours
checkpoint-status |  |  | checkpoint | The Insulation Resistance Should Be Measured Before The Drying Process And At Two (2) Hours Intervals During Drying. Perform Insulation Resistance At 500VDC Winding To Winding And Each Winding To Ground. Confirm All Results Above 100MOhm
checkpoint-status |  |  | checkpoint | The Drying Process May Be Deemed To Be Completed When The Insulation Resistance Levels Off And Remains Relatively Constant For Three Consecutive Two-Hour Readings
checkpoint-no-status |  |  | checkpoint | Before Drying Process Test
text | facfc071-4692-5ab8-832b-a63f7be27069 |  | textbox | Before Drying Process Test 1 - Bridge Primary L1, L2, L3, E And N If Any. Bridge Secondary L1, L2, L3 And N If Any. Test Between And Record Result
text | 49d44376-405d-5680-bf52-a5e20840423a |  | textbox | Before Drying Process Test 2 - Bridge Primary L1, L2, L3 And N If Any. Bridge Secondary L1, L2, L3, E And N If Any. Test Between And Record Result
text | f129ac30-52f5-5ff0-8f88-4c89e931a14f |  | textbox | Before Drying Process Test 3 - Bridge Primary L1, L2, L3 And N If Any. To Secondary L1, L2, L3 And N If Any. And Test This Point To E - Record Result
checkpoint-no-status |  |  | checkpoint | Post Drying 0-2 Hours
text | 671eb61a-335c-5334-a64a-ceecf5149b80 |  | textbox | Post Drying 0-2 Hours. Test 1 - Bridge Primary L1, L2, L3, E And N If Any. Bridge Secondary L1, L2, L3 And N If Any. Test Between And Record Result
text | 81d63317-7502-5c02-bd50-3fe604597051 |  | textbox | Post Drying 0-2 Hours. Test 2 - Bridge Primary L1, L2, L3 And N If Any. Bridge Secondary L1, L2, L3, E And N If Any. Test Between And Record Result
text | 6d876aa8-b0f3-5a78-8452-6a107887a406 |  | textbox | Post Drying 0-2 Hours. Test 3 - Bridge Primary L1, L2, L3 And N If Any. To Secondary L1, L2, L3 And N If Any. And Test This Point To E - Record Result
checkpoint-no-status |  |  | checkpoint | Post Drying 2-4 Hours
text | 6f7e3099-d0e6-595f-993e-db3b2c15e02b |  | textbox | Post Drying 2-4 Hours. Test 1 - Bridge Primary L1, L2, L3, E And N If Any. Bridge Secondary L1, L2, L3 And N If Any. Test Between And Record Result
text | e364e3c9-a1a1-5df6-80df-3daeb7ce99a4 |  | textbox | Post Drying 2-4 Hours. Test 2 - Bridge Primary L1, L2, L3 And N If Any. Bridge Secondary L1, L2, L3, E And N If Any. Test Between And Record Result
text | 6bc0492f-3876-57e0-944d-9aef6de33da2 |  | textbox | Post Drying 2-4 Hours. Test 3 - Bridge Primary L1, L2, L3 And N If Any. To Secondary L1, L2, L3 And N If Any. And Test This Point To E - Record Result
checkpoint-no-status |  |  | checkpoint | Post Drying 4-6 Hours
text | 8edb7394-d4f6-588d-be1d-84be41d8e108 |  | textbox | Post Drying 4-6 Hours. Test 1 - Bridge Primary L1, L2, L3, E And N If Any. Bridge Secondary L1, L2, L3 And N If Any. Test Between And Record Result
text | 8a58a811-936b-5f51-ad28-812c866d5f16 |  | textbox | Post Drying 4-6 Hours. Test 2 - Bridge Primary L1, L2, L3 And N If Any. Bridge Secondary L1, L2, L3, E And N If Any. Test Between And Record Result
text | 66a7a099-ea59-599b-bf03-de294654ea7a |  | textbox | Post Drying 4-6 Hours. Test 3 - Bridge Primary L1, L2, L3 And N If Any. To Secondary L1, L2, L3 And N If Any. And Test This Point To E - Record Result
checkpoint-no-status |  |  | checkpoint | Post Drying 6-8 Hours
text | 9b0782cb-da9f-5c76-90b4-461bd56fc9f5 |  | textbox | Post Drying 6-8 Hours. Test 1 - Bridge Primary L1, L2, L3, E And N If Any. Bridge Secondary L1, L2, L3 And N If Any. Test Between And Record Result
text | 958cb16c-60d3-5a5c-a65e-f7dd661ec003 |  | textbox | Post Drying 6-8 Hours. Test 2 - Bridge Primary L1, L2, L3 And N If Any. Bridge Secondary L1, L2, L3, E And N If Any. Test Between And Record Result
text | 8ea18c70-c50b-5f0b-b9cf-644ce9fcdcb1 |  | textbox | Post Drying 6-8 Hours. Test 3 - Bridge Primary L1, L2, L3 And N If Any. To Secondary L1, L2, L3 And N If Any. And Test This Point To E - Record Result
checkpoint-no-status |  |  | checkpoint | Post Drying 8-10 Hours
text | e8e9feda-4418-5d9e-8497-a0c654e73396 |  | textbox | Post Drying 8-10 Hours. Test 1 - Bridge Primary L1, L2, L3, E And N If Any. Bridge Secondary L1, L2, L3 And N If Any. Test Between And Record Result
text | d16778fb-85e8-55e5-9eef-130149ad5fba |  | textbox | Post Drying 8-10 Hours. Test 2 - Bridge Primary L1, L2, L3 And N If Any. Bridge Secondary L1, L2, L3, E And N If Any. Test Between And Record Result
text | 57f633de-af6e-5f00-8e8e-9cf0f04b089d |  | textbox | Post Drying 8-10 Hours. Test 3 - Bridge Primary L1, L2, L3 And N If Any. To Secondary L1, L2, L3 And N If Any. And Test This Point To E - Record Result
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
label | 10c7b1cc-fb8c-54cd-bf9f-d2fb4f9e4ca8 |  | note | Test Equipment Used - Megger MIT410/2
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | 5c1db329-7a08-5aae-9128-7135310f5057 |  | textbox | Tested By
text | 4203df94-aa2a-59b5-b7f3-e62727bb0784 |  | textbox | Witnessed By
text | 66ff6b64-9a85-5770-8bae-86c44a333da6 |  | textbox | Date
checklist-flat |  |  | checklist | First Fix |  |  |  |  | Yes | First Fix | fa586ace-bc27-45f6-94db-ec764d3b4a3d
checkpoint-status |  |  | checkpoint | Cable Tray / Trunking Completed
checkpoint-status |  |  | checkpoint | Cable tray / trunking, earth bonded, no sharp edges
checkpoint-status |  |  | checkpoint | Catenary Wire complete & supported above ceiling
checkpoint-status |  |  | checkpoint | All cables installed, supported and tied off.
checkpoint-status |  |  | checkpoint | Flush Boxes Position, check electrical and Arch drwgs for plan and elevation locations
checkpoint-status |  |  | checkpoint | Flush Boxes, fire pads fitted where required.
checkpoint-status |  |  | checkpoint | Acoustic sealing if required
checkpoint-status |  |  | checkpoint | Penetrations sealed through fire walls
checkpoint-status |  |  | checkpoint | Penetrations bushed thru metal studs
checkpoint-status |  |  | checkpoint | Earth bonding to sinks, benches etc.
checkpoint-status |  |  | checkpoint | Cables brought out in correct locations for recessed lights
checkpoint-status |  |  | checkpoint | Cables brought out in correct locations for surface lights
checkpoint-status |  |  | checkpoint | Circuit IDs, check cable marking vs drwg & DB schedule
checkpoint-status |  |  | checkpoint | PIR Lighting Control cabling installed
checkpoint-status |  |  | checkpoint | Check that all in-ceiling services are connected and there are no loose cables.
checkpoint-status |  |  | checkpoint | All Conduits installed, saddled correctly, box lids fitted
checkpoint-status |  |  | checkpoint | Walls ready for lining
checkpoint-status |  |  | checkpoint | Ceiling ready for lining
checkpoint-status |  |  | checkpoint | Remove rubbish, surplus materials & plant
checkpoint-status |  |  | checkpoint | Ensure area is clean and tidy ready for next trade
checkpoint-status |  |  | checkpoint | Record Photos (walls & ceiling)
checklist-flat |  |  | checklist | XFM/GEN Cable Pre Livening |  |  |  |  | Yes | XFM/GEN Cable Pre Livening | fb166699-0243-4a95-8599-617e7721430e
checkpoint-no-status |  |  | checkpoint | Details
label | e4c9d9f1-c2ea-5ca6-a1ac-aec8f796de3e |  | note | Supply Cable Type - XLPE
select | 3194288d-56a2-5495-b595-0d618a678831 |  | dropdown | Supply Cable Size | 240mm2, 400mm2
label | a58d3500-8ef5-5690-8508-f03b1902dff7 |  | note | Earth Cable Type - PVC
label | f6b6e1a2-5234-57b3-8288-b04ab7c5648f |  | note | Earth Cable Size - 150mm2
select | bf01f437-6d48-51a8-b641-3eca7ac6bff1 |  | dropdown | Number Of Parallel Sets Of L1, L2, L3 And N | Three, Six, Nine
text | 230d7b93-cb04-5f97-8233-5fc4167304b5 |  | textbox | Number Of Parallel Sets Of E
label | b2205b8e-9813-51bb-a003-d5a2a9b19146 |  | note | Breaker Size At MSB - 5000A
checkpoint-status |  |  | checkpoint | Complete Visual Inspection Of Cable Installation
checkpoint-status |  |  | checkpoint | Cables Tied In Specified Arrangement
checkpoint-status |  |  | checkpoint | Bending Radius's Correct
checkpoint-status |  |  | checkpoint | No Physical Damage To Outer Sheaths
checkpoint-status |  |  | checkpoint | Phase Identification Is Fitted
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For Red Phase
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For White Phase
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For Blue Phase
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For Neutral
checkpoint-status |  |  | checkpoint | Test And Confirm Continuity For Earth
checkpoint-status |  |  | checkpoint | Perform Insulation Resistance At 1000VDC And Confirm All Results Above 100MOhm
text | 93aa2e82-90d5-54cd-9276-05667fff9d1b |  | textbox | Red To White
text | 00f69a59-3ffe-5ed4-9427-ece2c233936d |  | textbox | Red To Blue
text | d4a0e4dd-9f87-5c5a-bd62-4c5d6d60fbf1 |  | textbox | Red To Neutral
text | de1eefd3-a4eb-5970-869d-c7c51b44f725 |  | textbox | Red To Earth
text | 4a3b6adb-933d-5816-b0c0-57569c3400c1 |  | textbox | White To Blue
text | eba06808-e888-52c6-a4ac-1c06fb6b87ed |  | textbox | White To Neutral
text | b5f6b7cd-8175-5ad3-93e6-61f4275f3cd2 |  | textbox | White To Earth
text | 8696e225-89a3-5aa5-b446-050b13a51846 |  | textbox | Blue To Neutral
text | 3cebb86b-1f4e-5c9c-981e-ed7faa5a57ec |  | textbox | Blue To Earth
text | 6c3b4849-112c-5f37-a48f-283466829089 |  | textbox | Neutral To Earth
checkpoint-status |  |  | checkpoint | All Cables Torqued And Marked
text | 178d7d7e-9ac6-5ce4-948b-da78063ed298 |  | textbox | Record Torque Value At Supply - Red
text | 640e4f47-5439-53b1-9e43-6891078e3084 |  | textbox | White
text | b303a5f6-e9f6-5a64-98f0-0f4c0673dd45 |  | textbox | Blue
text | 0b0fe33b-ac9f-540d-a39f-a2917ca6db5a |  | textbox | Neutral
text | 42c231b0-55a7-5b99-9349-d04d0e8c33bf |  | textbox | Earth
text | e3959855-4efd-5b35-9aef-10abb24fb320 |  | textbox | Record Torque Value At Load - Red
text | a0cc279d-ada5-5ad2-9e73-6c2459cfb98f |  | textbox | White
text | 6592c4aa-381a-5000-a102-5a3249562aeb |  | textbox | Blue
text | 1b9e4b0a-1f68-5144-9d20-b70b57c923f9 |  | textbox | Neutral
text | 5239d444-ce35-5695-9277-5eac0d1ec0d6 |  | textbox | Earth
checkpoint-status |  |  | checkpoint | Confirm Contact Resistance Testing Sheet Has Been Completed And Attached To This Checkpoint
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
label | b1e2f19b-d190-54c3-9e2d-05fef0866ceb |  | note | Test Equipment Used: Megger MIT410/2
label | 2653c779-f6b3-569a-8122-0e2943b00c41 |  | note | Test Equipment Used: Megger DLRO10X
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | aa7f397e-8aa5-534a-839e-6b94d0c86f2d |  | textbox | Tested By
text | 178250d4-5371-55a0-8465-a345a569ecdd |  | textbox | Witnessed By
text | a3d3f389-cc20-536c-a381-83ed5a013a22 |  | textbox | Date
checklist-flat |  |  | checklist | GEN Pre Livening |  |  |  |  | Yes | GEN Pre Livening | fbc2eeab-0939-4ad2-b244-52226206a284
checkpoint-status |  |  | checkpoint | Checks At MSB - Confirm Mains Supply Gland Plate is Secure With All Bolts Installed
checkpoint-status |  |  | checkpoint | Confirm Mains Supply Gland Plate Is Earthed
checkpoint-status |  |  | checkpoint | Confirm Mains Supply Glands Are Tight Allowing No Movement Of Cable Within Gland
checkpoint-status |  |  | checkpoint | Confirm Mains Supply Cables Are Secured Within Wireway To Bus Bar
checkpoint-status |  |  | checkpoint | Confirm There Is An Earth To The Body Of The Switchboard
checkpoint-status |  |  | checkpoint | Confirm Phase Identification Is Fitted
checkpoint-status |  |  | checkpoint | Confirm The Main Earth Has Been Tested And That It Has Shown A Result >1 Ohm
checkpoint-status |  |  | checkpoint | Confirm The Main Earth Is noteled
checkpoint-status |  |  | checkpoint | Confirm The MEN Link Is Installed
checkpoint-status |  |  | checkpoint | Confirm The Main Breaker Compartment Is Clean And Free Of Dust, Debris And Swarf
checkpoint-status |  |  | checkpoint | Confirm All Out Going Breakers Of The MSB Are LOTO
checkpoint-status |  |  | checkpoint | Checks At GEN - Confirm Gland Plate is Secure With All Bolts Installed
checkpoint-status |  |  | checkpoint | Confirm Gland Plate is Earthed
checkpoint-status |  |  | checkpoint | Confirm Glands are Tight Allowing No Movement Of Cable Within Gland
checkpoint-status |  |  | checkpoint | Confirm Cables Are Secured Within Wireway To Bus Bar
checkpoint-status |  |  | checkpoint | Confirm There Is An Earth To The Body Of The Switchboard
checkpoint-status |  |  | checkpoint | Confirm Phase Identification Is Fitted
checkpoint-status |  |  | checkpoint | Confirm The Main Breaker Compartment Is Clean And Free Of Dust, Debris And Swarf
checkpoint-status |  |  | checkpoint | Perform Insulation Resistance At 1000VDC On All Parts Of MSB Bus Bar Accessed During Installation Process Of The GEN Mains Supply, Consider Load Sides Of Breakers Not Connected When Breakers Open And Any Breaks In The Busbar Through Design. Refer To Shop Drawings And Single Line Diagrams. Rack out/switch off all breakers, remove all control fuses, fault current limiters and disconnect neutral and earth at surge diverters. Remove all RCD Earth and neutral tails. Confirm All Results Above 100MOhm
checkpoint-status |  |  | checkpoint | Perform Insulation Resistance At 1000VDC On All Parts Of GEN Bus Bar Accessed During Installation Process Of The GEN Mains Supply, Consider Load Sides Of Breakers Not Connected When Breakers Open And Any Breaks In The Busbar Through Design. Refer To Shop Drawings And Single Line Diagrams. Rack out/switch off all breakers, remove all control fuses, fault current limiters and disconnect neutral and earth at surge diverters. Remove all RCD Earth and neutral tails. Confirm All Results Above 100MOhm
checkpoint-no-status |  |  | checkpoint | Test Equipment Used
label | 54ed6f81-48de-5d14-ae42-9a6136f8e363 |  | note | Test Equipment Used: Megger MIT410/2
checkpoint-status |  |  | checkpoint | Tested and Witnessed
text | a8b4e836-197c-5d4d-a6ca-ff17de5af5f9 |  | textbox | Tested By
text | 1faa8c73-6199-5d2d-9827-e18937628f28 |  | textbox | Witnessed By
text | 5b964d9d-ee11-5cb5-831c-0ae1097c5911 |  | textbox | Date
checklist-flat |  |  | checklist | Earth Bar QA Two Incomers |  |  |  |  | Yes | Earth Bar QA Two Incomers | fcaa32b3-4953-4289-8218-66139ead10c7
checkpoint-no-status |  |  | checkpoint | Earth Bar QA Two Incomers
text | 69340f09-f97a-57e7-a2b6-9b7914f11052 |  | textbox | Earth Bar Identifier
checkpoint-status |  |  | checkpoint | Earth Bar note Attached
checkpoint-status |  |  | checkpoint | Supply Earths noteled
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Incoming Earth 1 Cable Torqued
select | 65aaf573-9616-54a2-bc68-03a6ee29ec5a |  | dropdown | Incoming Earth 1 Cable Type | Insulated PVC
select | 02b295ac-6b35-579f-810f-71f8091b9927 |  | dropdown | Incoming Earth 1 Cable Size | 95mm, 120mm
checkpoint-status |  |  | checkpoint | Incoming Earth 2 Cable Torqued
select | 04626dff-e9cf-5bd0-ab05-60529f3b7de6 |  | dropdown | Incoming Earth 2 Cable Type | Insulated PVC
select | 668dde0c-c22e-5d83-b3d7-60febb83505a |  | dropdown | Incoming Earth 2 Cable Size | 95mm, 120mm
checkpoint-status |  |  | checkpoint | Correct Incoming Earth Size Per Single Line Diagram
checkpoint-status |  |  | checkpoint | Earth Bar Securely Attached With Insulated Spacers
checkpoint-status |  |  | checkpoint | All Outgoing Earths Have Destination noteled At Earth Bar
checkpoint-status |  |  | checkpoint | All Outgoing Earths Are Torqued
label | f880a248-2382-51aa-8016-e928cf78020b |  | note | Photo Reference
text | 8e27105b-cbc3-593b-9e9c-e7324ea5bc1c |  | textbox | Comment
text | ce6ef6fa-07b1-5ad8-a9eb-0c6dcd03f635 |  | textbox | Date
text | f6585149-676c-5ff6-891e-d128a01451eb |  | textbox | Comment
text | eedef478-c43d-5094-b161-73bb1f615bac |  | textbox | Date
text | cb283e09-0203-5df6-bba8-9f6b34c1bb56 |  | textbox | Tested By
text | cc14ce5e-a62d-55e0-9788-e8b24057f65b |  | textbox | Witnessed By
text | f796b5d3-4ed7-503c-b201-646d450a6191 |  | textbox | Date
checklist-flat |  |  | checklist | Mains/Submain Termination |  |  |  |  | Yes | Mains/Submain Termination | fd6abe5e-dc0a-4875-a49c-6358e0d1c23f
checkpoint-status |  |  | checkpoint | Termination Kit complete
checkpoint-status |  |  | checkpoint | Termination kit issued for Source
checkpoint-status |  |  | checkpoint | Termination Complete Source
checkpoint-status |  |  | checkpoint | Termination kit issued for Destination
checkpoint-status |  |  | checkpoint | Termination Complete Destination
checkpoint-status |  |  | checkpoint | Cable Test Certificate completed
checkpoint-status |  |  | checkpoint | Cable Test uploaded to "Compass"