## PDU Transformer Pre Livening
Data Type | Description | Value
Checklist | PDU Transformer Pre Livening
Checkpoint | Perform Insulation Resistance At 500VDC Winding To Winding And Each Winding To Ground. Confirm All Results Above 100MOhm | Pass, Fail, NA
Text | Before Drying Process Test 1 - Bridge Primary L1, L2, L3, E And N If Any. Bridge Secondary L1, L2, L3 And N If Any. Test Between And Record Result
Text | Before Drying Process Test 2 - Bridge Primary L1, L2, L3 And N If Any. Bridge Secondary L1, L2, L3, E And N If Any. Test Between And Record Result
Text | Before Drying Process Test 3 - Bridge Primary L1, L2, L3 And N If Any. To Secondary L1, L2, L3 And N If Any. And Test This Point To E - Record Result
Note | Test Equipment Used | Megger MIT410/2
Text | Comments
Text | Date
Text | Tested By
Text | Witnessed By
Text | Date