## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | 19b387ea-8eb2-451b-b35d-b11f6c60d095 |  | checklist | Peno - Floor |  |  |  |  | Yes | Peno - Floor | 058a01ad-6082-44f4-807d-8b0b60d393fe
checkpoint-status | 4d0c8267-432d-4474-aea2-bae16e6e3373 |  | checkpoint | Installation complies with current IFC shop drawing
checkpoint-status | 66379da1-1a08-4924-8ef2-5d26cd03149d |  | checkpoint | Floor fire collar types & sizes are correct against IFC shop drawing
checkpoint-status | 20d24361-c228-4bab-9d19-68820f923c43 |  | checkpoint | Top and bottom of peno/collar is capped & sealed
checkpoint-status | 12f51222-bb2e-4581-9ffc-edd11ec281fb |  | checkpoint | Collars are firmly secured into formwork
checkpoint-no-status | d2949e62-3a52-4afe-b3f0-40f2680e150e |  | checkpoint | Concrete pour details
text | 81ab0617-0c00-5a87-8d57-5d18087433ea |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | cd221bc7-63c0-41d9-80e8-c77bb227cb3c |  | checklist | UQ Testing - Tempering Valve |  |  |  |  | Yes | UQ Testing - Tempering Valve | 060ae546-0846-4266-9d37-7daf63a6135e
checkpoint-status | 47e23b55-e5f5-43b5-8492-198bf1a701bd |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 18640628-1a31-5351-814d-efb031e55bbd |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
text | 85ce350c-7735-5e79-9690-0a4487df4321 |  | textbox | Hot water delivery time from cold to stable hot to be logged
text | 4e66f28d-f9f0-5152-8c7a-714a99c92736 |  | textbox | Hot water delivery temperature to be logged |  |  | degrees
checkpoint-status | 1ccad60d-1410-4be0-ad2e-33fae50b0e63 |  | checkpoint | System has been returned to working conditions
text | 8bab4b2b-debf-55c6-ba92-982b1958c5af |  | textbox | Temp and Time reading photos must be taken at start & finish of test
checklist-flat | a3e5bbd7-539d-46bf-83d6-e679281b56c4 |  | checklist | UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks |  |  |  |  | Yes | UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks | 07e4c04a-abe8-4b11-8095-0c46da163773
checkpoint-status | fc84e165-0dd5-411e-91ba-7be58e9e06d8 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 99262a51-f32f-5146-ba9e-9ba119477f92 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 851aa40d-6755-43f6-ad4f-b83a16fb862a |  | checkpoint | Pipe has been checked and is clear of blockage
checkpoint-status | c044d08f-54cd-4cb1-bdae-ad92436ab7be |  | checkpoint | Pipe work is securely clipped and ready for test
checkpoint-status | 7ddc2bc3-0aa5-4f0a-bf68-e0075bb14e60 |  | checkpoint | Open ends have been sealed
checkpoint-status | 5a52f6aa-310a-4b07-a833-414c3cf028fa |  | checkpoint | Temporary valved test point with union fitting was used
checkpoint-status | 96a60e37-bf9e-4a6d-bf48-3aee63f28e05 |  | checkpoint | Pressure testing device connected to temporary valve point
checkpoint-status | 4c4eb338-d8cf-4bd1-80fc-3fe8704dfc94 |  | checkpoint | Test consisted of slowly increasing pressure to 30 kPa
checkpoint-status | d1b76192-2fcf-47c4-a096-2ce597284b00 |  | checkpoint | Pressurization was discontinued to allow system to stabilise over 3 minutes
checkpoint-status | e4c331f9-3268-4ade-84fc-120668660893 |  | checkpoint | Testing was deemed successful if the pressure drop of less than or equal to 5 kPa over at least 30mins
checklist-flat | ebdb54ca-dfc6-429b-b553-1e87d85b3754 |  | checklist | Peno - Syphonic |  |  |  |  | Yes | Peno - Syphonic | 091e48c4-1130-483b-8e26-47e291221f66
checkpoint-status | de2f01b1-5854-4179-88ab-1606312525e6 |  | checkpoint | Installation complies with current IFC shop drawing
checkpoint-status | 8de569b6-3fa2-4b50-a985-2c222ebb16ac |  | checkpoint | Floor fire collar types & sizes are correct against IFC shop drawing
checkpoint-status | a6a79f17-5b07-459e-8e06-7a1254f6730e |  | checkpoint | Top and bottom of peno/collar is capped & sealed
checkpoint-status | 708dae35-0ce4-416f-bb6e-21f2ee872455 |  | checkpoint | Collars are firmly secured into formwork
checkpoint-status | 859f0a35-077a-4046-bd58-80464e49765c |  | checkpoint | Overlflow peno cast in to top of slab (no fall required)
checkpoint-status | ede29024-be62-499e-a420-3f43836132c0 |  | checkpoint | Primary peno outlet is set down 10-15mm
checkpoint-no-status | dc4fe07f-d060-4429-a6ee-9949a128932f |  | checkpoint | Concrete pour details
text | cadc565e-1a40-56ac-9154-36072206b10b |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | cf4a479b-f25f-4394-a7b3-a62a2c03f9cd |  | checklist | UQ Fit Off/ Fixture Install Toilets & Cisterns |  |  |  |  | Yes | UQ Fit Off/ Fixture Install Toilets & Cisterns | 0cb37e31-bb50-479c-a6dc-3af9e288b69d
checkpoint-status | b2a704c0-5afa-47c3-8fd9-e0d816cc9489 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | d74f5a3b-50ee-50bc-bd9e-f7a45e8cb06a |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | bd863804-22e9-416c-ab18-acdf1d33155f |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | ed0c15bd-5013-428c-b1fc-36f5e0a05e75 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 9b9033df-7143-4531-8afa-79cb18106b57 |  | checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint-status | 0293128f-a86e-4972-a5f0-69fbf2d67342 |  | checkpoint | Installation is aligned, level and secure
checkpoint-status | 9aabe28c-9d61-4e0e-9019-2a8520969d3b |  | checkpoint | Flush pipe has been measured to suit the pan prior to being cut to size
checkpoint-status | 2e20782c-cdf3-4725-94aa-573ed69702a5 |  | checkpoint | Button flush plate is in working order and not damaged/scratched
checkpoint-status | 0a926ec9-9f1e-4549-b708-571c410566d8 |  | checkpoint | Seat and accessories are secure and correct
checkpoint-status | 57b0b58d-f42d-46b2-abbf-d94d87b8700b |  | checkpoint | DDA suite back rest installed correctly
checkpoint-status | e062e3ab-6658-485d-8a68-2de60d010476 |  | checkpoint | Full function of installed toilet suite has been checked
checkpoint-status | 4c3ca9f7-7333-4256-a03f-1041083964f1 |  | checkpoint | Pan trap is clear of debris
checkpoint-status | 69bbf6ab-b07d-43f6-aa03-8767c14ac01d |  | checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint-status | 40c274ce-46e9-4208-a268-14dbaa103248 |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | 5342ca79-9d89-4136-aa67-ed384158ce88 |  | checklist | UQ Corridor Rough In (Hot Water) |  |  |  |  | Yes | UQ Corridor Rough In (Hot Water) | 0ebbbaa7-d6f5-4642-a6e8-947f8d382581
checkpoint-status | b9e00fb3-ad26-445e-accf-34e78b7e15ea |  | checkpoint | Existing work by previous plumbing contractor
text | ca0b4441-a2cc-5712-b5d0-632a794bd308 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | f987823b-9445-437b-acba-7d533e2a82c6 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | dd402f29-dd0d-4f17-af4f-e377b60d90d9 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 3ef0ab7f-5b8e-4df0-a6d8-53a2ec9ae59c |  | checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint-status | 7162aa7a-a3b4-4efa-97df-5e5b42554297 |  | checkpoint | Clips, fixings & furrel blocks are correct
checkpoint-status | 76b9340c-81c1-4599-8d18-8af2d81a8b86 |  | checkpoint | Pipe run position & levels are correct
checkpoint-status | 3c10fa16-4f3c-498e-8236-ca1c925c3d84 |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status | 9fc2d11c-5a95-4850-9842-2751f250b5e0 |  | checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint-status | a63fed4a-cf06-471b-8ba2-6a989d9d98a9 |  | checkpoint | Valve flow direction & disconnection unions are correct
checkpoint-status | 9e45a7d5-6bcc-48f4-9a97-138bf0b5ad90 |  | checkpoint | Hot water meter has been installed
checkpoint-status | b0c02ec4-936e-4a5b-847d-c93aa61207d8 |  | checkpoint | Extension points have sacrificial valves
checkpoint-status | 223b916b-28fb-4ba3-986f-618e8f0fc576 |  | checkpoint | Final check for cross connections has been undertaken
checkpoint-status | 23216cdf-6497-4649-8e86-0b992aca7140 |  | checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint-status | 82867e49-0993-469b-abf5-275a15a1dd5a |  | checkpoint | Labels have been applied where required
checkpoint-status | 85131453-6923-4dbc-89e8-0d7c4ec9a9f9 |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | bf18388f-75ad-42cc-ac68-8b575e01a8c0 |  | checklist | UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test) |  |  |  |  | Yes | UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test) | 14a2418e-245b-46f0-90a4-75eb56a89cee
checkpoint-status | 26119d13-2265-41ab-b8df-d6972b738716 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | a55bc236-36e8-5a3c-b2db-cec8595dc3b4 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 68061c8f-4551-444a-83b7-c69f69d6b6a3 |  | checkpoint | Water test is being conducted on material that is rated to withstand only 1000kpa
checkpoint-status | 8ebd51e1-a2b0-47d9-9e32-2a7f1d6eb6c5 |  | checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint-status | 1ab286e0-665f-4d6a-a2e6-d86764113371 |  | checkpoint | Air purging valve point has been nominated
checkpoint-status | a0b33240-add0-47a9-9f1c-5e337f546b39 |  | checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint-status | 0356ee8b-0d19-4144-9d25-100f0c80a4d5 |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | f9802bb1-eaa6-40f2-82f9-bbb3e63393b1 |  | checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status | a9bf2860-0c93-4f26-be76-cd7984739497 |  | checkpoint | All in-wall mixer assemblies & pressure sensitive meters, etc have been isolated/removed from the test zone (these items are only rated to max 500kpa)
checkpoint-status | b9839b81-876d-4be3-bf7d-66f0f680f031 |  | checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint-status | aabd3cd1-09a9-4f2a-9095-885dfc45286a |  | checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint-status | 14aecc17-8f30-4f48-9217-f4729726ea50 |  | checkpoint | Electric pressure testing pump is calibrated
checkpoint-status | afae8570-3c36-4668-ae6e-790506afe4ca |  | checkpoint | Test consisted of slowly increasing the pressure to 900kpa with the water feed shut off and the pressure held for not less than 30mins
checkpoint-status | f59d11db-19d0-443f-9640-2ec6645c375f |  | checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
text | e6c806e0-c0ab-5295-8762-09a466cf929b |  | textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | 8178dac9-9411-47ff-9bca-e6916b58ff0c |  | checklist | UQ Corridor - Meter Manifold Install |  |  |  |  | Yes | UQ Corridor - Meter Manifold Install | 16dbad77-94ac-46ca-a7df-b34eb99f44a5
checkpoint-status | 7197e0d6-3d26-4e7b-90a8-721ed541532b |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | a6feceae-d96f-5e42-971f-2d739603f3fa |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 5cff3691-df5b-48a2-958c-99bf50066fc9 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | ca435714-2072-4e1b-ba94-96bea79af6f6 |  | checkpoint | Installation in accordance with Water Authority requirements
checkpoint-status | 8486a8bb-0a20-4e30-8624-6d91b9b20a83 |  | checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint-status | 26d3cdef-ce1d-4509-b571-c7a214db2032 |  | checkpoint | Clips and fixings are correct
checkpoint-status | 33e7be25-92d6-4eba-b490-2c585f60914b |  | checkpoint | Connected to meter manifold and pipe labelled
checkpoint-status | 086becdb-075b-48f3-b700-87e6a75eae53 |  | checkpoint | All manifold points are capped
checkpoint-status | 1f9eba7c-3c79-476b-929f-3d14c7462db1 |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | 83fbdccf-62a2-4dee-99bd-7a16cd62d711 |  | checklist | UQ Fit Off/ Fixture Install - Bath & Tapware |  |  |  |  | Yes | UQ Fit Off/ Fixture Install - Bath & Tapware | 1fc988a2-ce6b-4a7a-ab50-801b8d9c7e27
checkpoint-status | b638a2d9-139d-41d3-adc4-257953a2a362 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 7b20a46c-bd46-50d6-8f31-332db84eecd6 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 397b8beb-4bf7-4aad-8a01-63434f2efbc7 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 49cda049-3568-426b-bc51-b241d7b0488a |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 5675432c-89f4-44b0-a7f3-e46e3018b4ac |  | checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint-status | dd293af0-74f6-4634-b99d-d520c13e71f2 |  | checkpoint | Bath has been installed aligned, level and secure
checkpoint-status | 78df67d7-b0f6-4f6a-a2d8-35ff753d7373 |  | checkpoint | Bath frame has been adjusted correctly
checkpoint-status | 722b375a-583e-4b8d-8461-4c7cd91a6d8c |  | checkpoint | Wall plate, spout & mixer are aligned, level and secure
checkpoint-status | 13ead681-31d9-4289-8fe8-a07e204c4368 |  | checkpoint | Wall outlet is installed correctly
checkpoint-status | 50cc86a5-1d89-4664-816a-5920551ddb5f |  | checkpoint | Full function of installed mixer and spout has been checked
checkpoint-status | 798ccee4-4b07-4150-82f3-a86994c292b1 |  | checkpoint | Waste and trap connections are tight
checkpoint-status | 6e346091-0860-425e-b362-f158e6af2a6e |  | checkpoint | Trap is clear of debris
checkpoint-status | c6c7e369-ad5d-4ea0-b763-22820b51318c |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | 57661cac-0e32-49bd-8353-934b7be245f2 |  | checklist | UQ Testing - Natural Gas |  |  |  |  | Yes | UQ Testing - Natural Gas | 289c0d2f-2aec-4fc2-94e4-3f4e1f42484a
checkpoint-status | 878e2ead-1d64-4f07-b504-c9d71cda71b4 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 1061778c-47a0-5b4c-ac0d-d5041f953134 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 2e025c7c-884c-4c56-a431-591059b34927 |  | checkpoint | Water test is being conducted on material that is rated to withstand only 1000kpa
checkpoint-status | 13ddee54-c234-4d2b-951b-c61caf3ce318 |  | checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint-status | 148ad86d-3583-4bd0-a79a-92e6716eede0 |  | checkpoint | Air purging valve point has been nominated
checkpoint-status | 01b48fa9-b60c-4aba-b7c6-b5609e08e953 |  | checkpoint | Pressure testing valve point has been nominated
checkpoint-status | 78d247ab-eef7-4bd1-a005-e4f5ca1aff87 |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | e409b186-6233-4b5e-aa4d-53c5009ba42e |  | checkpoint | All terminal open ends are securely capped off
checkpoint-status | befd0303-fb09-4b3c-9861-3d8b97c3b74f |  | checkpoint | Feeder valve was slowly opened & the test zone has filled with air until completely purged
checkpoint-status | 6363c5bb-198d-4c82-9328-150cf0adf5be |  | checkpoint | Pressure testing device was connected to the nominated test point
checkpoint-status | 2f6c8e78-5aff-4248-9cbe-fbab211517d2 |  | checkpoint | Pressure testing device is calibrated
checkpoint-status | dc4557c4-f71c-476b-8269-6a1751242b39 |  | checkpoint | For high pressure test: Test consisted of slowly increasing pressure to 1.5 kPa above working pressure
checkpoint-status | 24698c87-2a94-457b-ae54-7bc013414a71 |  | checkpoint | For low pressure test: Test consisted of slowly increasing pressure no greater than 7 kPa
checkpoint-status | 7ecafabb-a2e7-4e07-aaf6-5ae20ce01db1 |  | checkpoint | Testing was deemed successful if the pressure remains unchanged for 5 mins of every 30 litres volume of pipe
checkpoint-status | 774818f4-fed9-4c2e-b573-1b09f0591b71 |  | checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
text | 91f5aee2-b59e-5aa3-a9da-a037d828c7f7 |  | textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | 69c0ecae-cae5-4853-9fb5-4473c2264094 |  | checklist | UQ Corridor Rough In (Cold Water) |  |  |  |  | Yes | UQ Corridor Rough In (Cold Water) | 2cb7fb4a-a70d-4499-bf8d-7e39006b882d
checkpoint-status | b46d155c-8e4e-4411-91c6-754d9aec2d90 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 2b9c6075-52b6-5afa-b8d1-66306d549877 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | b6b60f13-f853-4962-a736-fb56af4b1f3e |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 1661b286-4453-49f0-841e-02f4dced8489 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 36400a08-8f3e-404c-b70f-ab617408669d |  | checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint-status | 2fe9bd6a-7d06-4b8f-8927-fbf4cd2145dd |  | checkpoint | Clips and fixings are correct
checkpoint-status | 09f1ee00-3f14-4694-a55f-280ff460f952 |  | checkpoint | Pipe run position & levels are correct
checkpoint-status | e1f567c6-bf45-4942-8cb3-cd3753f5886f |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status | fbc41050-532c-4380-8f94-6ae87b197180 |  | checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint-status | 996207ea-3c18-433c-9eb5-ab220b74920d |  | checkpoint | Valve flow direction & disconnection unions are correct
checkpoint-status | ddd7f111-b470-4b18-a8d4-c4a46505f64a |  | checkpoint | Extension points have sacrificial valves
checkpoint-status | bd1e47af-6722-4139-a81d-a89f70f69dea |  | checkpoint | Connected to meter manifold and pipe labelled with destination
checkpoint-status | c2aac82f-0aea-445f-930a-de761b8babe7 |  | checkpoint | Final check for cross connections has been undertaken
checkpoint-status | bea5908e-b488-4415-a302-0645995869f4 |  | checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint-status | 0a4b9a33-6052-43a3-a8a3-2994a63d5c81 |  | checkpoint | Flexible connections are correct
checkpoint-status | f6785be5-4ba7-4c51-bc52-d3abcc77e10f |  | checkpoint | Labels have been applied where required
checkpoint-status | 0a707623-3f41-4a26-862c-1604ccad0b9f |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | bbb5b858-e3d3-469b-b8ea-3a70ec6d3bbb |  | checklist | UQ Risers (CW, HW, Gas, Non Potable) |  |  |  |  | Yes | UQ Risers (CW, HW, Gas, Non Potable) | 47dce010-8efc-431e-a708-21377a195ef1
checkpoint-status | 0977ea2e-c8c8-42a6-a2ef-a7853123039d |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | a10244a2-124f-5111-9be8-292a3625ec1c |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 5e805558-c3b3-4898-a237-596c8039c55b |  | checkpoint | Installation complies with current IFC shop drawings, schematics & AS/NZS 3500 (2021)
checkpoint-status | 82f4a748-7880-497a-98aa-4d6934f00e4c |  | checkpoint | Expansion loop position and length comply with IFC schematics & AS/NZS 3500 (2021)
checkpoint-status | d709858a-2ead-4897-81ef-be70d7bdf672 |  | checkpoint | Clips, fixings & anchor points are correct (etc - fixed anchor, slide guide clamp, spring clip)
checkpoint-status | f22b8db7-b836-41d4-9be4-6d3b9b0dea1f |  | checkpoint | Clips used are not dissimilar metals and will not corrode an element
checkpoint-status | 30ef1ab6-04b6-4ec6-92ad-ba5e0f6fc7da |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status | 46de0285-9c9b-4cf1-aa4c-f7e19c6bc1e9 |  | checkpoint | Torque rates of all roll-groove joints are correct
checkpoint-status | f5dbe0de-ccc2-40db-bcd4-1e89eab381ba |  | checkpoint | Flange connection gasket is fibre and not rubber
checkpoint-status | f397a533-2d41-4299-b982-8968f113348b |  | checkpoint | Flange connection bolts are to the required torque rates
checkpoint-status | 0fe9a3a3-364b-43de-b872-3e2de71921ea |  | checkpoint | Branch junctions & off-set levels are correct
checkpoint-status | eca6017a-d21a-4f5f-af2d-b1d97640766b |  | checkpoint | Pipe joints & witness marks are correct
checkpoint-status | 692d9b6c-d88f-4abf-908e-43e9cc8f343d |  | checkpoint | Check for damage or leaks
checkpoint-status | cc019a5f-7b06-4487-88ad-8879f4613fea |  | checkpoint | Valve flow direction & disconnection unions are correct
checkpoint-status | 6e03504e-905c-465a-8323-6823b519a170 |  | checkpoint | Extension points have sacrificial valves
checkpoint-status | 90e7aa4a-1200-41cc-b68e-38ac3cd8a069 |  | checkpoint | Labels have been applied
checkpoint-status | a2eca1ca-37a0-40ad-a992-3eff7aebd8db |  | checkpoint | Pipes requiring lagging have been temporarily labelled
checkpoint-status | 2474d3fb-de5e-45b8-a14b-e6fbb63b0b46 |  | checkpoint | Penos have been caulked and meet fire rating requirements (top and underside of slab)
checkpoint-status | 94bb619c-902b-41fc-bc8d-647527a344cb |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | 7cf17544-a2ea-4aba-adf9-9a787ac4b9dc |  | checklist | UQ Fit Off/ Fixture Install - Dishwasher |  |  |  |  | Yes | UQ Fit Off/ Fixture Install - Dishwasher | 5f354753-0f76-4794-b689-f24e34aba720
checkpoint-status | f778e514-794f-4e25-851d-b16e992d0ffa |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 621e5357-0287-541f-987e-3ee0fc5c081d |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 622418b4-aa15-4484-b57a-de14aa36d36e |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 48ed4d08-4f79-4666-8869-830445cd2743 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 53e5f4c6-9152-4763-a187-f71beb6fba02 |  | checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint-status | 30f615d2-d957-452f-a497-69e48a061e4b |  | checkpoint | Dishwasher has been installed aligned, level and secure
checkpoint-status | 963d6703-f210-442e-9a0d-da37e2481828 |  | checkpoint | Full function of dishwasher has been checked
checkpoint-status | 5e84ee4e-4ad3-444b-b7c3-7776b51f4b91 |  | checkpoint | Trap is clear of debris
checkpoint-status | 32ddbba6-b8f0-4b84-9633-312d8a9d6ebc |  | checkpoint | Trap nuts are tight
checkpoint-status | d2457262-629f-41d6-81f0-f8418a343a7b |  | checkpoint | Mini stop is installed
checkpoint-status | 2b27a48d-b09a-4903-83c7-c22881e26b9a |  | checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint-status | 5843adaa-c886-40b9-9816-35b8f4e347f0 |  | checkpoint | Pressure reducing valve have been installed
checkpoint-status | b073c13f-5190-4524-943e-d5b3d1767532 |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | 37a1b038-c360-4270-b60d-8155a9185cc8 |  | checklist | UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks |  |  |  |  | Yes | UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks | 657bfe80-6d0c-47fa-b333-2fba773b5da0
checkpoint-status | 44ef6b08-22dd-46ee-8c67-26ae27e1a683 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 47b2362f-8b49-5065-adb6-2323a248a6cd |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 6f24a1a0-04f1-44c0-bbe2-27fdc0af6827 |  | checkpoint | Pipe has been checked and is clear of blockage
checkpoint-status | 22717841-b497-4fd7-b58f-aa5e8ba95b24 |  | checkpoint | Pipe work is securely clipped and ready to hold water
checkpoint-status | 603616a1-1e1b-452f-b569-70b824155a74 |  | checkpoint | Open ends have been sealed
checkpoint-status | 86a33272-70dc-4aef-91b2-b7d9f4a5c5d7 |  | checkpoint | Test was conducted from stack riser 1m above the highest overflow point
checkpoint-status | ac9265c9-413c-4b71-867d-f421af7a82d4 |  | checkpoint | Test was successful as it held water at an unchanged level for at least 30mins
checkpoint-status | 3137f0ad-542a-49b5-86ba-9f5f64e165ed |  | checkpoint | Water was drained from the pipe at the end of the test
text | 049b3e26-a0dc-573e-be18-fe840f276fdf |  | textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | c6a6bab1-2780-426d-bb7f-5398a84efc5a |  | checklist | UQ Fit Off/ Fixture Install - Showers & Tapware |  |  |  |  | Yes | UQ Fit Off/ Fixture Install - Showers & Tapware | 6ee7c343-70db-4962-b213-6774be76206c
checkpoint-status | 078d2141-23de-4197-a294-3350c993e17f |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 564c88ec-4fc7-5894-882d-9c9943442564 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 589f0b73-633b-485d-b626-15d2950fc0d9 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 5efce834-9c0d-48e2-964a-90a22f5090d6 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 781f8b8e-7e44-4b22-9df6-1a6c3c35443b |  | checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint-status | dcf91391-c1f2-468b-8b28-ee6824979b0c |  | checkpoint | Wall plates & mixer are aligned, level and secure
checkpoint-status | 073b2e61-b4c1-43b9-b344-ea25c801b631 |  | checkpoint | Wall outlet is installed correctly
checkpoint-status | 8404ef1f-de69-4216-845c-f46c1265a80f |  | checkpoint | Full function of installed mixer and shower head/s has been checked
checkpoint-status | 0e313ce0-9a6d-405e-9cd2-311b0ca2b1e3 |  | checkpoint | Floor grate is correctly fitted & aligned
checkpoint-status | 69c5eb77-5ffb-4923-9804-b40dd62b3b87 |  | checkpoint | Floor waste trap is clear of debris
checkpoint-status | 5377f5f1-2f52-4302-b1fa-faa984c9e483 |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | 76af306d-f27d-421a-ac09-6ffb8df763c0 |  | checklist | UQ Fit Off/ Fixture Install - Vanity Basin/s & Tapware |  |  |  |  | Yes | UQ Fit Off/ Fixture Install - Vanity Basin/s & Tapware | 7160fe3a-ef92-4081-ae8c-f621d83d8c46
checkpoint-status | d727d2ec-274e-4376-8078-33480be6b66f |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 1aea9483-e6b4-59db-a44e-3c3051fa43e8 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 711542b7-48a7-4225-ab95-7e006078eaad |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | ea50b26e-dabc-4b94-9644-428c5bf20dd7 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 557807d8-d9e0-46cd-83e5-cfc8f486c17c |  | checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint-status | f89cf862-39fe-4ef5-bb8c-234de3af21d7 |  | checkpoint | Installation is aligned, level and secure
checkpoint-status | 30170335-54f2-4377-9cdb-2f7c9ad6de06 |  | checkpoint | Plug & washers are correct for the fixtures being installed
checkpoint-status | 1d2e3210-da89-42e7-b41c-ed57b343c0cf |  | checkpoint | Waste and trap connections are tight
checkpoint-status | 7a133dc7-9be1-4429-af3b-bb06699989f8 |  | checkpoint | Trap is clear of debris
checkpoint-status | 2d9cdd2f-9f43-4d73-a7fd-fac22c302474 |  | checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint-status | fcd1a441-c0b2-4764-82e9-31c1660de822 |  | checkpoint | Any stop valves have been capped for future use
checkpoint-status | 91b6ccf2-8704-4b0e-affe-40b2e99edb5f |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | eb3a769d-fa0c-4db1-8794-e01097b273bc |  | checklist | UQ Fit Off/ Fixture Install - TMV |  |  |  |  | Yes | UQ Fit Off/ Fixture Install - TMV | 7574816b-1694-45a3-8e93-73cc682547d0
checkpoint-status | e537021f-9705-4bee-96c0-319ec135d46a |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | d205ade2-06cd-59b0-b5d6-a321b038c221 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 916092b6-d36f-461b-843e-32f7b9606def |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 01367691-7653-4c3c-8ec9-a1f2aa564865 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 27daf141-7682-4c34-943d-4534bd909cb4 |  | checkpoint | Fixture has been checked for damage and leaks. Damaged fixtures do not get installed
checkpoint-status | 7cd4f0e0-9362-40db-b256-46e393a23ae8 |  | checkpoint | Wall box has been installed correctly
checkpoint-status | a9462c18-2918-4747-82bf-fd89cd717c7f |  | checkpoint | Function and controls have been checked
checklist-flat | 3188b7d8-e709-4086-9ed6-f7164ccbea3c |  | checklist | UQ Testing - Potable Water - 1500kpa water test (not an air test) |  |  |  |  | Yes | UQ Testing - Potable Water - 1500kpa water test (not an air test) | 7797ac46-ae63-478f-8cd1-64a93718037b
checkpoint-status | cfaf61c5-8123-4b08-8077-75b14472d429 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 715ad605-1d43-5b60-812d-df32d0744afe |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 68a02855-1171-4a7f-b08f-b55350915faa |  | checkpoint | Water test is being conducted on material that is rated to withstand 1500kpa
checkpoint-status | 55a6d0de-793b-479a-8fed-8b5a45bdd0c8 |  | checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint-status | cbd7a779-bcab-4b05-a651-a2b7baf50ccc |  | checkpoint | Air purging valve point has been nominated
checkpoint-status | 671ccf33-d48a-4ebd-b7c6-af32f4a25a5d |  | checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint-status | b8e41103-c5ed-42f6-89d1-afd38c1ddb16 |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | 502076f8-b05d-4851-9a28-1f17b7d18082 |  | checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status | 53dd4ffe-9aec-486e-bfed-baedbd144a72 |  | checkpoint | All in-wall mixer assemblies & pressure sensitive meters, etc have been isolated/removed from the test zone (these items are only rated to max 500kpa)
checkpoint-status | 8f10fba0-ed8d-46c0-926c-4c6531de3ba6 |  | checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint-status | 137952b3-093b-4b8e-b57e-f9ef056884e5 |  | checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint-status | 5163d303-5a91-414c-8f43-d5b10668c731 |  | checkpoint | Electric pressure testing pump is calibrated
checkpoint-status | 13efc2cb-875e-47e2-8049-ab3a90375cf8 |  | checkpoint | Test consisted of slowly increasing the pressure to 1500kpa with the water feed shut off and the pressure held for not less than 30mins
checkpoint-status | c67e5b60-61cb-4e35-86b8-7ee15ef546ca |  | checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
text | 2b69356f-91e1-565c-b2a2-7c2e65a58cd8 |  | textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | 4c9c3ca3-0f75-47e2-b0b2-b7d1e57ce1c3 |  | checklist | UQ Fit Off/ Fixture Install - Tempering Valve |  |  |  |  | Yes | UQ Fit Off/ Fixture Install - Tempering Valve | 7875a868-578b-4c41-9222-c6cffc57b37b
checkpoint-status | 6f9dba2b-c613-4611-b91b-4b1be2fc565c |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | ab181f67-a42a-5d8a-b2a1-a853caa1c83e |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 71e877d0-0e50-4159-be07-fddbdcffe9bc |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 81560a2a-5bef-4757-878d-f9f331f5fe0f |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 69d7315e-ccc5-429e-b889-5eb90e3a5575 |  | checkpoint | Fixture has been checked for damage and leaks. Damaged fixtures do not get installed
checkpoint-status | 49c0dd45-16b0-4835-82c6-cbddb947e766 |  | checkpoint | Valve been installed correctly and in the correct location
checkpoint-status | 986ceeea-f78e-4664-ad4c-98f62698f08b |  | checkpoint | Function and controls have been checked
checklist-flat | 2bf17bcd-fb3d-44c4-b072-e402da6c8bd4 |  | checklist | Drain Inspection with camera |  |  |  |  | Yes | Drain Inspection with camera | 8b32d3f8-39ef-49f1-9f72-586f3e246808
checkpoint-status | ab800160-ef04-4954-8db8-67b1381f6781 |  | checkpoint | Extent of drain is clear of obstruction
checkpoint-status | b2ac965d-b291-4302-a157-b6d611742d92 |  | checkpoint | Extent of drain is free of damage
text | 4376f246-025a-57c2-976d-9cd2401b0ae4 |  | textbox | Any notes to be added here
checklist-flat | bead77aa-639c-4b50-8dd1-3d6c7abc90f7 |  | checklist | UQ Fit Off/ Fixture Install - Laundry trough & Tapware |  |  |  |  | Yes | UQ Fit Off/ Fixture Install - Laundry trough & Tapware | 93190776-db82-44e7-be2d-131749bffc9d
checkpoint-status | 741a314e-6b7f-483f-b6e4-74c2209147bf |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 5a87377e-d4f7-57d7-bb84-8a1d69e45394 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 1b084602-0a1a-42dc-8d9d-3153936f66cb |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 5bb676f1-ac30-41d0-9b20-c6a3775e8af0 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 4965ca32-c6b4-4c81-b961-803816a3e2d7 |  | checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint-status | 7ecfb414-7423-4e16-8cef-5440c78de12e |  | checkpoint | Installation is aligned, level and secure
checkpoint-status | c21d4761-a34c-4b4e-87d9-451636f929d4 |  | checkpoint | Plug & washers are correct for the fixtures being installed
checkpoint-status | 504a13e1-c992-4b22-802d-2d044d888304 |  | checkpoint | Waste and trap connections are tight
checkpoint-status | c486534d-3f8d-4611-9283-81f3d1b7c7c2 |  | checkpoint | Trap is clear of debris
checkpoint-status | c58e73dc-14ed-45bb-bb96-9a292e1e3d24 |  | checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint-status | 9b20cce2-cfdb-40c7-adaa-5cf56b01e8f4 |  | checkpoint | Any stop valves have been capped for future use
checkpoint-status | b27540dd-036c-40b3-b783-bd2ef2b80641 |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | e2220b8d-0595-4ce2-8701-e12224cca292 |  | checklist | UQ Corridor Rough In (Gas) |  |  |  |  | Yes | UQ Corridor Rough In (Gas) | 9ea659d7-5ac3-4722-878f-d8e5e2ca0b87
checkpoint-status | 31ad4a2c-eadf-4f74-90b6-141da4c52139 |  | checkpoint | Existing work by previous plumbing contractor
text | 75119293-0032-54e1-a774-3e1f6e1b9e35 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | b57f1711-5b50-4d6b-9572-f0939b7d481b |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 142279af-7d30-41e4-8c95-b87e2076668c |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 47bfa3be-a97c-420a-a330-74938efe89bd |  | checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint-status | 67229814-aaae-42d2-b6bd-f7efc5ddcdda |  | checkpoint | Clips and fixings are correct
checkpoint-status | b6c49da0-a333-46bb-9799-ccb3d385a38a |  | checkpoint | Pipe run position & levels are correct
checkpoint-status | b3b5ed26-b68e-4663-8bdb-ddca092bab32 |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status | 22f7c926-7959-494c-8281-4bd985352714 |  | checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint-status | 76c9ae32-0eee-444b-9c91-823e9e362c71 |  | checkpoint | Valve flow direction & disconnection unions are correct
checkpoint-status | 867d290c-9c5a-4bc7-b534-062dd04efd17 |  | checkpoint | Extension points have sacrificial valves
checkpoint-status | 57e40b33-7520-4e41-95ad-4a05fb1c3dd7 |  | checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint-status | e4d01d55-40a6-454c-83fb-2837c776c362 |  | checkpoint | Labels have been applied where required
checkpoint-status | eb091b09-b70b-47ca-8df7-f0bf1a2ff2b4 |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | 7fdff7f7-095e-43b6-aba6-7d938351d2c5 |  | checklist | UQ Testing - TMV |  |  |  |  | Yes | UQ Testing - TMV | 9fd8f91f-be37-4850-9915-21984de87165
checkpoint-status | a483d444-d3b5-491b-a269-3cc79f10b1f5 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 4f041658-c0aa-5731-a27b-4546cc9ba274 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
text | ce488675-d5d0-58db-986a-d932a8fdc54e |  | textbox | Hot water delivery time from cold to stable hot to be logged
text | 601deec6-8650-5932-8461-61fb8de0ca28 |  | textbox | Hot water delivery temperature to be logged |  |  | degrees
checkpoint-status | 3e45b140-cc83-4731-ae1e-be32e720bc53 |  | checkpoint | System has been returned to working conditions
text | 2fdd3bce-ad3c-5242-b460-c57566195548 |  | textbox | Temp and Time reading photos must be taken at start & finish of test
checklist-flat | b6d470af-bcdc-4696-8c11-95009abc450c |  | checklist | UQ Fit Off/ Fixture Install - Hose Taps |  |  |  |  | Yes | UQ Fit Off/ Fixture Install - Hose Taps | a290b84a-40e0-4f1a-aad5-b315afe16285
checkpoint-status | 38d345a4-d978-47b4-b1f8-725520581e39 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 5b982785-98b5-5447-b5cf-c777751e5213 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 1163d401-52fe-48aa-964c-579ca4129d81 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | b9a0b9ba-c3bd-49ac-8463-128739b806ad |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | c4354c07-92ed-4638-85a4-4ecaf8b53368 |  | checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint-status | 0c143f41-1982-438a-b97b-344550e325d2 |  | checkpoint | Hose Taps have been installed aligned, level and secure
checkpoint-status | a855d00b-ccb8-4993-8470-4f1d2f27d169 |  | checkpoint | Backflow prevention device has been installed
checkpoint-status | 3c0fc8aa-148a-45a1-bce4-2518d1689073 |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | 91fe7701-407e-4bc9-94cd-24883617ec56 |  | checklist | UQ Low Level Rough In |  |  |  |  | Yes | UQ Low Level Rough In | a791e111-8424-42b6-a150-04d6046bc9af
checkpoint-status | bcfa07f4-77ac-4427-b08c-3137dbd571ef |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 41bf94c5-c901-5268-880b-92cb12eb861f |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 3a34c4d5-2146-44dc-97a4-b61de294a495 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 84d6a5a8-1a72-40c5-9741-dee71f7c8a47 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 7ed9a6f4-0271-4f45-8730-a107e3cfe715 |  | checkpoint | Pipe joints & witness marks are correct
checkpoint-status | b2cc8931-b991-4367-9dd7-a1605644487f |  | checkpoint | Clips and fixings are correct
checkpoint-status | 36b821df-09ef-47ca-a298-b08b82320778 |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status | 8591ec5b-d8c2-4e0b-b5be-2fd59ddde81d |  | checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint-status | a462f8a1-f22e-4590-9b7d-156ce7f9f0c4 |  | checkpoint | Valve flow direction & disconnection unions are correct
checkpoint-status | 29488016-4609-4d9d-8710-59bc12153817 |  | checkpoint | TMV/TV have been installed correctly and in the location for future access
checkpoint-status | 1adb5559-8497-43aa-b5ee-3292f5a9af4d |  | checkpoint | Mixer bodies & lugged are installed at the correct height and on a nog
checkpoint-status | 6ba99a17-7e16-4bfd-ba23-cca2e00755d3 |  | checkpoint | In-wall pan & cistern brackets are correct and there is reinforcement behind flush pipe
checkpoint-status | 0815118e-779d-4700-a139-38db6c3b1df5 |  | checkpoint | Sharp edge pipe protection is secure and will not lead to pipe abrasion in future
checkpoint-status | f90f13ad-e62a-4c4e-924d-7640b1ca46c6 |  | checkpoint | Couta fittings have been visually inspected to ensure pex is in correct location and crimped correctly
checkpoint-status | b70f04d5-f5d5-4e8d-8ce9-ba07426c4adc |  | checkpoint | Final check for cross connections has been undertaken
checkpoint-status | e7900e4b-3a49-4d23-9fe9-b6b29461217e |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | add4559d-6090-4f03-9b70-1b6fd421fa4f |  | checklist | UQ Drains: Trade Waste - Underslung |  |  |  |  | Yes | UQ Drains: Trade Waste - Underslung | beedd7f1-f6fa-4b43-9fc9-405496eaf654
checkpoint-status | baaadb10-92bf-41bd-b905-1a2b1b1392d3 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 7bd38ddf-7be4-5774-8619-3636439757b5 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | d32ecb6e-7575-4255-9e64-dfdd4229d1f0 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 4f8414c0-a1e4-4881-b54c-b1aa8a1dc1a7 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | e779b040-e2a2-428f-b093-a95ef1713b26 |  | checkpoint | Penos above have been checked, opened and debris cleared
checkpoint-status | f0cfded7-be12-4897-91b8-9943294da005 |  | checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint-status | a440e9b6-76c3-4556-b58f-0465880d910a |  | checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint-status | 66fa0dd5-3de7-419e-84b1-16fe16f28427 |  | checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint-status | 6b51fa4c-91cc-4b0e-af48-a9df7d01795f |  | checkpoint | Pipes & traps are clear of debris
checkpoint-status | 30d114e0-c50d-4e80-9103-602263999b7f |  | checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint-status | 3507c0b1-81ed-4eb0-a467-629988e6aa87 |  | checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint-status | aedc65fa-be63-4d34-aa07-03d2e1aecb25 |  | checkpoint | Labels have been applied where required
checkpoint-status | c9266088-c263-4264-a46b-1d2e1a59cdb7 |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | ad265423-0984-4c2a-9296-31e2b240a96b |  | checklist | UQ Testing - Air Test - Sewer & Stormwater Underslung |  |  |  |  | Yes | UQ Testing - Air Test - Sewer & Stormwater Underslung | bf9c9279-826e-41ba-bf48-ea6885251bdb
checkpoint-status | c0c1924f-906a-4afb-970e-3f064fc4de5e |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 6040acfd-5287-5c81-85f5-627cae945970 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 963bd7cb-157f-407d-afe2-ece925364eb0 |  | checkpoint | Pipe has been checked and is clear of blockage
checkpoint-status | 185b352c-f414-418b-99df-0d58057df472 |  | checkpoint | Pipe work is securely clipped and ready for test
checkpoint-status | d246b615-1e8c-4ec2-83be-1d3766374f5d |  | checkpoint | Open ends have been sealed
checkpoint-status | 6a1f057f-093d-410b-815a-0c152b7f4f61 |  | checkpoint | Temporary valved test point with union fitting was used
checkpoint-status | f0c2b853-d054-49f5-b938-9dd4dffa3472 |  | checkpoint | Pressure testing device connected to temporary valve point
checkpoint-status | 8f98deb0-d5e2-4bd5-a561-2d725222fb1c |  | checkpoint | Test consisted of slowly increasing pressure to 30 kPa
checkpoint-status | d0ece201-9376-41ec-b6a0-3861ed2968b8 |  | checkpoint | Pressurization was discontinued to allow system to stabilise over 3 minutes
checkpoint-status | fba3b505-894d-4c6c-8acf-3ce48eb946ae |  | checkpoint | Testing was deemed successful if the pressure drop of less than or equal to 5 kPa over at least 30mins
checklist-flat | cefb6dc0-0e21-4b15-a294-43195a66a0ae |  | checklist | UQ Fit Off/ Fixture Install - RPZD |  |  |  |  | Yes | UQ Fit Off/ Fixture Install - RPZD | c1d209b6-6888-4db6-99fd-5883df50da69
checkpoint-status | 3c441c40-f0da-4a41-a183-661eb0618529 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 7e8ce852-2201-5656-83d7-6377cf249b20 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 03480335-80f9-4f7d-b990-4d28ac5013b7 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 3ce15b35-2e71-4bf4-8531-659cfc75e902 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 193ee9f9-7aa4-4af5-a348-ce922a000c16 |  | checkpoint | Fixture has been checked for damage and leaks. Damaged fixtures do not get installed
checkpoint-status | 85f9aca3-be58-4082-8242-0d1b4baded38 |  | checkpoint | Valve has been installed correctly and securely
checkpoint-status | 961c9383-d0a8-494d-9348-e310604c1055 |  | checkpoint | Valve is functioning correctly
checkpoint-status | 38a45d5e-5712-4c40-b490-156af07635f1 |  | checkpoint | Valve discharges to tundish
checkpoint-status | e33ec58a-6739-4543-a64c-988eb477968c |  | checkpoint | Water connections installed correctly
checklist-flat | c6f722c1-655f-4c58-9e23-b0292ee08c09 |  | checklist | UQ Drains: Sewer, Stormwater & Vent - Underslung |  |  |  |  | Yes | UQ Drains: Sewer, Stormwater & Vent - Underslung | c64a595b-69ea-4cd5-9b1b-e97aeeb53610
checkpoint-status | 3061505c-7576-4079-80a1-b55d04aa00a5 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 6e297e80-bdd6-515e-ae9a-e9bac2e163c7 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | b3df56ce-65e8-4f16-a79c-48fd093e493c |  | checkpoint | Installation complies with current IFC shop drawings
checkpoint-status | b34565a8-2e78-41ae-816c-150c39cd3709 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 606c1441-0c70-4b73-98f7-5d3a9b57a21e |  | checkpoint | Penos above have been checked, opened and debris cleared
checkpoint-status | d3f558b0-143d-40dc-9399-7bdb501b22db |  | checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint-status | 077f7b3a-206e-4e72-8b95-e241c8f7796b |  | checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint-status | d2737131-d0b5-41c6-ab70-238b3dbfb29e |  | checkpoint | Pipes & traps are clear of debris
checkpoint-status | 499b67b4-5f8b-4912-ad63-cbc217b8ae96 |  | checkpoint | Required fall/grade meets AS/NZS 3500 (2021)
checkpoint-status | c1b2302c-862d-4c49-9207-6d33a3e4e62f |  | checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint-status | 52115547-325c-4c34-b030-c2f83c4d18a7 |  | checkpoint | Labels have been applied where required
checkpoint-status | 2d7d622b-7c11-4b91-b063-01a49942d9bb |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | ea9ffa28-7759-43fd-afe1-5a9a2c63126b |  | checklist | UQ Fit Off/ Fixture Install - Kitchen sink & Tapware |  |  |  |  | Yes | UQ Fit Off/ Fixture Install - Kitchen sink & Tapware | cfb7dd6b-daf2-4695-8f99-a360ecef6bab
checkpoint-status | f6aff00d-4f7e-4772-baa0-b9157a036920 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 8d78bc8a-b209-51de-a90b-fd716bc4b266 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | c98faacf-70c1-4995-9ecf-d799ea84cd4b |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 738c9c55-a545-4945-9f22-0ed90869688b |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | eb6f23b1-afac-4ac6-8c83-0778ff504ef3 |  | checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint-status | 8cf80985-8d5e-4b6c-bf63-d7e7c03c001b |  | checkpoint | Installation is aligned, level and secure
checkpoint-status | 8c07c12c-3787-4eed-bdaf-a81f5090dc59 |  | checkpoint | Plug & washers are correct for the fixtures being installed
checkpoint-status | 7576931c-f36a-4198-95f6-b7d53183ccbf |  | checkpoint | Waste and trap connections are tight
checkpoint-status | 61e016e9-a830-422c-99fe-dad528c692b6 |  | checkpoint | Trap is clear of debris
checkpoint-status | 080e697b-7c1d-4342-99f2-bf6ccc6441fc |  | checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint-status | f57c8e8c-c637-42a8-8aff-7787cc21a49e |  | checkpoint | Any stop valves have been capped for future use
checkpoint-status | 1228fbd7-8e38-491a-988a-b6fc84190b23 |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | 7fef7995-443f-45cd-8c7e-c15baca764cf |  | checklist | UQ Stack Riser: Syphonic |  |  |  |  | Yes | UQ Stack Riser: Syphonic | d7ae4b17-4aaa-41f2-89d6-65c28043e260
checkpoint-status | f84e167d-1c67-42a5-af1c-7e24ca7fc36f |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | bebda911-3875-5aca-8e6b-5384e399d1c4 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 7e4031bd-bf12-4b17-a495-5b7f75232ba8 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | bea94fad-c37e-4841-a347-840e042aca7d |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | ed04c817-4f6f-4568-b031-e71af30aeacc |  | checkpoint | Specific clipping method & anchor points are correct
checkpoint-status | 3bc1d40c-18f8-4371-81d1-442ee30aa266 |  | checkpoint | HDPE fusion welds are witness marked
checkpoint-status | a90eeb0c-24ca-4b8c-a47c-8428632e8156 |  | checkpoint | Pipes & junctions are clear of debris
checkpoint-status | 49140756-7350-4962-a6ad-14b72e196d98 |  | checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint-status | 395d2e62-6614-41d6-a3bb-6c020386cf36 |  | checkpoint | Peno has been caulked (top and underside of slab)
checkpoint-status | 0847f867-54cf-4a87-9ddb-a80bad3d3819 |  | checkpoint | Labels have been applied where required
checkpoint-status | 65c15bd9-f68e-470e-8837-7b00880e747d |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | 67d74d8f-2088-46f7-9055-28d46ce310cb |  | checklist | UQ High Level Rough In |  |  |  |  | Yes | UQ High Level Rough In | d7f47d03-c4f5-40f4-b828-e5f1e1705052
checkpoint-status | 3d343231-8d0d-4f45-85ec-b30dfc92ab12 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | a335ad79-07fe-51d6-a035-82dfb0697444 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 3354e254-e7ab-4851-97c3-49088d133d23 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 6c61ece5-d728-4917-b2cc-f64f8473c38e |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | ebdf0fbc-de06-413a-a270-024015547c35 |  | checkpoint | Pipe joints & witness marks are correct
checkpoint-status | cea6a09c-83c5-4d23-afa1-b8b2df7131c7 |  | checkpoint | Clips and fixings are correct
checkpoint-status | a4503698-51b2-4b66-9c9b-7c53b298af1a |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status | d2b2f502-4847-4491-94de-7cf72aace618 |  | checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint-status | dc96a91a-6549-4694-b057-2949b880d54b |  | checkpoint | Valve flow direction & disconnection unions are correct
checkpoint-status | c3c64cf7-1965-4705-b644-797c56773c13 |  | checkpoint | TMV/TV have been installed correctly and in the location for future access
checkpoint-status | 9e30e2a6-1a80-4bec-9883-c1c52c36fef3 |  | checkpoint | Sharp edge pipe protection is secure and will not lead to pipe abrasion in future
checkpoint-status | 807a8e38-294d-4ddd-99cf-4dcb6b03251c |  | checkpoint | Couta fittings have been visually inspected to ensure pex is in correct location and crimped correctly
checkpoint-status | 9fac5247-9ea8-4c01-ba11-abe1f7ca4937 |  | checkpoint | Final check for cross connections has been undertaken
checkpoint-status | 704430c3-8fa2-4b42-91f1-a3c8dd791ace |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | 87646fa8-951e-46a5-8341-0aac12d33936 |  | checklist | UQ Drains: Syphonic - Underslung |  |  |  |  | Yes | UQ Drains: Syphonic - Underslung | e1b57c2f-c974-4ad0-a7f3-da2a9f73825e
checkpoint-status | 26f5f56c-c54b-4bb3-8d32-76070d903c17 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 31aa04c1-2b6d-5a3b-a8de-beec94f7bd07 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | b1b98ca7-2a89-4558-9b7e-212dc8d927d3 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 70047a6b-701c-4452-8954-6172502d8f6b |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 9b841bdd-5001-4b0c-9ffa-7031279c96f9 |  | checkpoint | Penos above have been checked, opened and debris cleared
checkpoint-status | 5596bdc6-394f-466c-bcc1-815a77da40ab |  | checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint-status | c7967e29-b423-4b64-9c59-98cc19d2bc5f |  | checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint-status | d51e6525-9250-494a-a941-5a44f0dd02dc |  | checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint-status | 121b3e0f-763a-4dbc-9812-b08714b1ec82 |  | checkpoint | Pipes & traps are clear of debris
checkpoint-status | d87e1256-30b2-49b7-a074-5ae02cfb8167 |  | checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint-status | f4dd4c4a-4b60-4bc8-8584-0f4065f733e4 |  | checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint-status | c2972009-aa16-4e12-9468-e8ca597dd3cd |  | checkpoint | Labels have been applied where required
checkpoint-status | b81659c5-81ad-4f24-b459-dbdaa74c8fb8 |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | f3f4b17b-e49a-490b-a959-8dc85e1a64cb |  | checklist | Peno - Cast In |  |  |  |  | Yes | Peno - Cast In | e2c902db-c242-4ac4-8005-1fc18cd87ca7
checkpoint-status | 1c1e768a-c3c6-4d06-bb56-a0fe478c0e71 |  | checkpoint | Installation complies with current IFC shop drawings
checkpoint-status | 78d58304-bd84-45f3-86c6-403a94bc5196 |  | checkpoint | Collar & pre-fab elements free of damage prior to install
checkpoint-status | b9342b06-3350-4949-8f51-c496daf3e2dc |  | checkpoint | Where practical, pipes water tested prior to the pour
checkpoint-status | 3cca1f14-8c62-43d0-82b9-22eaa4a731d5 |  | checkpoint | Pipe grades and size have been checked
checkpoint-status | 0fb51a67-bd21-4e54-afec-aa5c1955dd4d |  | checkpoint | Invert levels and finished levels have been checked
checkpoint-status | 7875a762-d9c1-4fa1-a9d2-56a86bcd1277 |  | checkpoint | PVC has been lagged (add photos)
checkpoint-status | 58003e0d-c326-4c93-bf03-56f207e4730b |  | checkpoint | HDPE fusion welds are witness marked
checkpoint-status | 196844ff-3858-4238-8170-b0395a15db95 |  | checkpoint | RWO body installed level
checkpoint-status | c47e9638-f0d0-456f-9f18-124cc53835f6 |  | checkpoint | Clips, fixings & anchor points are correct and secure
checkpoint-status | 1eb9a338-fd97-41f6-8e9e-c020661f8005 |  | checkpoint | All cast in elements are clear of debris, securely capped & sealed prior to pour
checkpoint-status | e365584e-ce3e-468a-8b4c-9c5ae0f4a011 |  | checkpoint | Water has been poured into PVC for deep beam/thick slab pour
checkpoint-status | 2be7395d-353d-4b86-a70c-a894a6c4e632 |  | checkpoint | Unfixed pipes are tied to reo (where necessary)
checkpoint-no-status | fd7a7c7b-a3ad-4c97-a55d-bebfc68e7fc5 |  | checkpoint | Concrete pour details
text | 99efa2b8-6b81-5d80-8d94-527bc1d423b5 |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | 7acbd625-0817-4eaf-a2ce-8492603ddb24 |  | checklist | Peno - Wall |  |  |  |  | Yes | Peno - Wall | e304523d-ddb3-4ec8-abf4-5f27594e7935
checkpoint-status | 69ea2306-f5d8-4c00-875c-8f97cea2f298 |  | checkpoint | Installation complies with current IFC shop drawings
text | 87e6249b-66a3-51fa-8d9b-4c587015df19 |  | textbox | Document invert level wall peno has been installed at |  |  | mm
checkpoint-status | fed1f220-e232-4ba0-90c0-ae3e1acae055 |  | checkpoint | Collars and sleeves are capped & sealed
checkpoint-no-status | 31798881-7997-44d2-99bb-6975e3cdf359 |  | checkpoint | Concrete pour details
text | 32a49a1e-372a-5ab4-b748-3370b3b81381 |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | fac6bf37-2eae-475b-a957-a0f7d3e81221 |  | checklist | UQ Fit Off/ Fixture Install - Gas Cooktop |  |  |  |  | Yes | UQ Fit Off/ Fixture Install - Gas Cooktop | eaf7f440-42a8-4682-9bf3-6dc41bc1a21c
checkpoint-status | 01df276f-a4dd-4fa4-8b66-a5e3ca249f77 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 0184142c-bb8a-52e9-bec0-60f3874c50a8 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 4c31fdaf-20e2-4e9f-9616-0a171ee9651d |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 73bdc4a4-44a4-4028-b895-ee5c0bd504f0 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 15e52049-4026-47bb-b041-7e24e11da684 |  | checkpoint | Fixture has been checked for damage and leaks. Damaged fixtures do not get installed
checkpoint-status | 106028eb-bdd5-46bb-b423-f39c3639b786 |  | checkpoint | Cooktop has been installed aligned, level and secure
checkpoint-status | 9289ea3c-0111-45eb-b8c1-1375f76000ad |  | checkpoint | Surrounding wall material is fire rated and complies with manufacturer specs
checkpoint-status | cbf081ea-c2b6-4d18-818c-6358cadf2048 |  | checkpoint | Distance from cooktop flame to underside of overhead joinery/rangehood complies with manufacturer specs
checkpoint-status | 5a6d0ddd-1e29-4107-aa2b-0a980bfb9b7c |  | checkpoint | Isolation valve has been installed
checkpoint-status | bec28b8a-7a73-4646-bbe0-6e9becb128e0 |  | checkpoint | Gas regulator has been installed
checkpoint-status | 32edafd7-640e-484f-81c4-eb120710a62c |  | checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint-status | 48659d5a-e8bf-4b42-89fb-17396866fe27 |  | checkpoint | Full function of cooktop has been checked
checkpoint-status | 4fa17411-c779-42ec-a0b0-2d63fc623ac7 |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | 36a9e70a-f4b6-4688-9ade-b2b779cf5103 |  | checklist | UQ Testing - Water Hold - Sewer & Stormwater Underslung |  |  |  |  | Yes | UQ Testing - Water Hold - Sewer & Stormwater Underslung | eb301a2b-cd30-43f7-a6ca-bcf809c73d85
checkpoint-status | 87ffe41e-bd59-428a-a5ba-a8da92b7c962 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 4134cf94-1eff-5c58-8aef-9cae19bbf9a7 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 9b7e8753-717e-4618-89de-b3caad736417 |  | checkpoint | Pipe has been checked and is clear of blockage
checkpoint-status | 22d17fcb-9d8b-4f2d-8d79-ec52883bc07c |  | checkpoint | Pipe work is securely clipped and ready to hold water
checkpoint-status | c44fb64d-ce2f-42b0-87fa-649611a836ca |  | checkpoint | Open ends have been sealed
checkpoint-status | 65766b91-f8d1-4943-b7c9-77275ad623bc |  | checkpoint | Test was conducted from stack riser 1m above the highest overflow point
checkpoint-status | 2f994dd7-d1a6-492a-8d92-d9bc899244a7 |  | checkpoint | Test was successful as it held water at an unchanged level for at least 30mins
checkpoint-status | 71a6218c-351d-48e0-8c40-7ce35d045cb5 |  | checkpoint | Water was drained from the pipe at the end of the test
text | a00eebea-55d4-5baf-bd7e-122c988a70b3 |  | textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | d4e9e586-4433-4d09-9c9f-f1949aa9b9db |  | checklist | UQ Corridor Rough In (Non Potable/Rainwater) |  |  |  |  | Yes | UQ Corridor Rough In (Non Potable/Rainwater) | ef0d9306-ef21-42c2-8027-cc8f4057fa35
checkpoint-status | 3032855c-24ea-424e-b561-4a2dcf92649f |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | fbe7c0b5-304a-5a05-8313-7e0960a6acce |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | 4ffddf76-d540-4969-889c-0eb825996117 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | a8268619-40ea-4334-9311-58872c247f9b |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 39801945-b351-488c-b850-4e46e349a4be |  | checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint-status | 5a5d9a59-aec7-4233-a28e-ddce70429ed5 |  | checkpoint | Clips and fixings are correct
checkpoint-status | f751cc9d-fd67-4270-b4a6-9b2a2bb2445c |  | checkpoint | Pipe run position & levels are correct
checkpoint-status | b3fae6dc-47ab-44a3-a2e8-389f734817d4 |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status | a5d234c5-3706-4187-b278-7ea7a92d2084 |  | checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint-status | 240ff766-4c7a-4587-97b9-6776b994fb17 |  | checkpoint | Valve flow direction & disconnection unions are correct
checkpoint-status | 02d30572-9aa9-4d14-9d5e-0c1fd96165ec |  | checkpoint | Extension points have sacrificial valves
checkpoint-status | 78dd69ee-b067-48f4-8630-89cf8aa0c5cc |  | checkpoint | Final check for cross connections has been undertaken
checkpoint-status | 408108f1-adbc-4a04-8572-1713519f5168 |  | checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint-status | 1acb884e-198f-4fe9-8511-88569927bb3c |  | checkpoint | Flexible connections are correct
checkpoint-status | 080f455f-5d8b-4ab1-8264-27e34c61d912 |  | checkpoint | Labels have been applied where required
checkpoint-status | 06c3b59a-1f61-422f-958f-2876968026e4 |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | dc731563-ce0f-4b02-b7c8-99b56d20e215 |  | checklist | UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater |  |  |  |  | Yes | UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater | f3adee41-b2ac-4044-9d6b-9e23dfcad8e2
checkpoint-status | 02a7ac47-5405-480d-a86a-51d12da66320 |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | 1f0a67fd-0eee-59fb-93c8-ba827fe17fd4 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | bdfbc313-ee6a-48bd-b310-6dad40c0aa24 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 01b05c57-7247-4721-b432-f2e710d8767e |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | 9f033310-cb34-49d9-a1cd-7e975820b72b |  | checkpoint | Clips, fixings & anchor points are correct and secure (includes independent clipping (no piggy backed clips)
checkpoint-status | 825b62bf-917a-4524-8bfc-2730bc85d335 |  | checkpoint | Peno has been caulked (top and underside of slab)
checkpoint-status | 5d54e466-7e34-4d17-8ea4-23b45ac2646f |  | checkpoint | Branch junction/s & off set invert levels have been checked and are correct
checkpoint-status | 3431bead-c1c0-43bc-ab83-a172a6026139 |  | checkpoint | Pipes & junctions are clear of debris
checkpoint-status | d2e348b3-76b7-4d5f-a979-056689e7fb28 |  | checkpoint | Inspection opening caps have been tightened and duct tape applied
checkpoint-status | 6da78c9a-3a0a-4e4f-8a3f-874a93dacadc |  | checkpoint | Expansion joint clipped and spacer removed (to allow for expansion)
checkpoint-status | 0171d7dc-83d5-44d4-b582-25b393c6bf7f |  | checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint-status | a6412292-f97d-4dc4-aee5-7e5d308f60b2 |  | checkpoint | Labels have been applied where required
checkpoint-status | 803affdb-f35f-4c56-b8ee-e841072ee562 |  | checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | f6781585-3e4b-4b0b-b5c8-d09b56451bba |  | checklist | UQ Fit Off/ Fixture Install - Wall Tundish |  |  |  |  | Yes | UQ Fit Off/ Fixture Install - Wall Tundish | fe5ca688-45e9-4b91-9766-f86b08fcb634
checkpoint-status | 42947278-7e83-44c9-bbf1-f53f5dc26cef |  | checkpoint | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | a86bc1fc-219d-54fe-95bd-9abf9f8f8a62 |  | textbox | Photos of prior works BEFORE RSG commencement must be included here
checkpoint-status | f9c8371a-6af9-4cc3-9c04-1258955360f0 |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status | 623f2aab-0abb-4721-83a1-69909e1ee184 |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status | af2e154a-c5ce-4466-9ed9-ce669e006742 |  | checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint-status | e62beccf-0e9b-4d36-8ae3-4662592e7565 |  | checkpoint | Tundish has been installed aligned, level and secure
checkpoint-status | 97414404-f210-4155-afc3-b6a1fa95af96 |  | checkpoint | Trap connection is clear of debris
checkpoint-status | 94602692-f9b4-438e-b43a-7bc59947ff42 |  | checkpoint | Fixture has been left covered and protected and the area is clean