## Master List Templates
Id | Type | Name | Values | Prompting Name
f610e499-b7de-411f-b38c-80f54c8baa2a | checklist | Air touch First Fix |  | Air touch First Fix
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
cf254215-124d-4f5d-b990-d185d9a32ac7 | checkpoint | Supply power to surface mount Plug
197b53e3-c2d0-4c14-ba0a-f0defbfbe5bb | checkpoint | Connect power to surface mount plug
117745ad-d868-41c5-8317-a87f2c3fc23d | checkpoint | Main Module connected to gateway
c7a0aa30-025f-4e02-871c-add141fbef60 | checkpoint | Gate way connected to indoor unit
d82eb844-28ab-484e-9ee3-07d5a8b73caa | checkpoint | Main module all connected
870d37b3-dbb0-47e5-83b9-e1494090387d | checkpoint | Dampers connected as per plan
149a925c-f7d6-4e69-b9c5-8229d94c7703 | checkpoint | Control cable run to flush box (Tape over controller connection)
0fd6a3be-f56f-44e1-9b20-b844b659422a | checkpoint | Zones Labeled and marked on plan
c5d669f1-b881-4540-af91-99d2a52bc5b8 | checklist | Air Touch Second fix |  | Air Touch Second fix
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
3adb4798-d3ed-438e-9735-d115f2684542 | checkpoint | Air touch controller mounted level
947acae7-4938-42a3-b95c-18f4b9593935 | checkpoint | Air touch sensors mounted labeled behind switch
717587c8-1e41-4ec7-b152-8a3789abd874 | checkpoint | Air Touch set up and commissioned
a48443d0-36ff-48fd-9fc7-065da6dc1b88 | checklist | Cassette First Fix |  | Cassette First Fix
9813380b-c0c8-49cc-8de1-7157546e3392 | section | Indoor Unit
7ebea9c9-2e39-4781-b816-c6c7430ab48f | checkpoint | Unit Hung Level
b8756e47-8da5-4596-980d-c044c674a6b7 | checkpoint | Threaded rod/Nuts tight and secure
4bab1655-cf42-49b9-a149-010d780ad7af | checkpoint | Indoor Unit Model And serial
353fe3d7-2dec-4472-8445-a351a0068bf7 | checkpoint | Seismic installed (if applicable)
5b087389-cc78-42ef-90a3-2296caeed345 | section | Pair coil pipe run
2ef0e20b-22ba-4a6b-852c-4f261fdcdad5 | checkpoint | Pipes run straight down wall and suported
d14c0f8d-e69f-4973-aad6-5ca7cf273693 | checkpoint | Pipes brought out exterior wall with protective pipe and trade seal
37e68668-41d9-4144-b281-cdb084df6bc9 | checkpoint | Pipes tidy to indoor
919ac7fa-4056-4916-996b-486908067e43 | section | Drain
63780665-b462-44fd-8329-c8b8735e9edf | checkpoint | Unit has pump and is installed to below the max height
320d5f96-937f-43c6-8404-4b3e3f0276a7 | checkpoint | Drain has fall across the full legnth
82b7b66b-2497-4eef-9818-f41029528e60 | checkpoint | Drain exits wall through Trade seal
01b2e7f6-2109-4ed4-85ca-bca06ddb209d | section | Power supply/cabling
08ae6b3b-953b-4ffc-849b-8cc78ec3062a | checkpoint | Interconnect is supported by pipe and or pin clips
c57c563c-a9d1-4c1c-9b78-14a3f98c8f47 | checkpoint | Indoor feed run (if applicable)
f287158f-d83f-4d40-80c3-2561dfb9cc59 | checkpoint | Indoor isolator installed (if applicable)
ab16aaa9-7d14-49c9-be0e-33ef669bbcf9 | checkpoint | Indoor electricla connections
ba28ccc0-feb7-4478-9a67-6e3b3be66119 | checkpoint | Outdoor feed run to switch board
b4fc5a8b-d48f-455b-a9be-f3fdc914c2e1 | checkpoint | Control cable run to flush box
2f859eda-e4e4-41ae-a42e-dc894a90f30a | checklist | Cassette Second Fix |  | Cassette Second Fix
28851d4a-b8f6-42a5-b16c-b65c7c3247ed | section | Indoor Unit
13e65b32-9959-4ec1-9703-a8585fc5ddda | checkpoint | Face plate installed square and flush with ceiling
5eb369e6-dc8f-4c8c-80b6-4fa1a27a2ceb | checkpoint | Face plate plugged into PCB
4900e489-5734-4a87-b7ba-1488995ef960 | checkpoint | Controller installed level
370cd486-d99d-4953-aafa-0a96d797cc0a | section | Outdoor
a9e95ec9-c271-4e87-9f10-44f855466236 | checkpoint | Feet installed
f6939a48-4de9-4b44-9ac9-581bd8fa5d3c | checkpoint | Sitting level
9d007608-8856-4f34-90ed-4ff26024e6b5 | checkpoint | Isolator installed
ca214b4f-bda9-468b-835b-577adceb2a1f | checkpoint | Silicone behind isolator
a253cd9f-7128-4ba1-983e-7c94c6450f2e | checkpoint | Sealed penetration
f238f909-cc98-40a4-853e-6ce4cd884f6f | checkpoint | Wall cap installed
a47748b4-4527-4c3b-82d8-cecf0d1bb676 | checkpoint | pipe connection complete
3e9b8f50-7574-45fb-98db-e4246ede826f | checkpoint | Outdoor model and serial
388a4cb8-7109-426e-9d48-b89ef14fbc11 | checkpoint | Ampt sticker installedExterior drain fit off
74745c9e-2933-43c2-af94-352fe0ea8b14 | section | Power Supply
3e0562af-2a87-42d3-b845-be8638c5e635 | checkpoint | MCB installed
3ece615c-b1aa-4d1a-99e5-3bb111753ce8 | checkpoint | Labelled in switch board
9153a475-ff01-452c-ad3a-4dafde83c2ed | checkpoint | Testing complete
18c17973-570c-4fef-99f5-8e317c7d21fc | checkpoint | COC filled in
9cc46d07-7902-4ab1-adce-508276de085e | checkpoint | Photo
94a8b01a-5e61-4f66-bec2-f43945d017bc | checklist | Decommission AC Unit |  | Decommission AC Unit
ddaa6630-045d-401d-a483-a37526485571 | section | Details
3cdc49f4-92ee-499a-b5ac-427f9d7b8806 | checkpoint | Indoor unit Condition
2aed0b13-00af-4e95-963f-e9d223080fc0 | checkpoint | Outdoor Condition
f5a08100-2c26-47b8-9400-a2f169c19423 | checkpoint | Test unit is cooling/heating correctly
47ce835a-0b20-499e-9f6f-569ed94b76b3 | checkpoint | Units has been pump down correctly
52ec9c7c-d9b8-470f-a655-594014a5ea98 | checkpoint | Old installation with units removed
86358083-1e86-47ae-87e0-cb845fec9378 | checkpoint | Wall plate attached
09c28a1a-259c-4d40-9731-460df4c61b57 | checkpoint | Remote attached to indoor unit
e47d6196-42e5-492a-a56e-39c6cba0fbf3 | checkpoint | Indoor model and serial
b3705229-ae34-45f5-b75f-861e352604c1 | checkpoint | Outdoor Model and serial
3b258c57-98d9-4e34-bc0a-c715d4a5a66e | checkpoint | Indoor and outdoor stored away
53b4cdfd-ed2d-4ac0-b908-d92ba3d4a121 | checkpoint | Electrical left safe (Lock out tagg out)
db9d2907-3dde-596c-b497-0079dcd60412 | checklist | Ducted fit off |  | Ducted fit off
43ee5d29-e904-52a8-bb1d-e0395c6b4b7f | section | Outdoor unit
77750d50-6f7f-5d8c-9408-79b43e950fda | checkpoint | Sitting on feet
5204a1dd-8c4f-575f-8234-75cf75367be0 | checkpoint | Sitting level
325c3792-1203-596a-bcf5-e65900817353 | checkpoint | Isolator installed
b1b8b454-8386-578b-b6bc-37dd45ab1067 | checkpoint | Have we installed silicone behind the isolator
65b3adf7-46e3-5222-82c7-3716485eb26b | checkpoint | Sealed penetration
15276e8f-a8ff-53ee-88fb-cbcaa047cc75 | checkpoint | Wall cap installed
8c13e86d-5a61-52fd-ba27-3b5f79a5ed73 | checkpoint | Pipe connections complete
07d7a250-8020-5f3f-a2e7-2a25f0f73509 | checkpoint | Electrical connections complete
346fccf6-7645-555b-9365-67ae1eeae9a1 | checkpoint | Ampt sticker on unit
1dd8b6d3-f260-5269-868a-3b53ffbfe319 | checkpoint | Drain
e55d06a6-58be-520a-ac84-85eee23468aa | section | Return grille(s)
1c6294b5-e6cf-5257-bea6-cf05be0f35dc | checkpoint | Fitted into neck adapters
f5ee6a9d-a623-52ff-a38a-30f2e2e99b3e | checkpoint | No gaps evident around flange
88981f9e-3d7f-5bea-b39f-9018a9501255 | section | Supply grilles
61f6b43a-147c-5bdd-8215-30da6d1fb91f | checkpoint | All installed
798759aa-b9bd-571a-8894-1f873846cfba | checkpoint | Clean
9846885a-afe0-493e-98c9-233d26281fba | section | Power Supply
c67b3408-d2e1-4f80-b9ae-4d6cb04d496f | checkpoint | MCB fitted off
ce7394c4-32e8-419e-a427-6de6a0e001e9 | checkpoint | Switchboard labelled
334e391d-6436-4d5f-b1ad-e7e545029c69 | section | Electrical Testing
16c9c6d7-a177-405b-8399-24bd7e4f8cb4 | checkpoint | Plant / Equipment Earthing
68b8cd5c-9887-4618-8f26-c197d08836a2 | checkpoint | Insulation Resistance
03cbcced-2327-42dc-95e7-47c43c07ae16 | checkpoint | Polarity
02bd317b-805c-43ee-a617-20f1caf00022 | checkpoint | Voltage
074015a1-c3b0-4588-8582-0ad32a74e444 | checkpoint | Fault Loop Impedance
e9cd8f85-3a45-4353-9f1e-1f891f77e891 | checkpoint | Test Sheet Complete
bdd5cda7-43e6-5934-bc03-37a69b742c8c | section | Commissioning
26d4be49-93a7-42eb-b917-7b3f98ef8815 | checkpoint | Record Heating Temperature – 45 degress and above
de7b6a1b-d59f-477c-b15d-225380db707f | checkpoint | Record Cooling Temperature – 15 degrees and below
9ec5b52b-af87-55b4-b96c-f38bef9399a6 | checkpoint | Record Air Flow (2m/ps)
25ce56d8-5bcd-5578-a7f4-c64501ecb614 | checkpoint | Instruction manual left on site
875202ae-7581-56f6-ab70-62a7cfb9310d | checkpoint | Outdoor unit model and serial number
2b861131-7b9e-51e9-95bf-a57d2d62e13a | checkpoint | Additional photos (if applicable)
e1d90015-8005-5928-876e-fcf6dd3d0792 | checklist | Ducted Prepipe |  | Ducted Prepipe
10092771-7046-51de-9e83-0bbf1a463951 | section | Indoor Unit
70ad7469-27b9-560b-a834-397c4c486e27 | checkpoint | Hung level (all axis)
be517eb6-4c9a-5411-8c31-b9322b772374 | checkpoint | Threaded rod/nuts tight and secure
1cfc7530-611a-5eae-b912-1139fb873f88 | checkpoint | Supply plenum installed
03977493-a704-5b68-a9f4-4ef9e26c0c2d | checkpoint | Top plate stiffener
aaa19e95-6e39-5758-bf32-94fcd8f1218e | checkpoint | Indoor unit model and serial number
eac1070f-d1f3-569e-a322-71c9f387627c | section | Pair coil pipe run
6087756f-7be2-5973-9146-900d6cbd1464 | checkpoint | Pipes run straight down wall
a30280c4-d2f9-52fa-b46d-eafa7c12e58e | checkpoint | Pipes supports through roof cavity to indoor unit
b0870521-7e60-53bb-85d9-9eab42114a46 | checkpoint | Pipes supported down wall to exterior
8a79637e-b626-5d33-a7da-fc6218714040 | checkpoint | Pipes brought out exterior in protective pipe with tradeseal
bfb066a1-1a51-52cf-8c85-c570e6453573 | checkpoint | Pipes brought up to indoor, connected and insulated
1dd8b6d3-f260-5269-868a-3b53ffbfe319 | section | Drain
1251a8fe-9deb-5d32-822f-330b2d304192 | checkpoint | Drain trap is installed
176bfadd-c17e-5a03-b255-784056a3abaf | checkpoint | Drain has fall the length of run
6b54e4f8-149c-5de9-ad46-43ad7168f638 | checkpoint | Drain exits exterior wall with tradeseal
2651cf51-6748-5311-a12e-a69588299761 | section | Power supply/cabling
e4c7d9e7-4534-5d9c-bc74-0d9122e2b117 | checkpoint | Interconnect is supported by pipes and/or pin clips
03683a7e-f2b0-54d5-a436-28b34f1da07e | checkpoint | Indoor feed at switchboard
026aff44-9bfa-5273-a038-ab2096067725 | checkpoint | Outdoor feed at switchboard
8cc20daa-432d-590c-8c71-ac75a512ec35 | checkpoint | Indoor isolator
5c82630a-8728-52bd-8f8e-06b675d72af8 | checkpoint | Indoor electrical connections
864681ac-17f1-5583-90ff-a88660312d86 | checkpoint | Outdoor isolator loop with tradeseal
c45bf07d-e89a-5edc-ba91-bea6710c3bf5 | checkpoint | Controller cable run and brought out through flushbox
e55d06a6-58be-520a-ac84-85eee23468aa | section | Return grille(s)
dfcec88a-0da5-531e-81fe-147100848962 | checkpoint | Framed in on 2 sides
7790ebc1-1295-5b46-9ec7-0a943d989eee | checkpoint | Framing is above gib line
9c569601-299f-5bb9-abd3-71739bae15de | checkpoint | Neck adapter installed
a3982d7b-46f5-56da-9217-3fee9d129841 | section | Ducting
868e0424-3f5b-5aa4-a1b0-319fddef030a | checkpoint | Supply ducting installed
10372326-d3fb-5bbf-8f08-ce8da7b88c35 | checkpoint | Return ducting installed
c977d8bc-29ea-5a0a-9099-4a5e083fe4c1 | checkpoint | Grille locations marked on plan
2b861131-7b9e-51e9-95bf-a57d2d62e13a | checkpoint | Photos
ee5bbe63-6520-5c49-986d-586f707a4b10 | checklist | Highwall Fitoff |  | Highwall Fitoff
2ea6aae4-416a-55b0-bed8-ba67c6f283a0 | section | Indoor unit
d8174b54-ea09-57be-bfd1-bcac7f3f7fde | checkpoint | Installed level
9fbe020c-ee56-5bfc-ac20-db6d6d64b39e | checkpoint | Drain fitted and secured
fd8aaff9-7a57-59bd-b1ac-09ee853bc6a9 | checkpoint | Pipes insulated
c83027ca-f480-5768-b43f-a879d62ee1c5 | checkpoint | Wiring correct
43ee5d29-e904-52a8-bb1d-e0395c6b4b7f | section | Outdoor unit
8f434238-fc40-52f7-a744-1c0e850ac165 | checkpoint | Unit is level
63961157-dcaf-5790-9632-7179957f5ca6 | checkpoint | Unit is on feet
acf0eeea-6a21-5ba9-8f9c-00a0b9e6c0f5 | checkpoint | Isolator installed with correct terminations
b1b8b454-8386-578b-b6bc-37dd45ab1067 | checkpoint | Have we installed silicone behind the isolator
a576977e-0025-5231-ac24-1c77977faac0 | checkpoint | Wall penetration is sealed
15276e8f-a8ff-53ee-88fb-cbcaa047cc75 | checkpoint | Wall cap installed
6d0502b4-0f34-5a61-bd27-63448e0e0bea | checkpoint | Pipe connections correct
0222e9be-12a8-50c7-88dc-2dd212a09dbb | checkpoint | Electrical connections are correct
1dd8b6d3-f260-5269-868a-3b53ffbfe319 | section | Drain
836d1300-2650-54b7-bfe5-fd28d498588f | checkpoint | Securely fitted off
fefa0428-8785-5469-92aa-7d40b79d8c87 | section | Unit details
57bd4505-97b2-54d0-a534-8ea400f109b8 | checkpoint | Indoor unit plate
f4a6566b-beec-5b31-9e6e-bd78f3fabd4d | checkpoint | Outdoor unit plate
994225b1-53b9-575e-bf1f-83d441455fc2 | section | Power Supply
cb70bb18-6b7b-589d-a8a8-c57e32f3a932 | checkpoint | MCB fitted off
6e0caf2c-7bab-54fd-b34b-5efb96f6ab72 | checkpoint | Switchboard labelled
90291f7b-5202-409f-b9c8-a00e26090b71 | section | Electrical Testing
8841e5b0-afce-42ee-a43a-76e48e3fba27 | checkpoint | Plant / Equipment Earthing
fd96f9b6-6a96-4b21-9be7-9fc21160e4f0 | checkpoint | Insulation Resistance
16164aa2-06c3-4c7f-9d26-110c680d1347 | checkpoint | Polarity
b60aa6f3-fc12-4f9d-92e9-6e555282ea7d | checkpoint | Voltage
bd2599b3-4b5e-4bf3-885c-0d10854ca3ed | checkpoint | Fault Loop Impedance
5106bb0d-b363-494a-8d90-d8871e07c7d3 | checkpoint | Test Sheet Complete
bdd5cda7-43e6-5934-bc03-37a69b742c8c | section | Commissioning
f3df06f2-620c-4324-b446-cbe08ffd87a0 | checkpoint | Record Heating Temperature – 45 degress and above
239bc4b9-b16a-47e2-9250-0edd5559a914 | checkpoint | Record Cooling Temperature – 15 degrees and below
90fd09f1-04ee-59e5-a414-0ca582f59bc4 | checkpoint | Remote and instruction book left on site
d43e1134-b1c0-573e-a6cd-c6e31303d136 | checkpoint | Ampt sticker on outdoor unit
00c1c453-b8d3-5b9c-9611-f0da5a51ad65 | section | Additional Photos
2b9c1527-26d7-5531-95ea-a4081d11a131 | checkpoint | Additional photos (if applicable)
6c18d633-a7c1-5892-b87f-edb99f53bc3c | checklist | Highwall Prepipe |  | Highwall Prepipe
246177cc-067a-546b-8198-337f2b93d84c | section | Top Plate
e817081a-d671-59a4-b292-e82b79efab70 | checkpoint | Top plate stiffeners x2
eac1070f-d1f3-569e-a322-71c9f387627c | section | Pair coil pipe run
6087756f-7be2-5973-9146-900d6cbd1464 | checkpoint | Pipes run straight down wall
17da2236-f5c6-55fb-99da-f1cb3fbe3376 | checkpoint | Pipes secured at indoor unit and bent at right heigh
ba7af446-f3bf-50d7-bed0-14e111cd604f | checkpoint | Supports are in place on pipework
31d99002-9278-5e64-8b3a-81903069f1e4 | checkpoint | Interconnect fixed at 300 centres/taped to pipework
1e63bac3-b908-52a5-bac9-bf0d29b78e0c | section | Exterior pipework
f07c8304-b4b8-5adf-bb63-2b5f04176802 | checkpoint | Has tradeseal and pipe protection been installed for exterior pipes
8d378ac8-1baf-5be7-834c-8a9851fe917d | section | Drain installation
be657b7b-0af6-5ea9-8e98-00d1cf6b4c2a | checkpoint | Indoor taped to bottom of pipes
e7603c3e-deb4-5337-bb11-1f42377a63f8 | checkpoint | Has drain got significant fall from indoor to outdoor
b832acd8-aa78-5901-8a42-cd9e5326807c | checkpoint | Exterior brought through building paper with protection pipe and tradeseal
706d9f54-1429-5039-b000-9d753aa9a714 | section | Powersupply
89c90586-d877-5ef5-b218-7b207af85673 | checkpoint | Feed located at switchboard
f1716d35-8180-5710-bbdf-087a2b0d6cc9 | checkpoint | Isolator loop with tradeseal
be5c40f3-5d59-5ea6-83eb-c97a7937d31f | checkpoint | Tail brought out with pipework
78a42ede-4c50-5666-8515-27bc089533bd | checkpoint | Has power supply been clipped every 300mm and is clipped on side of trusses. If ran with pipe work is this every 300mm also
101fac59-7a64-51d4-ab70-00cf2d57fc8f | section | Pipes Pressurized
e176f9a6-e751-5777-a625-0e0ed07619bb | checkpoint | Have internal pipes been looped and welded together
dfaba010-f148-5f2b-80ff-e7b619019ab4 | checkpoint | Have external pipes been welded and Schrader installed
e8009b07-60e4-57b6-a2b2-040a0b68fce1 | checkpoint | Please show pipes holding 400PSI Minimum (this can be greater than 400PSI)
ff1493bb-f9ec-5b40-b259-1d06026e7f8e | checkpoint | Have we got photos of stickers on internal and external pipes advising this
00c1c453-b8d3-5b9c-9611-f0da5a51ad65 | section | Additional Photos
2b9c1527-26d7-5531-95ea-a4081d11a131 | checkpoint | Additional photos (if applicable)
8a4862a2-64d0-49ec-b53d-bb3c1832e662 | checklist | Hung Appliance First Fix |  | Hung Appliance First Fix
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
6463ec84-a916-44e4-9559-bae5caf34793 | checkpoint | Power supply Run
e95a37ca-1460-4776-b704-9f4cc36f94c2 | checkpoint | Control cable run
46317437-a054-4c43-bfd6-05826956488b | checkpoint | Flush box/ enclsure installed
80f281bd-5693-4ecc-8a35-971c882b5a36 | checklist | Hung Appliance Second Fix |  | Hung Appliance Second Fix
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
06b20558-3dca-4c5f-adf6-c057961e0422 | checkpoint | Isolator/surface socket installed
74ef2caa-2ec2-48d6-b1a6-aabe61e7132c | checkpoint | Controller installed
a155fbfa-12f9-47c5-8712-3b418e8d6b4b | checkpoint | Flush box/ enclsure installed
080151fc-8221-433e-a040-05517f59a886 | checkpoint | Units installed Level and to manufactrure instrucitons
78412cc9-3bf7-5c13-93bc-bbafa158c65f | checklist | Small Commercial - After Project |  | After Project
32478a70-3599-593b-8f6a-8a63b14868a3 | section | Customer Follow up
2a048d8b-8995-5b9c-92b5-812324f48093 | checkpoint | Follow up with customer on installation and training with in 2 weeks of occupation
8be2110f-605e-512b-b6b7-80967be3cfa7 | checkpoint | Set up maintenance agreement and submit for approval.
0a38c365-bcc1-5c1a-a19e-5cbc493e0ce1 | checklist | Small Commercial - Commissioning |  | Commissioning
da1465dc-6f34-52f6-b18c-5838fc396db1 | section | Commission AC units
09eee05e-b098-514a-b6fa-fd2341a0506b | checkpoint | AC Units, Power on, units vacced and crackecd
206aaba5-5c5d-51a6-aa73-47f80f9a178a | checkpoint | Units operated in heating and cooling
68bb94d4-f6d0-529c-9756-ea9abfea5aa4 | checkpoint | Airflows balance for AC Ducted - Design airflow obtained +10%
2ccce29a-4225-52c8-be57-0c2bcff42e54 | checkpoint | Commissioning sheet filled out
4ebb0ad9-6704-500f-8028-6ecb1d897cb7 | checkpoint | AC Units model and serial numbers recorded and photographed
48677be0-d0d2-53a6-9919-0337bb8a42ba | section | Commissioning Ventilation Systems
ae369caf-d623-5247-b791-a72235349d10 | checkpoint | Fresh air systems, airflows commissioned +10% of design airflow
1a0132d1-73e2-5aa1-aa74-b4800bfd2537 | checkpoint | Extract systems, airflows commissioned +10% of design airflow
6ab86807-2ffc-558f-a754-ea4ce4bb597c | checkpoint | Ventilation commissioning sheet filled out
396c065e-d8fb-5f1c-a262-868357aaeb02 | checklist | Small Commercial - First Fix |  | First Fix
9cac26a2-4c4f-516e-a752-7613e04a3b30 | section | Penetrations
17ec9896-1c6c-5886-8122-f45e9a424e38 | checkpoint | Penetrations are marked out on roof and walls
0cb6d706-9fb0-53a3-b2be-2491757f22ea | checkpoint | Penetrations being done by builder. Builder has been infomed of our requirements
2b861131-7b9e-51e9-95bf-a57d2d62e13a | checkpoint | Photos
d00ebb95-b3db-5572-bf6c-083fb840b7da | section | AC Preppies and prewire
471523cd-dd73-558b-b243-3eaafac1e9d8 | checkpoint | AC Units (Ducted or Cassette) Units have been hung and siesmically restrained
7742df31-11c1-5ab6-9cf8-15a04c9c1e41 | checkpoint | AC Units refrigeration pipe and interconnect cable runs between indoor and outdoor. Connected at indoor if cassete or ducted
0903d9cc-b2fb-555f-9a75-7456c6f71e3e | checkpoint | AC Units Condensate drains have been run to agreed connection point by plumber or outside.
8284f2b9-194c-5dfa-b871-4e48a1421e3f | checkpoint | AC Units Power feed to indoor and out door run
2cac99de-179f-5201-be68-80d29c0731b4 | checkpoint | AC units Pipe work put under pressure 500 PSI and leak checked. Label added to pipework at outdoor location.
5683c432-c2be-5dd5-9be4-55aa0b14e79b | checkpoint | AC Units (Ducted) solid and flexible ducting has been run and restrained
ad1aeb89-5d2f-48ee-b8b3-e4fbc464c6a0 | checkpoint | Photos
95fd8627-7ffb-5f7c-a8b4-9ffb81be4ec0 | checkpoint | Drawing marked up for as builts.
11a27920-90e6-556c-878a-b9155d89de5e | section | Toilet Extract Systems first fix
fb809dd7-3069-5b2b-85df-97d90f735f8d | checkpoint | Toilet extract fans installed
61dddfd4-b186-5c81-b2eb-7208552ce6d1 | checkpoint | Toilet extract cowl supplied to builder
c8731a8d-497c-5156-bc90-a2c639883186 | checkpoint | Solid nude extract duct installed
cde07a44-2596-5b19-b876-5e901ec87de3 | checkpoint | Toilet extract cowl installed
3ca1c228-4893-575f-8777-21ef167568c2 | checkpoint | Flexible ducting installed and connected
5d501576-ec8f-55bb-b6e9-eae50b026484 | checkpoint | Extract grill boots installed
a13fea68-9617-5647-93fc-3667485665fd | checkpoint | Fan is pre wired and connected
a8cc3043-25e0-550d-97e6-2aad25f9e306 | checkpoint | Builder advised of hatch location and size
6f869257-b227-56fb-9686-c0f6a230bcd1 | checkpoint | Builder advised of undercuts to doors required
bc87f0fb-5faf-5d18-900b-b7236f17c787 | checkpoint | Builder advised of door grill location and size for penetration to the door
cbd83e1d-5eff-59f7-97a9-4a712ab3ba02 | checkpoint | Drawing marked up for as built
c9073401-1273-46b5-934b-d5017a60b1ad | checkpoint | Photos
a3d5a1ef-6421-5ba1-a577-14b029170581 | section | Fresh Air Systems first fix
a94a37d7-54f6-5cb0-b939-2656b4682fea | checkpoint | Fresh air iline fan installed (if applicable)
c7219362-34f8-5e7b-a7da-90e3b3762da2 | checkpoint | Fresh air roof mount fan installed (if applicable)
7f5543e1-b8d8-52a1-8952-d90acb9b3555 | checkpoint | Fresh air in take cowl or lourve installed (if applicable)
c624f141-1be7-55b0-b16c-a79dc7ae968b | checkpoint | Fresh air filter box and filter installed or filter in roof mount fan dropper (if applicable)
13a36ac2-f0b4-53f1-8833-3725f0ba2f22 | checkpoint | Fan / heaterbank is pre wired and connected
09a5daab-bfb1-5ce0-8d86-fc75cd9d00b8 | checkpoint | Builder advised of hatch locations and sizse
cdd7efa8-7de5-5520-bfc1-1ff973c5cdcb | checkpoint | Grill boots installed
37ec91f4-9c26-5701-881f-cbba12951258 | checkpoint | Grill Locations mark on plan
f032d208-6550-562d-8489-8afd4ee0392d | checkpoint | Flexible ducting installed and connected to grill boot
427a9aa9-ce3e-543d-ab15-5c15c494b229 | checkpoint | Drawings marked up for as builts
e325b34e-5707-4546-8465-5706e45fc2a4 | checkpoint | Photos
c59d104e-2d56-56f8-941c-b76df81aa074 | checklist | Small Commercial - Pre start stage |  | Pre start stage
000447ae-3628-523a-846e-2765cc79f664 | section | Drawings
740f87f5-a80e-5138-952b-19a93cd0c685 | checkpoint | Drawings saved in job
4d0375d2-ccb4-5644-8d3e-f5e514827833 | checkpoint | Unit/plant selections labelled on drawings
2cb611a7-c17d-584e-8a3d-f81b56141c8c | checkpoint | AC pipe sizes shown on drawings
5e5d190d-488f-5ba9-9395-9a6562908d56 | checkpoint | Ducting sizes shown on drawings
b9d44031-be90-5a80-8881-284154dc803b | checkpoint | Penetrations to wall and roof are shown (with sizes)
7bee30c6-7e4a-55ca-a2de-a0c4254bd150 | checkpoint | Condensate connection points marked on drawings
2b861131-7b9e-51e9-95bf-a57d2d62e13a | checkpoint | Photos
9ea9f41f-5e6f-52bb-9cf2-9df6f4546aad | section | Purchasing
66e93e05-ff95-5ad5-9c3a-a82a9c1c33c8 | checkpoint | All plant has been ordered for first fix
3d5f9238-2114-5bad-9c7c-7c7b2d62eac1 | checkpoint | All plant has been ordered for second fix (check Programme)
dfa06c80-0548-4852-ac9f-9c3cf2d51e3c | checkpoint | Photos
cf54b55b-9c7a-5056-8a2f-94718453675d | section | Health and Safety
c2d33aac-9b9a-5130-9e31-521706e9ca87 | checkpoint | SSSP has been produced
a824a5ed-5b4f-5df3-80d6-9c6a5156597e | checkpoint | SSSP has been dropped to site office
e44034f7-f63a-579a-b464-2c98db828513 | checklist | Small Commercial - Project Completion |  | Project Completion
c33d5268-fff4-51b4-874a-d5e87d3072b7 | section | Compliance Information
a07c8e13-2f4b-5929-a8f0-3173ba253b61 | checkpoint | Airflow test results submitted
cdbd65ca-89da-56d3-a2dd-b780eed6eb18 | checkpoint | Warranty completed and submitted
2f5e51fb-7cf8-58ae-818a-cc8bf6af8982 | checkpoint | Producer statements completed and submitted
7fa99e3e-88df-5ac7-84c7-dcf739cb7c3e | checkpoint | COC submitted
03054628-7815-5aa6-8a73-1f11bb952b58 | checkpoint | As builts updated and submitted
f644fbe0-ad39-57db-b2ba-4d39b1866315 | checkpoint | Photos uploaded
08e4b0f4-ab47-5210-8495-ea5242578b21 | section | Manuals
c9660018-35e9-5afe-a303-1a9e1db4b062 | checkpoint | Manual info compiled
12fa51b2-20c7-5ce8-9737-743132aa9e0a | checkpoint | Manual Structure and descriptions completed in word document
8c61e088-2bf1-59de-95ee-4f21f77e0de8 | checkpoint | Word document converted to PDF snd relevant info added to each section
7354ba90-4905-56ce-8d25-e13b858b9e7b | checkpoint | Manual submittied to client
65f5042e-4a28-5d82-89d9-aab6e624ef1c | checklist | Small Commercial - Second Fix |  | Second Fix
49856cc1-5a6a-580a-85da-2527446447e0 | section | Outdoor AC units
e5db5167-c908-56e9-b31b-66549378b7fd | checkpoint | AC Units Pipes connected, pipe run and capping.
78fe438d-bec2-5f3d-963d-7020743200f2 | checkpoint | AC Units Pressure tested to 500psi 24 hrs
b6116acf-20ed-5b52-9c0c-e6f0009e10db | checkpoint | AC Units vaced to,100mirons and precharge with extra charge
4420f818-4bd3-5cb8-b6d5-21bfff890d73 | checkpoint | Units wired and ready for Commissioning
f9f6fc0d-e1be-5569-9743-b61558decc42 | checkpoint | Units fixed with stainless fixings
2b861131-7b9e-51e9-95bf-a57d2d62e13a | checkpoint | Photos
6b9806b1-03b7-54b1-873c-efb6955333f9 | section | Indoor AC units
91429ec4-65a2-5370-9e7c-f75ed4d213c6 | checkpoint | AC Units Higwall Pipes, drain and cabling is connected
cfba42cd-13e4-5f84-a7dc-0a855f04ac31 | checkpoint | AC Units are level
48604a94-7806-5983-bf46-1bbeac38c087 | checkpoint | Units are left clean and any marks on walls are removed
fc52a1a2-2fb2-5840-9793-f34a5dcd1de5 | checkpoint | Remote controls are mounted to wall in agreed locations or handed to client
1fe6fac0-b851-4c0e-b6f5-4848f968de78 | checkpoint | Units fixed with stainless fixings
39d44eac-397c-4bef-ac3e-377a01312d9e | checkpoint | Photos
649ce94f-4a15-5c4e-bcba-178cfd537f68 | section | Fit Off Grills
62869af6-a711-54b1-981b-a3f4acf8f5d3 | checkpoint | AC Ducted unit grills fitted
91d763cc-4b07-52a2-8723-75be5ff061bd | checkpoint | AC Unit covers fitted
412394d6-25ea-58d4-b58f-2aa9c8e9cfc5 | checkpoint | Toilet extract grills fitted
a0f8ee90-ab0b-558b-87ba-0909fda296e9 | checkpoint | Fresh air grills fitted
8c12da24-d16a-4f56-b0d6-e179663db3fe | checkpoint | Photos
ad9d6e58-935e-55e1-889b-de7798a4b629 | checklist | Ventilation - First fix |  | Ventilation - First fix
0c5ce72b-b50d-59c1-a3ce-db4ae82efafa | section | Fan
68e10d7c-c265-563b-895e-689907d37cb7 | checkpoint | Suspended in accessible location
5204a1dd-8c4f-575f-8234-75cf75367be0 | checkpoint | Sitting level
b9c77a5c-b577-56d2-ab09-64a0a75f1ee4 | checkpoint | Power Supply brought up to surface mount powerpoint
ad230ce1-cff9-5956-9ae8-2faf0b2d84d5 | checkpoint | Power supply run to switch as shown on plan.
2a3bcaa0-e78c-52ef-ac88-abff5b932af0 | checkpoint | Filter
e392cb7c-9da9-586d-a58d-0c064b1729f0 | checkpoint | Filter box installed in accessible location
8ab21a97-deb8-5fb9-9bac-dead6af6a79e | checkpoint | Filter inside filter box
a3982d7b-46f5-56da-9217-3fee9d129841 | section | Ducting
dcf60256-1ad1-5101-b6f9-df5dc7c4c07b | checkpoint | Ducting run to locations shown on plan
1fcba150-b84d-554b-af0d-0cc8c3a4d53c | checkpoint | Air inlet is brought out in correct location
47e0f60c-5eb0-5f33-b19d-0880aa3f465b | checkpoint | Air inlet has tradeseal
a3f87c68-dee9-5b29-bfcf-4ce283c599b5 | checkpoint | All joins are taped
c977d8bc-29ea-5a0a-9099-4a5e083fe4c1 | checkpoint | Grille locations marked on plan
5c19e479-2aad-5453-9cd2-8d5188dfc151 | checklist | Ventilation - Second fix |  | Ventilation - Second fix
52f837fa-499b-580f-b260-d2391770aaa4 | section | Grilles
59acf45e-0770-5ed2-8362-7becba81f4be | checkpoint | All internal grilles are fitted off
cdb5e834-e294-54b8-86e5-64e9706bd8ca | checkpoint | Air inlet is fitted off and sealed
2e84f952-4c66-5972-8622-cee0166aab20 | section | Testing/Commissioning
a9e7b8f2-1cee-5660-a64a-47031dc36c33 | checkpoint | Fan switch is fitted off
626786a9-4788-539d-96e8-ebdfa1486605 | checkpoint | Fan switch is labelled
66d0260a-b569-53df-a76d-c678f3ec8b32 | checkpoint | Fan works on switch (switch is up the right way)
c16bc9dd-470f-5bef-95a4-2d81be1f28ea | checkpoint | Air flow felt through all supply grilles.
7d935e56-b7e0-5487-a359-93cdffbee033 | checklist | Walkthrough Checklist |  | Walkthrough
1be75a78-df38-594c-a3d8-8671642cbe7e | checkpoint | Power outlet locations confirmed and marked
51c39314-3f90-5a66-ae9c-82d71a5609bc | checkpoint | Light switch locations confirmed and marked
9a352152-bdea-5e5d-affc-5d410c5c6a01 | checkpoint | Switchboard locations confirmed and marked
896d17b9-21ad-52c1-9511-ed8ec396b10b | checkpoint | Bathroom outlet locations confirmed and marked
b45c9f48-c1c1-57b8-b10f-173e97cd3a8a | checkpoint | Bathroom outlets vertical or horizontal
cf3c0b96-0d2a-5578-a664-75c2eb4beb0c | checkpoint | Towel rail locations confirmed and marked
9f424859-b7e2-5782-a4d8-d35b3c32062f | checkpoint | Interior light locations confirmed
bffb0ff3-5c83-5bd4-a258-cbec2687a477 | checkpoint | Exterior light locations confirmed and marked
b0ff5a7e-34b9-53a7-bac1-0e48eb9e6add | checkpoint | Exterior fan grills soffit mount or wall mount
b08c8290-8c20-5843-800e-921b3c157c90 | checkpoint | CCTV locations confirmed
3c24ba49-b822-5115-9e0e-d732813be2c5 | checkpoint | CCTV soffit mount or wall mount
a537bfb4-8c55-5a0f-9900-ff5e0a957da1 | checkpoint | Aerial locations confirmed
16131259-fa1a-53b9-ad61-41ca6dbc21f3 | checkpoint | Aerial cabling location confirmed and marked
2caf321f-8c92-51c2-8c99-ef39e5eaa91d | checkpoint | Plans updated with changes