## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DN1210-017 ITP Watermain Open Cut | itp |  |  |  |  | DN1210-017 ITP Watermain Open Cut Rev 1
section | SECTION 3 – PRE-CONSTRUCTION - P&G and ESTABLISHMENT
checkpoint | 3.1.1 - Pipe Laying
label | Detail - Method Statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - Appendix V
label | Verifying Document - Watermain Construction Work Pack- Open Cut Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.1.2 - Butt-Fusion Welding
label | Detail - Method Statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - PS- 22.9.4
label | Verifying Document - Watermain Butt-Fusion Welding Work Pack Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.1.3 - Electrofusion (EF) Welding
label | Detail - Method Statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - PS- 22.9.5
label | Verifying Document - Watermain Electrofusion (EF) Welding Work Pack Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.1.4 - Pipeline Pressure Testing
label | Detail - Method Statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - Appendix V
label | Verifying Document - Watermain Pipeline Pressure Testing Work Pack Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.1.5 - Water Disinfection
label | Detail - Method Statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - PS- 22.8
label | Verifying Document - Watermain Disinfection Work Pack Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.1.6 - Extent of Line Setout
label | Detail - Ensure line and level of watermain RM has been marked out and agreed with Engineer in accordance with water RM drawings.
label | ○ Identify any clashes before construction.
label | ○ LOT- markup
label | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
label | Standard / Specification - Design Drawings
label | Verifying Document - ITP Sign Off / Mark-up
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.1.7 - Existing Watermain system (If any)
label | Detail - Confirmation of existing Watermain network.
label | Acceptance / Conformance Criteria - Survey Informations
label | Standard / Specification - Appendix XI
label | Verifying Document - Survey data
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 4 – PRE-CONSTRUCTION - MATERIAL, PERSONEL & THIRD PARY APPROVALS
checkpoint | 4.1.1 - Material grading: Alternative: PSD,MDD Embedment Materials
label | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone compliance.
label | Acceptance / Conformance Criteria - Engineer Approval
label | Standard / Specification - PS 22.4.5, AS/NZS 2566.2
label | Verifying Document - Lab Test Report NZS 4407 3.8.1
label | Testing Quantity Required (based from schedule qtys) - 1 test
label | ○ 1 Test for each additional 1000m3
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2.1 - Material Grading - Materials for Backfilling
label | Detail - Tranch Backfill Material: Particle Size Distribution
label | Acceptance / Conformance Criteria - Engineer Approval
label | Standard / Specification - PS 22.4.5 AS/NZS 2566.2
label | Verifying Document - Lab Test Report NZS 4402 4.1.3
label | Testing Quantity Required (based from schedule qtys) - 1 test
label | ○ 1 Test for each additional 1000m3
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2.2 - Material Maximum Dry Density
label | Detail - Trench Backfill Material: MDD
label | Acceptance / Conformance Criteria - Engineer Approval
label | Standard / Specification - PS 22.4.5 NZS 4402:1986, Test 4.1.2
label | Verifying Document - Lab Test Report NZS 4402 4.1.2
label | Testing Quantity Required (based from schedule qtys) - 1 test per Material, per Source
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2.3 - Weathering index: Materials ( GAP65)
label | Detail - Trench backfill material, WI
label | Acceptance / Conformance Criteria - Engineers Approval AA,AB,AC,BA or CA
label | Standard / Specification - PS-21.7.2
label | Verifying Document - Lab Test Report NZS 4407 3.11
label | Testing Quantity Required (based from schedule qtys) - 2 test per source
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2.4 - Crushing Resistance: Materials (GAP65)
label | Detail - Trench backfill material, CR
label | Acceptance / Conformance Criteria - Engineers Approval >100kN
label | Standard / Specification - PS-21.7.2
label | Verifying Document - Lab Test Report NZS 4407 3.10
label | Testing Quantity Required (based from schedule qtys) - 2 test per source
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2.5 - Geotextile/Geogrid
label | Detail - Minimum Strength Class C & Filter Class 1 or TNZ F/7geotextile is to be used in Trench Backfill of Drainage pipe in Wet conditions.
label | Acceptance / Conformance Criteria - Engineers Site Representative to inspect trench.
label | Standard / Specification - PS-16.5.7
label | Verifying Document - Certification
label | Testing Quantity Required (based from schedule qtys) - 1 time
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.3.1 - Pipes (PE/ Sleeve)
label | Detail - Manufacturer's record and location of extrusion plants.
label | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
label | ○ Full Traceability information and certification of analysis for the resin batch.
label | Acceptance / Conformance Criteria - Engineer Approval
label | Standard / Specification - PS-22.4.1 (d)
label | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets.
label | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.3.2 - Valves, Adaptors, Flanges and Fittings
label | Detail - Have a pressure rating no less than the designed pressure.
label | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
label | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
label | Acceptance / Conformance Criteria - Engineer Approval AS/NZS 4129
label | Standard / Specification - PS-22.4.2
label | Verifying Document - Test Report showing pressuer rating and compatibality from the Material Suppliers
label | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.4.1 - Pipe and fittings (PE100- DN355 PN12.5)
label | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Acceptance / Conformance Criteria - As Per Drawings
label | Standard / Specification - Design Drawings
label | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.4.2 - Valves, Adaptors, Flanges and Fittings
label | Detail - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
label | Acceptance / Conformance Criteria - As Per Drawings
label | Standard / Specification - PS-22.4.2
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.4.3 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
label | Detail - Confirm Specification and material in good condition.
label | Acceptance / Conformance Criteria - Site Engineer Approval
label | Standard / Specification - PS-22.4.1
label | Verifying Document - Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.4.4 - Bidim/Geogrid
label | Detail - BIDIM A29 Duragrid 30/30 or similar.
label | Acceptance / Conformance Criteria - Site Engineer Approval
label | Standard / Specification - PS-22.4.1
label | Verifying Document - Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | SECTION 5 – CONSTRUCTION ACTIVITY
checkpoint | 5.1.1 - Foundation Compliance
label | Detail - On Granular or Cohesive Material
label | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
label | (Or)
label | ○ Cohesive Material: Vane Shear Strength 70kPa
label | Standard / Specification - PS 21.6.5 and AS/NZS 2566.2
label | Verifying Document - Scala/Shear test result
label | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
label | Verification Activity: Activity - W
label | Review of text reports/records or other evidence of compliance
label | Verification Activity: By - SE
checkpoint | 5.1.2 - Undercut approval
label | Detail - Trench Foundation
label | Acceptance / Conformance Criteria - 300mm Max cut
label | ○ IFC Drawing Sheet 320
label | (Or)
label | ○ Engineers approval
label | Standard / Specification - IFC Drawing WAT 0320. AS/NZS 2566.2/2002
label | Verifying Document - Lab Test Report / Watermainline record
label | Testing Quantity Required (based from schedule qtys) - If Undercut required
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 5.1.3 - Undercut Backfill Compliance
label | Detail - On Granular Material / On each layer as per specification / on the trench foundation.
label | Acceptance / Conformance Criteria - Visiual Inspection
label | Standard / Specification - IFC Drawing WAT 0320
label | Verifying Document - Lab Test Report / Watermainline record
label | Testing Quantity Required (based from schedule qtys) - Every Undercut
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 5.1.4 - Bedding Zone Compaction Testing (PE Pipe)
label | Detail - On Granular Material / On each layer as per specification (Imported Sand or GAP20) NDM testing as per NZS4407:2015, Test 4.3
label | Acceptance / Conformance Criteria - Bedding Zone:
label | ○ 100mm minimum thickness (compacted) over the bottom of the trench.
label | ○ Minimum Compaction- Trafficable 95% MDD and Non-Trafficable 85% MDD
label | Standard / Specification - IFC Drawing 0320-1, AS/NZS 2566.2/2002
label | Verifying Document - NDM:Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - As per Water Specification. One test per 20m evenly spaced intervals.
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 5.1.5 - Laying of Pipes
label | Detail - Lay in straight lines, beginning at the lower end of the line.
label | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
label | Acceptance / Conformance Criteria - As Per Drawings.
label | ○ Facing upwards
label | Standard / Specification - PS22.7.1 C
label | Verifying Document - Visual Inspection / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 5.1.6 - Pipe Installation on Curved Alignments
label | Detail - All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
label | Acceptance / Conformance Criteria - AS Per POP 202
label | Standard / Specification - PS 22.7.1 D
label | Verifying Document - Visual Inspection / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - WP (Review of text reports/records or other evidence of compliance)
label | Verification Activity: By - ENG
checkpoint | 5.2.1 - Flanges
label | Detail - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
label | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
label | Standard / Specification - PS 22.7.5
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - First flanged joint
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2.2 - Bends
label | Detail - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
label | ○ Fitting must meets the same PN rating as the adjacent PE 100.
label | ○ Fittings must be suitable for producing the joints shown on the Drawings.
label | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
label | Standard / Specification - PS 22.4.2
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
label | Verification Activity: Activity - H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 5.3.1 - Butt-Fusion pre construction weld test
label | Detail - One weld on the most common size of pipes used for the project.
label | ○ One weld on the thickest wall (highest PN) pipe
label | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode.
label | ○ WMS Report
label | Standard / Specification - PS 22.9.6 (a)
label | Verifying Document - Visual Inspection/ Test Reports
label | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.3.2 - Butt-Fusion Welding
label | Detail - Use only semi-automatic or automatic welding machines.
label | ○ Maintain a site record for all butt-fusion welds.
label | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
label | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
label | ○ WMS Report
label | Standard / Specification - Appendix 22. PS 22.9.4 C
label | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report
label | Testing Quantity Required (based from schedule qtys) - Every Welding Point
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.3.3 - Butt-Fusion Construction weld test
label | Detail - Test at least two welds from the first 50 welds.
label | ○ One of the welds to be selected by the Engineer for satisfactory result.
label | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
label | Standard / Specification - PS- 22.9.6 (a) (iv)
label | Verifying Document - Test report
label | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.3.4 - Survey
label | Detail - Inspection of Pipeline Inverts
label | Acceptance / Conformance Criteria - Vertical design Setout:
label | ○ Pipes ≤ 1% grade: +/- 10mm variance
label | ○ Pipes > 1% grade: +/- 20mm variance
label | Horizontal design Setout:
label | ○ +/-30mm variance
label | Standard / Specification - PS- 21.7.6, Table 21.15
label | Verifying Document - Survey Data / As-built record
label | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 5.4.1 - Electrofusion (EF) pre construction weld test
label | Detail - Use the designated welding equipment and the approved WMS.
label | ○ On the largest size of PE pipe used in this Contract
label | Acceptance / Conformance Criteria - ISO 21751 (strip-Bend test) or ISO 13954 (Peel-decohesion test)
label | ○ WMS Report
label | Standard / Specification - PS 22.9.6 (b)
label | Verifying Document - Visual Inspection/Test Report
label | Testing Quantity Required (based from schedule qtys) - One test welds per operative(Welder)
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.4.2 - Electrofusion (EF) Welding
label | Detail - Required if Butt fusion welding cannot be perform.
label | ○ EF Jointing in accordance with PIPA POP 001.
label | ○ The lead welder or welding supervisor must verify on the site record form.
label | Acceptance / Conformance Criteria - WMS Report
label | ○ Checklist (refer to CWP).
label | Standard / Specification - PS 22.9.5, Appendix 22
label | Verifying Document - Visual Inspection / Electrofusion (EF) welding record checklist. WMS Report
label | Testing Quantity Required (based from schedule qtys) - Every Welding Point
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 5.4.3 - Electrofusion (EF) construction weld test
label | Detail - EF weld quality to be maintained.
label | Acceptance / Conformance Criteria - EF coupler and EF saddle testing
label | Standard / Specification - PS- 22.9.6 (b) (iv)
label | Verifying Document - Test report
label | Testing Quantity Required (based from schedule qtys) - 1 test per 5 welds
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.4.4 - Survey
label | Detail - Inspection of Pipeline Inverts
label | Acceptance / Conformance Criteria - Vertical design Setout:
label | ○ Pipes ≤ 1% grade: +/- 10mm variance
label | ○ Pipes > 1% grade: +/- 20mm variance
label | Horizontal design Setout:
label | ○ +/-30mm variance
label | Standard / Specification - PS- 21.7.6, Table 21.15
label | Verifying Document - Survey Data / As-built record
label | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 5.5.1 - Emebment Zone - (Side Haunch Overlay )
label | Detail - AP 20 backfill Compacted in 200mm Layers.
label | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays .
label | ○ NDM BS to be Carried Out
label | Acceptance / Conformance Criteria - in 200mm layers.
label | ○ More than 85% of MDD.
label | Or
label | ○ Minimum Compaction- Trafficable 95% MDD and Non-Trafficable 85% MDD
label | Standard / Specification - NZS 4407:2015 Test 4.3 Nuclear Moisture Density Gauge; BS
label | Verifying Document - Lab Report / Watermainline record
label | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals. 200mm lift
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 5.5.2 - Pipe Markers
label | Detail - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
label | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
label | Acceptance / Conformance Criteria - AS Per Drawings.
label | Standard / Specification - PS 22.7.3 a
label | Verifying Document - Visual Inspection / Watermainline record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 5.5.3 - Backfill Compaction Testing
label | Detail - GAP65/AP65/LRAP65 Backfill Compacted in 200mm Layers.
label | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
label | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers.
label | ○ Testing to be completed on maximum 200mm lifts of backfill.
label | ○ LRAP65- achive 90% NDM on Grassed Area and 95% NDM on Shared and Carriageway.
label | Standard / Specification - PS- 22.13.5, NDM Standard 25832, NZS 4402 Test 4.1.3
label | Verifying Document - Lab Report / Watermainline record
label | Testing Quantity Required (based from schedule qtys) - As per 200mm lift. One test per 20m evenly spaced intervals.
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 5.6.1 - Pipe Inspection
label | Detail - Inspection of Water Rising Main line
label | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
label | Standard / Specification - Internal
label | Verifying Document - Watermain line record
label | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
label | Verification Activity: Activity - I
label | Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - SE
checkpoint | 5.7.1 - Pressure Acceptance Testing
label | Detail - Backfill/cover with embedment before testing
label | ○ End caps in place, provision for filling the pipeline and bleeding air.
label | ○ Thrust Blocks installed- backfilled and concreted.
label | Acceptance / Conformance Criteria - WatermainRising Main Pipelines – 1250kPa
label | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
label | Standard / Specification - PS 22.7.4, PS 22.7.12(d), PS 22.7.13(b)
label | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
label | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG & TPI
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.8.1 - Watermain Disinfection
label | Detail - Introducing a solution containing a free available chlorine (FAC) residual of 15 – 20 mg/L (ppm)
label | Acceptance / Conformance Criteria - At the end of the disinfection time the Free available chlorine (FAC) in the water being flushed from the pipelines must be at least 5 mg/L.
label | Standard / Specification - PS22.8
label | Verifying Document - Observation and monitoring of disinfection solution on site by Engineer.
label | Testing Quantity Required (based from schedule qtys) - Once for Watermain pipeline
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 6 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - ACCEPTANCE BEFORE COMMENCING DISINFECTION WORK
checkpoint | 6.1.1 - Survey As-Builts
label | Detail - Quality Check on Nee pipeline and structure based on the tolerances in RITS
label | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
label | Standard / Specification - Project Specifications
label | Verifying Document - CAD File as per PS12.3 and Red pen markup only
label | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature