## Sheet1
Type | Name | Values | Prefix | Postfix | Prompting Name
checklist | GPL QA 6 - Quality Control Pressure Test Report (CAM) |  |  |  | QA 6 - Pressure Test #
checkpoint | Quality Control Pressure Test Report:
textbox | Drawing No.:
textbox | Rev.:
button | Test: | Air, Water
textbox | Section
textbox | From
textbox | To
textbox | Specified System Working -
checkpoint | Specified System Test:
textbox | System type
textbox | Pressure (1500 kPa)
textbox | Duration (2 HRS)
checkpoint | 1st Reading
textbox | Time
textbox | KPA
textbox | Ambient Temp
checkpoint | 2nd Reading
textbox | Time
textbox | KPA
textbox | Ambient Temp
checkpoint | Test Result - Passed?
textbox | Repeat
note | Company: Geschke Group
note | Phone: 03 9798 1619
note | Address: 45 Pacific Drive, Keysborough
note | Project: I NEED TO ADD INDIVDUALLY
note | Principal: I NEED TO ADD INDIVDUALLY
checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Signature Sign-Off added below | Yes, No
button | Principal Contractor Representative Sign-Off added below | Yes, No
checklist | GPL QA 16 - PE Electrofusion Welding - Field Operational Sheet (CAM) |  |  |  | QA 16 - EF00#
checkpoint | Operator Details
textbox | Name
textbox | ID No.
textbox | Company
textbox | Address
checkpoint | Welding Machine Details
textbox | Manufacturer
textbox | Type/Model
textbox | Serial Number
textbox | Year Built
checkpoint | Actual Pipe Size
textbox | Type
textbox | Brand
textbox | En
textbox | OD
textbox | Ovality %
checkpoint | Fitting Data
textbox | Brand
textbox | Type (Coupling, Tee, Reducer etc.)
checkpoint | Unit Setting
textbox | Manual
textbox | Automatic
checkpoint | Preparation
textbox | Cleaned and Peeled
textbox | Pipe/Fitting Clamped
checkpoint | Welding Times
textbox | Joining Seconds
textbox | Cooling Minutes
checkpoint | Conditions
textbox | Ambient Temp
textbox | Weather
textbox | Preventive Measures
checkpoint | Power
textbox | Mains
textbox | Gen Set
checkpoint | Operator Sign Off
checklist | GPL QA 25 - Butt Welding Checklist (CAM) |  |  |  | QA 25 - BW00#
checkpoint | Operator Details - Pass once entered
note | Supervisor sign off at completion of ITP after weld #16
textbox | Name
textbox | Certification Number
checkpoint | Welding Machine Details
textbox | Manufacturer
textbox | Type/Model
textbox | Serial Number
textbox | Year Built
checkpoint | Pipe / Material Details - Pass once entered
textbox | Dn (OD)
textbox | SDR
textbox | En
textbox | Type
textbox | Parameter
textbox | SLP
textbox | SHP
checkpoint | Weld #1
textbox | Time
textbox | Ambient C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #2
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #3
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #4
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #5
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #6
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #7
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #8
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #9
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #10
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #11
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #12
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #13
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #14
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #15
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Weld #16
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
note | Company: Geschke Group
note | Phone: 03 9798 1619
note | Address: 45 Pacific Drive, Keysborough
note | Project: Clyde North Primary School
note | Principal: Hutchinsons
checkpoint | Foreman Sign-Offs completed - Click to Attach Signature(s) below
note | Operator Sign-off added to each weld above as required
button | Geschke Group Signature Sign-Off added below | Yes, No
button | Principal Contractor Representative Sign-Off added below | Yes, No
checklist | GPL QA 8 Below Ground Pipework Checklist (CAM) |  |  |  | QA 8 - BGS00#
checkpoint | Principal Contractor Permits Issued
checkpoint | Set out pits trench depths and runs.
textbox | Drawing & Revision # (or Attach photo below)
textbox | Survey setout completed by:
textbox | Manhole Coordinates - enter Eastings & Northings
textbox | Starting IL established - enter IL
button | Survey confirmed drain started at correct IL | Yes, No
button | Drawings attached | Yes, No
checkpoint | Pipes and fittings comply with relevant Authority and Specification.
note | Spec#: AS3500
textbox | Materials used:
button | Approved by Principal | Yes, No
checkpoint | Bedding material, placement and compaction meets specification.
note | Spec#: AS3500
note | 7mm Q-Minus Bedding
checkpoint | Laying and jointing of pipes - RL and fall
button | PVC pipe with Solvent welded joint | Yes, No
button | Fall achieved | Yes, No
checkpoint | Connections to pits and existing services as per spec and Australian Standards
checkpoint | Hydrostatic tests are carried out as required.
button | Air or Water? | Water, Air
note | Inspected and recorded by Independent Certifier or PIC
checkpoint | Mirror tests completed
textbox | Independent testing company:
button | Inspection report attached | Yes, No
checkpoint | Placement and compaction of backfill and material meets spec - attach applicable reports below
tickbox | Civil specification 13.4: Trench Backfill Service trenches shall be backfilled with General Fill (Type B Material) compacted to 98% SDDR within 500mm below the Subgrade Level and to 95% SDDR below this depth in pavement areas. The moisture content of the compacted material shall be within 0% and +3% of SOMC.
tickbox | 5% Stabilised Sand
textbox | Compaction testing completed by:
button | Compaction report attached | Yes, No
checkpoint | Temporary cover provided to open drain.
checkpoint | PVC/ Plastic caps to open ends
checkpoint | As built information updated onto drawings
button | Drain installed as per nominated drawing | Yes, No
button | Invert levels checked by independent surveyor | Yes, No
note | As Built drawings to be updated as required
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
note | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
note | Company: Geschke Group
note | Phone: 03 9798 1619
note | Address: 45 Pacific Drive, Keysborough
note | Project: Clyde I NEED TO ADD INDIVDUALLY
note | Principal: I NEED TO ADD INDIVDUALLY
checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Signature Sign-Off added below | Yes, No
button | Principal Contractor Representative Sign-Off added below | Yes, No
checklist | GPL QA 8 Below Ground Pipework Checklist - Water, Recycled Water and Fire (CAM) |  |  |  | QA 8 - W/RW/F-00#
checkpoint | Principal Contractor Permits Issued
checkpoint | Set out of trench depths and runs
textbox | Drawing & Revision # (or Attach photo below)
textbox | Survey setout completed by
button | Drawings attached | Yes, No
checkpoint | Pipes and fittings comply with relevant Authority and Specification
note | Spec#: AS3500
textbox | Materials used
button | Approved by Principal | Yes, No
checkpoint | Bedding placement and compaction and material meets specification
note | Spec#: AS3500
note | Packing sand encased pipe
checkpoint | Jointing of pipes
note | If either of below are selected, please reference the ITP/Attach below - As applicable
tickbox | Electrofusion GPL QA 16 form
tickbox | Butt Welds GPL QA 25 form
checkpoint | Connections to pits and existing services as per spec and Australian Standards
checkpoint | Testing of pipes are carried out as required
note | If below is selected, please reference the ITP/Attach below - As applicable
tickbox | Water system hydrostatic test
tickbox | Fire system test completed by Independent tester
checkpoint | Additional service within trench
button | Are there other services to be installed in this trench? | Yes, No
button | If Yes have these services been installed prior to backfill of trench? | Yes, No
checkpoint | Placement and compaction of backfill and material meets spec - attach applicable reports below
tickbox | Civil specification 13.4: Trench Backfill Service trenches shall be backfilled with General Fill (Type B Material) compacted to 98% SDDR within 500mm below the Subgrade Level and to 95% SDDR below this depth in pavement areas. The moisture content of the compacted material shall be within 0% and +3% of SOMC.
tickbox | 5% Stabilised Sand
note | Detectable marker tape
checkpoint | Temporary cover provided to open drain
checkpoint | PVC/ Plastic caps to open ends
checkpoint | As built information updated onto drawings
note | Ongoing
note | To be provided
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
note | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
note | Company: Geschke Group
note | Phone: 03 9798 1619
note | Address: 45 Pacific Drive, Keysborough
note | Project: I NEED TO ADD INDIVDUALLY
note | Principal: I NEED TO ADD INDIVDUALLY
checkpoint | Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Supervisor Sign-Off added below | Yes, No
button | Principal Contractor Representative Sign-Off added below | Yes, No
checklist | GPL QA 8 Below Ground Pipework Checklist - Water, Recycled Water and Fire CAM |  |  |  | QA 8 - W/RW/F-00#
checkpoint | Principal Contractor Permits Issued
checkpoint | Set out of trench depths and runs
textbox | Drawing & Revision # (or Attach photo below)
textbox | Survey setout completed by
button | Drawings attached | Yes, No
checkpoint | Pipes and fittings comply with relevant Authority and Specification
note | Spec#: AS3500
textbox | Materials used
button | Approved by Principal | Yes, No
checkpoint | Bedding placement and compaction and material meets specification
note | Spec#: AS3500
note | Packing sand encased pipe
checkpoint | Jointing of pipes
note | If either of below are selected, please reference the ITP/Attach below - As applicable
tickbox | Electrofusion GPL QA 16 form
tickbox | Butt Welds GPL QA 25 form
checkpoint | Connections to pits and existing services as per spec and Australian Standards
checkpoint | Testing of pipes are carried out as required
note | If below is selected, please reference the ITP/Attach below - As applicable
tickbox | Water system hydrostatic test
tickbox | Fire system test completed by Independent tester
checkpoint | Additional service within trench
button | Are there other services to be installed in this trench? | Yes, No
button | If Yes have these services been installed prior to backfill of trench? | Yes, No
checkpoint | Placement and compaction of backfill and material meets spec - attach applicable reports below
tickbox | Civil specification 13.4: Trench Backfill Service trenches shall be backfilled with General Fill (Type B Material) compacted to 98% SDDR within 500mm below the Subgrade Level and to 95% SDDR below this depth in pavement areas. The moisture content of the compacted material shall be within 0% and +3% of SOMC.
tickbox | 5% Stabilised Sand
note | Detectable marker tape
checkpoint | Temporary cover provided to open drain
checkpoint | PVC/ Plastic caps to open ends
checkpoint | As built information updated onto drawings
note | Ongoing
note | To be provided
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
note | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
note | Company: Geschke Group
note | Phone: 03 9798 1619
note | Address: 45 Pacific Drive, Keysborough
note | Project: I NEED TO ADD INDIVDUALLY
note | Principal: I NEED TO ADD INDIVDUALLY
checkpoint | Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Supervisor Sign-Off added below | Yes, No
button | Principal Contractor Representative Sign-Off added below | Yes, No