## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 01. Issued for Construction Drawings |  | 1. Issued for Construction Drawings | 8b34247c-5439-4472-9287-ebcbd1681cc2
| checkpoint | IFC drawings issued. Clear scope of work
0e17550c-3b90-5dfc-9855-ef43c7cb476b | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
0025b9f5-2e1e-5877-ba77-6e6c932a9e41 | note | Leading Hand - N/A
2719fd41-d2bf-5c45-a926-d5023a05af7f | note | Supervisor - N/A
19f768bd-51ef-52a1-8084-bd01bd82e35d | note | Third Party (state) - P - Worley’s project engineer
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 02. Change Details |  | 2. Change Details | 249af915-394f-4577-a87c-bdbc7ef30898
| checkpoint | Change Details. Details of design changes Details of approved scope changes
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 03. Waste Management/Disposal |  | 3. Waste Management/Disposal | ae8803f3-b658-4b9b-8fcf-c38eca888446
| checkpoint | Waste Management methodology produced by civil contractor and confirmed by CTS Environment Department. All excavated contaminated material and concrete to be taken off site. To be taken to landfill.
4698783f-ec6e-5d20-bf90-cfde4c17cec5 | note | Applicable Documents - CTS General Civil Construction Specification CTS Containment Environmental Ground Soil Management plan RW-231
5430428d-81e7-5e65-8710-db3fc5579b9a | note | Leading Hand - N/A - Leading Hand
4ff7448e-62b3-5cce-b5ea-5dfb7e5785d8 | note | Supervisor - H - UCCL Supervisor or Project Engineer
e109757d-a898-537b-8a69-83005b7e8513 | note | Third Party (state) - H - Environmental team/ Client Representative
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 04. Site survey and set out of levels. |  | 4. Site survey and set out of levels. | 060aceb2-de73-460e-9f91-f3ec409d50af
| checkpoint | All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Existing services located, marked, and protected if required. All works to be accordance with CTS Excavation works Specification. CTS General civil construction Specification
7d6c91ab-12d4-51b5-9d8a-fa0b627a3ecd | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
1342c53d-f9a7-57c9-8140-e846c8774ec8 | note | Leading Hand - P - Surveyor
aee2882f-b145-55f3-a81f-63183a9e3c52 | note | Supervisor - Surveyor - H
4249eaa0-49b7-5377-b71a-456e7071a0c0 | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 05. Demolition scope and removal of bitumen/grass/concrete from compound bund walls and prepare and shape. |  | 5. Demolition scope and removal of bitumen/grass/concrete from compound bund walls and prepare and shape. | d2c83746-7e65-4e7e-9054-c56ba1cd6473
| checkpoint | All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Structures footings are not undermined. Inspection once the bitumen/concrete has been removed prior to sand blinding. Site plan of area inspected to be signed off by Civil inspector after each inspection.
08e661d4-f80a-57ab-9115-e54cfa16dc8b | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Site plan with inspection areas inspection.
43aba6b6-af31-5c18-93be-d5c79ac08e74 | note | Leading Hand - N/A - Leading Hand
77b7d251-eed0-59f2-8e12-b81853294cda | note | Supervisor - Leading Hand - H
d0e7b2d9-6b57-5b9f-993c-264a2ef1019a | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 06. Demolition scope and removal of bitumen and concrete away from tank annular |  | 6. Demolition scope and removal of bitumen and concrete away from tank annular | c5b5c449-e91a-49b7-b52f-4ee9c41a04dd
| checkpoint | All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Tank annular is not undermined. Inspection once the bitumen/concrete has been removed prior to sand blinding. Site plan of area inspected to be signed off by Civil inspector after each inspection.
16ca7d1a-1d86-5420-8163-1f1327c742a0 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Site plan with inspected areas.
c1436631-296a-59bb-9d36-06c8f3467926 | note | Leading Hand - N/A - Leading Hand
4bdd0229-f4d5-5c90-91e0-b401841c74d8 | note | Supervisor - Leading Hand - H
ff6de013-0554-5efc-b475-1ff0a876a43b | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 07. Demolition scope and removal of bitumen and concrete from compound floor |  | 7. Demolition scope and removal of bitumen and concrete from compound floor | 46f7b2b4-2fca-48c3-b184-c854b18c1ec9
| checkpoint | All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Structures footings are not undermined. Inspection once the bitumen/concrete has been removed prior to sand blinding. Site plan of area inspected to be signed off by Civil inspector after each inspection.
5cf58501-bfd5-594e-b326-0a50b5207486 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Site plan with inspected areas
d7a2e7c5-8ad8-5818-9718-0c89da4ea51f | note | Leading Hand - N/A - Leading Hand
38a91b2d-2977-5842-bc1c-d994379d2975 | note | Supervisor - Leading Hand - H
7f7fe736-75b0-5e2b-887d-757031b04462 | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 08. Subbase preparation under liner compound bund walls |  | 8. Subbase preparation under liner compound bund walls | 4e83bcbf-e33f-4e92-a7f9-fc3a38560954
| checkpoint | All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Existing services located, marked and protected if required. All works to be accordance with CTS Excavation works Specification. 50mm sand/cement bedding clean and free of debris Sand/cement placed to line and level. Site plan of area inspected to be signed off by Civil inspector after each inspection.
4598452a-4480-535f-b805-51c706657e79 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Site plan with inspected areas.
f37d2b6e-fefd-5160-96dd-17389899631d | note | Leading Hand - N/A - Leading Hand
5c943679-809f-5922-b494-2466ea3b775b | note | Supervisor - Leading Hand - H
826726fd-38d5-5212-bc56-aff1176fa40c | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 09. Subbase preparation under liner around annular |  | 9. Subbase preparation under liner around annular | a348413c-05fc-4bb1-ae34-db738071f45e
| checkpoint | All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Existing services located, marked, and protected if required. All works to be accordance with CTS Excavation works Specification. 50mm sand/cement bedding clean and free of debris Sand/cement placed to line and level. Site plan of area inspected to be signed off by Civil inspector after each inspection.
f553f0d2-7427-54ae-8443-7cc10c785cce | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 CTS General Civil Construction Specification Site plan with inspected areas.
e599ca26-b8b9-583d-b057-135a9543493c | note | Leading Hand - N/A - Leading Hand
d9a77602-d000-51ef-abfa-9aa838a45ff2 | note | Supervisor - Leading Hand - H
0cd038ec-3b74-59b7-9391-f0398caf35d3 | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 10. Subbase preparation under liner over compound floor |  | 10. Subbase preparation under liner over compound floor | d86326af-30c2-43cf-8fb8-065249d5036e
| checkpoint | All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Existing services located, marked, and protected if required. All works to be accordance with CTS Excavation works Specification. 50mm sand/cement bedding clean and free of debris Sand/cement placed to line and level. Site plan of area inspected to be signed off by Civil inspector after each inspection.
a2913cb8-2c7c-582c-8e54-09d9bc07718a | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 CTS General Civil Construction Specification Site plan with inspected areas
96d3dd03-a4b9-5f37-8d0a-efcde90447f8 | note | Leading Hand - N/A - Leading Hand
f3335744-bd4f-5506-960c-5c44f17258b6 | note | Supervisor - Leading Hand - H
877f0df6-09a4-5fff-862b-af2fdc3ac29c | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 11. Install subsoil drainage. |  | 11. Install subsoil drainage. | 29a7060d-1fbe-4c47-8065-a8344fcd8327
| checkpoint | All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Existing services located, marked and protected if required. All works to be accordance with CTS Excavation works Specification. Site plan of area inspected to be signed off by Civil inspector after each inspection.
82235ec1-b087-57aa-abe2-5c50012e2437 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 CTS General Civil Construction Specification Site plan with inspected areas
381556cc-11b6-57e9-bb3d-7e8b204af316 | note | Leading Hand - N/A - Leading Hand
3a97e4d2-a78a-5e0f-b651-8f3fa81c96b8 | note | Supervisor - Leading Hand - H
e2ec5a75-13df-5fe0-a46d-8fd9cb9c2305 | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 12. Install 1.5mm PE liner on Bund Walls. |  | 12. Install 1.5mm PE liner on Bund Walls. | 497180b3-6098-4ca7-817f-a8f8db36a24d
| checkpoint | PE liner installed with Bidim A64 cloth T&B PE liner installed as per installers QA-QC and Worley’s QC requirements as per Civil /Struct Design pack 310449/C1 Rev A drawing notes T3084782 on IFC drawings issued 05 May 2023 Review installers QC documentation before placing Bidim Site plan of area inspected to be signed off by Civil inspector after each inspection.
0e2b4eec-3301-5ca8-928a-f4437eacdd0d | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Site plan with inspected areas
0dff8067-edcd-573f-8e20-66ade34d8853 | note | Leading Hand - N/A - Leading Hand
3c2c51d5-63b7-5912-ba5d-fb1c21a8958a | note | Supervisor - Leading Hand - W
f312b117-90aa-5480-8b22-0b88a2382081 | note | Third Party (state) - W - UCCL Supervisor or Project Engineer
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 13. Install 1.5mm PE liner on tank shoulder. |  | 13. Install 1.5mm PE liner on tank shoulder. | 0d67bc23-4105-48f7-b88b-db3582ac10fd
| checkpoint | PE liner installed with Bidim A64 cloth T&B PE liner installed as per installers QA-QC and Worley’s QC requirements as per Civil /Struct Design pack 310449/C1 Rev A drawing notes T3084782 on IFC drawings issued 05 May 2023 Review installers QC documentation before placing Bidim Site plan of area inspected to be signed off by Civil inspector after each inspection.
2ea1b228-7075-50d3-8593-f9b63fdc5cc6 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Site plan with inspected areas
d7fd8dd9-c45b-5ec6-b78c-436f876f04b8 | note | Leading Hand - N/A - Leading Hand
1826221e-5f24-53d1-9d41-bd1ef869a0e5 | note | Supervisor - Leading Hand - W
34b74a81-54c1-5076-bd38-89d605bd617d | note | Third Party (state) - W - UCCL Supervisor or Project Engineer
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 14. Install 2mm PE liner on compound floor. |  | 14. Install 2mm PE liner on compound floor. | 6b365391-b67e-4c24-9983-e090ee206cb6
| checkpoint | PE liner installed with Bidim A64 cloth T&B PE liner installed as per installers QA-QC and Worley’s QC requirements as per Civil /Struct Design pack 310449/C1 Rev A drawing notes T3084782 on IFC drawings issued 05 May 2023 Review installers QC documentation before placing Bidim Site plan of area inspected to be signed off by Civil inspector after each inspection.
0c366490-8216-5175-b45a-90d3b377a580 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Site plan with inspected areas
542211fe-ce30-5da1-98e8-e8b9cdd4fe14 | note | Leading Hand - N/A - Leading Hand
aaf3c399-a30f-512d-b180-92be8434853e | note | Supervisor - Leading Hand - W
3d5fcd31-ce1f-54d7-852a-090e4faecd56 | note | Third Party (state) - W - UCCL Supervisor or Project Engineer
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 15. Concrete pre-pour inspection Bund Walls |  | 15. Concrete pre-pour inspection Bund Walls | 6ed12754-e970-4784-b522-1381f2bca3df
| checkpoint | All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 All works in accordance with CTS General Civil Construction Specification Concrete pre-pour check sheet completed and filed with ITP. General Civil Construction Specification Concrete shall be high or special grade certified “ready mixed concrete” manufactured at a currently certified plant and shall comply with NZS 3104. Delivery dockets retained. Site plan of area inspected to be signed off by Civil inspector after each inspection.
f2cb0bc5-42bc-54d6-b0eb-9f86abb4dde9 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Site plan with inspected areas
b2d18204-9031-5118-9fe8-f4e9b6756538 | note | Leading Hand - N/A - Leading Hand
e8ff2228-6344-5b82-97e1-12bceb54a62a | note | Supervisor - Leading Hand - W
33452c39-0817-55c5-926a-b8dba6d3ad06 | note | Third Party (state) - W - UCCL Supervisor or Project Engineer
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 16. Concrete pre-pour inspection Tank Shoulder |  | 16. Concrete pre-pour inspection Tank Shoulder | 1f4c2225-9db9-44de-8fbe-9bcaafec962a
| checkpoint | All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 All works in accordance with CTS General Civil Construction Specification Concrete pre-pour check sheet completed and filed with ITP General Civil Construction Specification Concrete shall be high or special grade certified “ready mixed concrete” manufactured at a currently certified plant and shall comply with NZS 3104. Delivery dockets retained. Site plan of area inspected to be signed off by Civil inspector after each inspection.
0c181d79-124c-5823-acf2-69c444367599 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Site plan with inspected areas
73c9e3eb-9ccc-5cf5-9c47-d9f89ca1ec06 | note | Leading Hand - N/A - Leading Hand
a4ebea82-591d-5fce-914a-3c554a922bfe | note | Supervisor - Leading Hand - W
c2f60af6-f133-53bb-afe3-7e7d401f620e | note | Third Party (state) - W - UCCL Supervisor or Project Engineer
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 17. Replace 50mm sand on top of HDPE liner followed by recovered in situ aggregate then 75mm AP40 aggregate. |  | 17. Replace 50mm sand on top of HDPE liner followed by recovered in situ aggregate then 75mm AP40 aggregate. | 8b01ab1b-0e63-48e1-9618-e99885c21a5a
| checkpoint | All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 All works in accordance with CTS General Civil Construction Specification 50mm sand/cement bedding clean and free of debris All layers placed to line and level. Compound floor to be graded to allow free draining to lowest point. Site plan of area inspected to be signed off by Civil inspector after each inspection.
2e6a09c8-6993-5389-8194-5602ed7767dd | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 CTS General Civil Construction Specification Site plan with inspected areas
6553031c-1042-5d2b-9043-5383b234aa3a | note | Leading Hand - N/A - Leading Hand
db57aa83-ff43-5cf3-b0f6-c74657585f29 | note | Supervisor - Leading Hand - W
108df430-c8d6-56a6-9cef-9f8cfe08c20e | note | Third Party (state) - W - UCCL Supervisor or Project Engineer
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 18. Compound Flood Test |  | 18. Compound Flood Test | 103ef413-51cd-4660-9caa-e61eb510ca1a
| checkpoint | Timing of the flood test will be conducted as per the approved Compound C3 Flood test methodology. All items on Compound Pre-Flood Check Sheet to be completed by relevant parties. The infiltration test will be as detailed in HSWA COP 47 ‘Secondary Containment Site plan of area inspected to be signed off by Civil inspector after each inspection.
fca553ae-aeca-5900-ab1f-4cd43ecad4b2 | note | Applicable Documents - UCCL Compound C3 Flood test methodology HSWA COP 47 ‘Secondary Containment’
e83a41db-4bb8-5d11-bdee-19fccf0fdedb | note | Leading Hand - N/A - Leading Hand
465c31ef-b097-5115-b946-f1eaafcdfc68 | note | Supervisor - Leading Hand - H
1e7abad5-4fad-59aa-9406-3574d47c0c3a | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 19. Sealing construction/expansion joints on tank annular |  | 19. Sealing construction/expansion joints on tank annular | ee753c81-42d9-4269-a3d5-b9bbc80d9366
| checkpoint | All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Seal manufactures specifications followed. Site plan of area inspected to be signed off by Civil inspector after each inspection.
6d0d1887-62b1-51a5-ace8-4ea9133c552d | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Product manufactures specifications Site plan with inspected areas
92eebef7-1b32-547b-9452-5c828928d724 | note | Leading Hand - N/A - Leading Hand
0ccf7b25-3d0f-50e1-8857-14d46f3625bc | note | Supervisor - Leading Hand - W
4c9db8ea-24cb-5fa8-b929-78d41ec78849 | note | Third Party (state) - W - UCCL Supervisor or Project Engineer
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 20. Install Denso steel coat base protection or approved equivalent (Viscotaq) around tank annular |  | 20. Install Denso steel coat base protection or approved equivalent (Viscotaq) around tank annular | 0bb2a8f1-49ef-4eb2-be44-89002dd9301e
| checkpoint | All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Viscotaq installed in accordance with manufacturers recommendations. Site plan of area inspected to be signed off by Civil inspector after each inspection.
3a0afbf9-e05f-5285-863b-8478938e73e0 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Product manufactures specifications Site plan with inspected areas
3842f58d-6221-5ca1-a00e-05f86c213754 | note | Leading Hand - N/A - Leading Hand
34f559ff-92a2-51bb-afdb-b0d8d002dc66 | note | Supervisor - Leading Hand - W
68a710f0-071e-5077-af62-591618a4c67d | note | Third Party (state) - W - UCCL Supervisor or Project Engineer
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 21. Sealing construction/expansion joints on bund walls |  | 21. Sealing construction/expansion joints on bund walls | c60b8395-d209-496f-82cc-dab1a70a5b1d
| checkpoint | All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Site plan of area inspected to be signed off by Civil inspector after each inspection.
a0b7ac6e-cf1e-5661-8907-f2b67beea4c0 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023 Product manufactures specifications Site plan with inspected areas
ece80e22-d5ec-5b3a-9c10-c17d62490e76 | note | Leading Hand - N/A - Leading Hand
780e6e13-7dd7-5ce4-9b34-342c288bb414 | note | Supervisor - Leading Hand - W
9e605fd1-581e-5bdb-82a4-8cf8d62bcae6 | note | Third Party (state) - W - UCCL Supervisor or Project Engineer
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 22. Complete final Civil inspection and close off ITP. |  | 22. Complete final Civil inspection and close off ITP. | 29372d70-c292-4347-8b65-34bc5085e000
| checkpoint | ITP / QC has been completed; all steps & hold points signed by relevant party. All work scope completed as per design pack and any field instructions issued during construction. Job site has been left tidy.
4aa95d40-8292-5a3e-97e4-1cfe2105f6cf | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
d1fc134f-5065-5346-9eba-d46edb8ede69 | note | Leading Hand - N/A - N/A
42a47edc-1de1-5f53-8ded-b3d3d79211bb | note | Supervisor - N/A - H
65377666-0710-5438-bd27-ae8f3f14909a | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 23. Non-Conformance reporting |  | 23. Non-Conformance reporting | 2ce78e3d-4438-49cd-990f-3986969d5432
| checkpoint | In accordance with the approved Work Pack, drawing, Field Instruction and agreed scope of work. CTS General Civil Construction Specification CTS QC Requirements for Civil Works
6f14e852-6918-5523-9684-4b24a9301774 | note | Applicable Documents - UCC internal NCR and or CTS Lucidity event NCR CTS QC Requirements for Civil Works
6f5fb261-725c-5dfd-9b69-0c54a2e61a69 | note | Leading Hand - N/A - N/A
f8ce29ad-8e27-5dbf-a7e4-7899bfacda69 | note | Supervisor - N/A - H
835794cf-e72e-57c9-9e14-48152675b96c | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 24. “As- Built” Information/Drawing |  | 24. “As- Built” Information/Drawing | 76f5c50e-e1f7-4ba2-9fb7-20378c014dfa
| checkpoint | CTS General Civil Construction Specification CTS QC Requirements for Civil Works
2a7211a2-a378-593d-8b4e-4656c4c274bf | note | Applicable Documents - Section 9 CTS QC Requirements for Civil Works
56f389f2-532f-5d87-9baa-398ce5d8a2db | note | Leading Hand - N/A - N/A
4aab0fac-b204-5ed4-9153-e67a987ea182 | note | Supervisor - N/A - H
ffc98fef-dc60-5e4b-b9a6-bcf9e4a3e55b | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 25. Reference info, specifications etc |  | 25. Reference info, specifications etc | 4fef4776-af48-4b28-b806-0be0283e0162
| checkpoint | Applicable Documents - Relevant sections of Controlled doc’s Material specs (Epcon, coatings etc)
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 26. Punch listing |  | 26. Punch listing | c2a105ed-4421-4299-adee-06f489f3592e
| checkpoint | CTS QC Requirements for Civil Works
49cb1a04-4022-5d22-96c6-37b96b0b09cd | note | Applicable Documents - Section 10 CTS QC Requirements for Civil Works
de64f149-502e-53cd-83da-445556b73679 | note | Leading Hand - N/A - N/A
9cab090d-73c6-555f-87a2-f027d0c2cf2b | note | Supervisor - N/A - H
f1cde280-d554-5091-9a8b-dd33dac49504 | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - 27. Compilation of inspection and test record |  | 27. Compilation of inspection and test record | 226be7ba-0ca8-4711-a8d4-303214fc9780
| checkpoint | CTS General Civil Construction Specification CTS QC Requirements for Civil Works
a5807a29-0d3a-5c26-8f28-9100cc3fbb95 | note | Applicable Documents - Signed off ITP & work pack, Section 7 and 8 UCC Producer Compliance Statement. These documents will be compiled to form a complete MDR/QC Pack.
81c12676-8c0c-5dc1-85c7-efb260910f75 | note | Leading Hand - N/A - N/A
595aa7bd-24ce-5b15-a642-aa63cc861b71 | note | Supervisor - N/A - H
fcec7d48-6354-59f2-a81c-d3536d32f0f9 | note | Third Party (state) - H - UCCL Supervisor or Project Engineer
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - C3 Bund Compound Upgrade |  | C3 Bund Compound Upgrade | 43d191ed-96f5-4f73-baa6-f14aa14ce080
| checkpoint | 1. Issued For Construction Drawings
de289349-c21b-557a-adc8-d892a2d66b2b | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
45e9dd59-53ac-577c-9a0a-feca6517e088 | note | Acceptance Criteria - IFC drawings issued. Clear scope of work
5e5eb155-58ab-5d3a-9882-64a8a4f04ab1 | note | Leading Hand - N/A
720869e9-9d9e-5990-8694-91a8529269fb | note | Supervisor - N/A
b470049d-cece-5267-bf27-7bddbcc3da76 | note | Third Party (state) - P - Worley’s project engineer
| checkpoint | 2. Change Details
f39c932f-90bb-59f8-ac51-acb0e37ef553 | note | Applicable Documents - Details of design changes, Details of approved scope changes
| checkpoint | 3. Waste Management/Disposal
edfb88a7-bd32-5434-bb26-ccffc5c02877 | note | Applicable Documents - CTS General Civil Construction Specification, CTS Containment Environmental Ground Soil Management plan RW-231
8258a023-41eb-5c56-8e3f-b3ce2d39900b | note | Acceptance Criteria - Waste Management methodology produced by civil contractor and confirmed by CTS Environment Department. All excavated contaminated material and concrete to be taken off site. To be taken to landfill.
a3d43d1b-744e-572e-9935-66db6ec929de | note | Leading Hand - N/A - Leading Hand
d49dd988-cf12-59ec-a693-9a5535eea18d | note | Supervisor - H - UCCL Supervisor or Project Engineer
421c48f8-c03f-5697-a30f-e5ba2f495e0f | note | Third Party (state) - H - Environmental team/ Client Representative
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4. Site survey and set out of levels.
43e1d58e-73f2-5d3f-a08c-4cd9b7b6c0c6 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
dbc7cd54-d0f9-5f9e-9214-85537fe30a86 | note | Acceptance Criteria - All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
6feff350-3cbe-5cdc-b3fd-43d3522a02e2 | note | ○ Existing services located, marked, and protected if required.
3bebb5ff-8973-52a4-a16a-db1189937088 | note | ○ All works to be accordance with CTS Excavation works Specification.
6726c8ee-c1da-5384-801f-e191065abb2e | note | ○ CTS General civil construction Specification
984f8842-3482-573b-8650-2943777fb2eb | note | Leading Hand - P - Surveyor
9061daa5-5ad8-50c3-abd4-d0757334eb90 | note | Supervisor - H - UCCL Supervisor or Project Engineer
ba2acd2e-7095-5f7a-b4c1-013d14e4dd01 | note | Third Party (state) - R - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 5. Demolition scope and removal of bitumen/grass/concrete from compound bund walls and prepare and shape.
52cc883d-4829-593e-b94d-21ae102d99fd | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
4fab95ff-a571-5c60-b888-f7fbeae66944 | note | ○ Site plan with inspection areas inspection.
0152f77a-c959-5e23-9110-0ef133401712 | note | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
2661971a-d1da-5bc4-aaf3-26c04efab83a | note | ○ Structures footings are not undermined.
65aa5588-98c7-5668-8b3f-f0359bd3bf32 | note | ○ Inspection once the bitumen/concrete has been removed prior to sand blinding.
544d8919-91c9-54bb-8e46-686703e2ecb0 | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
a7004871-9188-595a-9d3b-b203b2d573a2 | note | Leading Hand - N/A - Leading Hand
2a8252b2-ac3a-588c-a8cf-022bc048c165 | note | Supervisor - H - UCCL Supervisor or Project Engineer
35105867-4a53-542f-aaff-fdc17d1f7c48 | note | Third Party (state) - H - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 6. Demolition scope and removal of bitumen and concrete away from tank annular
06dbab3c-5268-5ea1-88f5-12654f0302f8 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
a9d6ecc2-cd54-5c4c-88c3-49a6e4cb89db | note | ○ Site plan with inspected areas.
a05e5d6c-a591-5103-8e0c-4afd1bb986bd | note | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
90b9c299-25d9-5d09-8ac0-a6efbde175cb | note | ○ Tank annular is not undermined.
f5d90f32-35fc-5d9d-8a37-54cbd7dcc135 | note | ○ Inspection once the bitumen/concrete has been removed prior to sand blinding.
ebfdad87-ed0b-53a1-9b3e-c80f5540a5a1 | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
fc4a7477-2a7a-57f2-9b23-37754f6532f9 | note | Leading Hand - N/A - Leading Hand
00c26107-f254-5011-ba35-c139c5419ef5 | note | Supervisor - H - UCCL Supervisor or Project Engineer
7d04b022-f900-566a-8859-239e24599f64 | note | Third Party (state) - H - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 7. Demolition scope and removal of bitumen and concrete from compound floor
01ce6e1e-55f8-5436-8453-fec87588fff0 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
765cfbc1-9b49-50f1-8dc7-23b859ef4274 | note | ○ Site plan with inspected areas
64378036-0f01-59ed-abe2-183b3db43faf | note | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
d49d0a01-da3c-559c-8f15-cc4460cda35d | note | ○ Structures footings are not undermined.
5b678805-e2ab-5430-8d7c-e007d7bc245d | note | ○ Inspection once the bitumen/concrete has been removed prior to sand blinding.
d8be9190-7ea3-5e0d-841b-c8756d9c777e | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
3ca5e38c-557b-55e7-8e7e-b1a648b59054 | note | Leading Hand - N/A - Leading Hand
221f8380-b969-5bef-ba0f-948feb5afc16 | note | Supervisor - H - UCCL Supervisor or Project Engineer
d06f4a1d-b202-5995-a358-dde1614e9358 | note | Third Party (state) - H - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 8. Subbase preparation under liner compound bund walls
2cf36153-0bff-5aa6-b619-6000ee0f9b38 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
d6f15af9-d6b8-5b54-9dcd-425ea448fd82 | note | ○ Site plan with inspected areas.
13c7c5e5-3ca5-5796-a6cf-ca23ebe70d27 | note | Acceptance Criteria - All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
9ce514bb-e073-574f-ad1b-3655b341e686 | note | ○ Existing services located, marked and protected if required.
8a8aeffd-2d08-57fe-848c-5f3c2e8e61d5 | note | ○ All works to be accordance with CTS Excavation works Specification.
6bccf9fa-36b3-53a2-b053-eefc3f71e691 | note | ○ 50mm sand/cement bedding clean and free of debris
6db9ed0f-ed49-5352-959c-f0c69a5575fd | note | ○ Sand/cement placed to line and level.
139debe2-79b3-5429-a3e8-cb5e4ba23eb6 | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
76247134-fb49-52f9-81d7-fff90f803cf4 | note | Leading Hand - N/A - Leading Hand
55d3c70f-4c6a-5b1e-90bb-a3da751e62f6 | note | Supervisor - H - UCCL Supervisor or Project Engineer
3cc16ce0-2847-5fde-b1c2-37e672466572 | note | Third Party (state) - W - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 9. Subbase preparation under liner around annular
55157059-79af-5fe5-91fc-a49931f87b4f | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
b311ac14-fb8e-561f-9ba0-d199666afa58 | note | ○ CTS General Civil Construction Specification
ffe283c8-3b3d-598d-b38f-8b909265f806 | note | ○ Site plan with inspected areas.
261154e4-a94d-5e49-8110-b9a7e974309b | note | Acceptance Criteria - All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
1a1c30b3-de39-5579-85a3-a74b31813008 | note | ○ Existing services located, marked, and protected if required.
a2ab8452-1c8e-5e85-9065-419e068616eb | note | ○ All works to be accordance with CTS Excavation works Specification.
eb4ddb22-9480-52bc-9390-d1b40d3681c5 | note | ○ 50mm sand/cement bedding clean and free of debris
34960900-b24a-5f18-a355-4aa2749973c1 | note | ○ Sand/cement placed to line and level.
77dc9f3b-34a7-5f12-a477-926558878368 | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
58e3d094-e162-5d32-b1f2-e506455d8634 | note | Leading Hand - N/A - Leading Hand
bd9951c9-683a-5cc3-8f8b-70fe2269d70c | note | Supervisor - H - UCCL Supervisor or Project Engineer
039ca727-185e-5492-b86e-358e9804af52 | note | Third Party (state) - W - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 10. Subbase preparation under liner over compound floor
5e49f524-f6f3-52f1-a3aa-5fa2a489ce34 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
94955f22-3989-5d4f-98a5-05afb3539434 | note | ○ CTS General Civil Construction Specification
ef1646d8-c9b6-52d6-ab16-a839cdb26155 | note | ○ Site plan with inspected areas
8404d6cd-5123-5b0a-bf47-2afe9ac13196 | note | Acceptance Criteria - All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
ff321bc9-cefd-5de9-8ff4-1d8ecb7a8f15 | note | ○ Existing services located, marked, and protected if required.
b83b75ff-b4f6-5170-94e0-e5e35cef88db | note | ○ All works to be accordance with CTS Excavation works Specification.
1ef5bac7-db3c-5bc2-95f4-036365c033c5 | note | ○ 50mm sand/cement bedding clean and free of debris
56fe8236-db1b-56fb-ac11-6a8bf465a1ac | note | ○ Sand/cement placed to line and level.
dae187e9-aa13-508c-a7f3-61e96836f5d0 | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
62b24605-0b59-5801-85ac-1ded691c69f1 | note | Leading Hand - N/A - Leading Hand
f09b5425-dbfb-5feb-921c-49da4e179da3 | note | Supervisor - H - UCCL Supervisor or Project Engineer
c8e93d83-39a3-5a56-9949-ecad0ae4d971 | note | Third Party (state) - W - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 11. Install subsoil drainage.
ecd0ed5e-4591-5b5a-8955-876262e8456d | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
919615bf-9766-59d2-8b48-5c37ef0464f1 | note | ○ CTS General Civil Construction Specification
7dd3c208-fbb6-5d5b-bd1a-96e435cf183f | note | ○ Site plan with inspected areas
4e7fa5fa-cbc6-5e3e-bdb6-34803f4c773d | note | Acceptance Criteria - All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
f5339554-ba6d-502d-b421-5a9909e8c1a6 | note | ○ Existing services located, marked and protected if required.
bde5a6c4-b3e9-56fe-8050-9faec2f63b1a | note | ○ All works to be accordance with CTS Excavation works Specification.
2b178690-eb25-5ade-90da-c696d7893d2c | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
b8a595d8-40bb-5732-8024-41c3fe2ea598 | note | Leading Hand - N/A - Leading Hand
9149b55d-1f0b-5e7b-a362-936d00cad7c3 | note | Supervisor - H - UCCL Supervisor or Project Engineer
a0aedb99-2157-5942-a17d-e77c39297c6d | note | Third Party (state) - W - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 12. Install 1.5mm PE liner on Bund Walls.
267a6d39-6bac-5aa8-9933-a6f4781b9caf | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
6b020cf7-ee57-554a-93db-7b2b9aa6d205 | note | ○ Site plan with inspected areas
b4dd7db1-a8e4-572d-b5b8-ed42cd18d1fe | note | Acceptance Criteria - PE liner installed with Bidim A64 cloth T&B
94e4e179-c8c3-5787-812a-1cd03ad601b9 | note | ○ PE liner installed as per installers QA-QC and Worley’s QC requirements as per Civil /Struct Design pack 310449/C1 Rev A drawing notes T3084782 on IFC drawings issued 05 May 2023
844c3998-fdf3-56d4-9494-d2520fa3ec47 | note | ○ Review installers QC documentation before placing Bidim
f420d3fc-76d8-5096-959c-ab176070f510 | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
9a38afe6-c1c3-53ab-b24a-4ab6f3837ab8 | note | Leading Hand - N/A - Leading Hand
5a3432df-784e-5c98-9eae-f0fe779cd434 | note | Supervisor - W - UCCL Supervisor or Project Engineer
d6b73909-5972-5e81-b9eb-b8e73a09e277 | note | Third Party (state) - R - Civil Inspector
| checkpoint | 13. Install 1.5mm PE liner on tank shoulder.
675e77a5-c7ee-5167-8124-d6d26f51b4b9 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
22809ed7-a345-5f34-8b7f-4a12b365dba0 | note | ○ Site plan with inspected areas
da4fca12-579c-5b1a-9852-4bafc77786c1 | note | Acceptance Criteria - PE liner installed with Bidim A64 cloth T&B
24992867-2a20-5d16-8ff6-02ec347f9964 | note | ○ PE liner installed as per installers QA-QC and Worley’s QC requirements as per Civil /Struct Design pack 310449/C1 Rev A drawing notes T3084782 on IFC drawings issued 05 May 2023
d2aab214-c63e-5ba0-804e-e1f735f9f125 | note | ○ Review installers QC documentation before placing Bidim
30b5ae1a-660b-5867-9710-181e0d4205bf | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
c259ceb5-8d40-562a-88c4-ff4caf67aedc | note | Leading Hand - N/A - Leading Hand
768fcef6-9b44-58a9-ae07-2227fc332fec | note | Supervisor - W - UCCL Supervisor or Project Engineer
090c7537-513f-5427-9f18-862b97fe5e53 | note | Third Party (state) - R - Civil Inspector
| checkpoint | 14. Install 2mm PE liner on compound floor.
cd1de204-4506-53a6-b298-f5831597b0f3 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
08e69109-a50e-501a-b4ff-b08c145c0799 | note | ○ Site plan with inspected areas
4244110d-2b9f-5bac-af86-fc800c254b38 | note | Acceptance Criteria - PE liner installed with Bidim A64 cloth T&B
9f1cdfad-3dd0-55d1-93e1-07fb2328fe2e | note | ○ PE liner installed as per installers QA-QC and Worley’s QC requirements as per Civil /Struct Design pack 310449/C1 Rev A drawing notes T3084782 on IFC drawings issued 05 May 2023
4f7ee300-3e47-5f9b-9a6c-49e4e33129fe | note | ○ Review installers QC documentation before placing Bidim
f19db4ca-24ba-592e-b7d9-05c1b4dccf1c | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
433c21cf-58dd-543b-88fa-5426e3516ba1 | note | Leading Hand - N/A - Leading Hand
6a401c5e-be93-5a32-ae40-347093351cc5 | note | Supervisor - W - UCCL Supervisor or Project Engineer
1345f35b-6216-5832-a96d-b1d1d1d8aa20 | note | Third Party (state) - R - Civil Inspector
| checkpoint | 15. Concrete pre-pour inspection Bund Walls
22fcbe87-4be9-5ddc-b3f6-e3809e96d03c | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
6f3d4dc1-e0c0-5439-a834-dca96eaae1c8 | note | ○ Site plan with inspected areas
d0c52193-4092-5be4-871b-d5a952aa2b56 | note | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
3ecd9aea-0e36-582e-8f74-46bc365eee84 | note | ○ All works in accordance with CTS General Civil Construction Specification
19906ce8-31c0-5680-a076-950f5adafd1f | note | ○ Concrete pre-pour check sheet completed and filed with ITP.
9cd4d5b5-7902-5075-9a1c-d1bce754d679 | note | ○ General Civil Construction Specification
4b9485a8-cfde-557f-a8f4-20f9ba4534b9 | note | ○ Concrete shall be high or special grade certified “ready mixed concrete” manufactured at a currently certified plant and shall comply with NZS 3104.
123f6575-7b25-5373-ac80-3a3876cf3d18 | note | ○ Delivery dockets retained.
069752a6-a299-5df1-a094-d24a334315cc | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
ea20f3e5-20d2-5e89-ae29-e399b009bb82 | note | Leading Hand - N/A - Leading Hand
ba130283-41e3-583d-8327-6a1f6f95a521 | note | Supervisor - W - UCCL Supervisor or Project Engineer
69d85993-e213-5f07-b38a-fce5ff9f4f5c | note | Third Party (state) - H - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 16. Concrete pre-pour inspection Tank Shoulder
6caea87f-5bd6-5530-a970-658f5ce33873 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
12daf234-dfb0-52ad-8fa9-571b255aa53e | note | ○ Site plan with inspected areas
9c43bd2e-5827-51dc-a9a2-1fb9cd9e1fe4 | note | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
4f7168eb-e5ec-5e4c-b54a-b5bb7b334f19 | note | ○ All works in accordance with CTS General Civil Construction Specification
7600137e-2cf5-5c09-8cfd-629f5997e25c | note | ○ Concrete pre-pour check sheet completed and filed with ITP
74bdd401-2155-54f7-a84b-26b96f1a130b | note | ○ General Civil Construction Specification
d82cbf63-1a27-5e97-934e-9f76d3bcbf40 | note | ○ Concrete shall be high or special grade certified “ready mixed concrete” manufactured at a currently certified plant and shall comply with NZS 3104.
9f46c2d2-7ab8-5ba5-96a6-b30a94a6976e | note | ○ Delivery dockets retained.
ce0d3e83-f8e4-5552-be14-4e23b05503dc | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
722a06b9-db18-5612-9097-35590502810c | note | Leading Hand - N/A - Leading Hand
247f5f92-382b-5872-8226-3714645b38fd | note | Supervisor - W - UCCL Supervisor or Project Engineer
ea103f3b-c5ea-518e-b668-e6f2ce2cce2f | note | Third Party (state) - H - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 17. Replace 50mm sand on top of HDPE liner followed by recovered in situ aggregate then 75mm AP40 aggregate.
071966b3-f684-5881-bf07-77e0d86441bd | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
b77fd412-137e-5919-b61d-148162079ebf | note | ○ CTS General Civil Construction Specification
b357f47f-3355-50c2-9cbb-a54e77efe9bc | note | ○ Site plan with inspected areas
3a70e098-74ea-526a-a8e1-65c7fdc3f647 | note | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
24be75a9-fb20-5454-b5b4-a2674da4feeb | note | ○ All works in accordance with CTS General Civil Construction Specification
bd30facf-3478-5c9d-a675-daa42837f477 | note | ○ 50mm sand/cement bedding clean and free of debris
5ae25855-cea7-5a63-a915-85eac9fc133b | note | ○ All layers placed to line and level.
a361397e-8d9a-50f6-a3c3-28e06a96c0db | note | ○ Compound floor to be graded to allow free draining to lowest point.
7a37b698-a17d-5c3e-af2c-d69235066101 | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
6323233b-1e06-5641-b318-6bbe61781b6e | note | Leading Hand - N/A - Leading Hand
268fb4ed-b4a1-5d85-9df5-d5ed9fba0bf2 | note | Supervisor - W - UCCL Supervisor or Project Engineer
1cbc3479-54a5-528b-9834-977180472445 | note | Third Party (state) - W - Civil Inspector
| checkpoint | 18. Compound Flood Test
97311d12-6df8-522e-b256-696302df12bd | note | Applicable Documents - UCCL Compound C3 Flood test methodology, HSWA COP 47 ‘Secondary Containment’
081583df-cfbe-5f6e-a06b-e28f927463b5 | note | Acceptance Criteria - Timing of the flood test will be conducted as per the approved Compound C3 Flood test methodology.
ff2565af-854d-55df-8461-97f5f242e506 | note | ○ All items on Compound Pre-Flood Check Sheet to be completed by relevant parties.
b71c0c7e-dd0e-529f-b19a-f4c453beaeae | note | ○ The infiltration test will be as detailed in HSWA COP 47 ‘Secondary Containment
136cb9ac-50be-57af-9736-488f62d769c0 | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
03ab7c9f-3337-5074-a725-d5e441abbbb0 | note | Leading Hand - N/A - Leading Hand
0a7c6a89-529c-5e2b-9187-0af231997cf8 | note | Supervisor - H - UCCL Supervisor or Project Engineer
af375e0f-0614-5938-90a1-e0975573d0e7 | note | Third Party (state) - H - Worley’s PE/ Representative
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 19. Sealing construction/expansion joints on tank annular
ee5e83bc-9cb8-585a-9fc5-2e8b14ca2f5f | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
3df9da5e-d413-57fa-ae1f-0c1a59b89916 | note | ○ Product manufactures specifications
9d3a5010-2749-511a-9257-8564512be143 | note | ○ Site plan with inspected areas
23324df0-7031-574b-8446-c0adadc1e0cc | note | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
e581c658-c04f-5226-87d0-d77f348b24e1 | note | ○ Seal manufactures specifications followed.
18d0e503-36c6-58c1-9ce9-56212d8ee296 | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
2705a87d-d87e-5f9b-8bcc-e36cabd9922f | note | Leading Hand - N/A - Leading Hand
6c1aa17c-8b7a-5862-9cc4-802df12f1ee8 | note | Supervisor - W - UCCL Supervisor or Project Engineer
d228f2d3-6c38-5fda-963b-27aabeff493c | note | Third Party (state) - R - Civil Inspector
| checkpoint | 20. Install Denso steel coat base protection or approved equivalent (Viscotaq) around tank annular
0f9060d5-1879-5307-94d9-8a50e0b98a70 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
d02fc92d-9969-56e9-827b-d36e1413e9e6 | note | ○ Product manufactures specifications
ac066236-4b26-5262-b15f-faf1966c1043 | note | ○ Site plan with inspected areas
3df47830-2039-53f0-ab62-0da657d76443 | note | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
df6420bc-64e0-5c28-af4f-b3f7aac26b77 | note | ○ Viscotaq installed in accordance with manufacturers recommendations.
2df3574d-17e1-5861-a9c6-3f62989341b0 | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
c178de6b-24ff-59ca-a78b-b259b75e7763 | note | Leading Hand - N/A - Leading Hand
4c6e60bd-d1c0-56db-8edb-c5163b56e797 | note | Supervisor - W - UCCL Supervisor or Project Engineer
2ab4dc71-9755-54dc-ba46-b212a50190c1 | note | Third Party (state) - R - Civil Inspector
| checkpoint | 21. Sealing construction/expansion joints on bund walls
fd2cf863-bfe3-5f56-8960-152497e8cbe4 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
db1646ca-5ced-5624-9894-4efe35581390 | note | ○ Product manufactures specifications
ed3953c1-e65b-5144-b49f-d92fc48e3b63 | note | ○ Site plan with inspected areas
62c2a7c7-6afb-5e74-b3bb-ae5ce6e11441 | note | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
fa860972-e0fa-5ca9-ab50-f5f61d355508 | note | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
905ba9f9-26f2-52dc-aadf-1ea063dc0f4a | note | Leading Hand - N/A - Leading Hand
0916638f-0e3b-53be-b3ed-b706a2dec890 | note | Supervisor - W - UCCL Supervisor or Project Engineer
02118835-396c-5af6-8604-3ace670395bd | note | Third Party (state) - R - Civil Inspector
| checkpoint | 22. Complete final Civil inspection and close off ITP.
8681c983-44d9-5443-81b8-28a4efd67aa6 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
6d027830-857e-516a-b673-0f08cb80094e | note | Acceptance Criteria - ITP / QC has been completed; all steps & hold points signed by relevant party.
aa90169b-f1bd-5750-b1a9-79156a6c87f4 | note | ○ All work scope completed as per design pack and any field instructions issued during construction.
0c2322ca-5228-59b8-a5d2-18881521e09a | note | ○ Job site has been left tidy.
0c22279f-bfdb-52d4-8413-6e61e052a30b | note | Leading Hand - N/A
e83b0470-84f7-5cc3-a7c8-82f76e5c244b | note | Supervisor - H - UCCL Supervisor or Project Engineer
3c00c4a7-82da-532d-8d9f-5ad7269f2fb7 | note | Third Party (state) - R/H - Worley’s project engineer
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 23. Non-Conformance reporting
7cffbe2e-2501-58d7-8e6e-bf17d50aa799 | note | Applicable Documents - UCC internal NCR and or CTS Lucidity event NCR, CTS QC Requirements for Civil Works
a56a791d-9286-56f8-a7df-16823e2f687e | note | Acceptance Criteria - In accordance with the approved Work Pack, drawing, Field Instruction and agreed scope of work.
e8c10ed4-19e2-587b-8ee5-f6efa3da80e0 | note | ○ CTS General Civil Construction Specification
0338cb5e-93c6-5caa-a057-be5859d6d8c0 | note | ○ CTS QC Requirements for Civil Works
302dfb40-dd90-56be-b34a-ccf113155384 | note | Leading Hand - N/A
ce555493-9cf4-55a3-8dcd-93d00978683e | note | Supervisor - H - UCCL Supervisor or Project Engineer
4c10e202-d73d-522d-a04d-a4d841610c73 | note | Third Party (state) - H - Civil Inspector / Worley QC Coordinator
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 24. “As- Built” Information/Drawing
cd51be93-1a47-50ae-849c-86cc1c99efad | note | Applicable Documents - Section 9 CTS QC Requirements for Civil Works
05bf8409-9cc8-5985-a104-18003ea1e47e | note | Acceptance Criteria - CTS General Civil Construction Specification
6b8e2ea0-da5f-5139-9df5-00bade30ae31 | note | ○ CTS QC Requirements for Civil Works
057c709b-73b5-5be0-95bf-63f729e551b4 | note | Leading Hand - N/A
db219f51-67e6-5b91-ad49-1d7a6c18c149 | note | Supervisor - H - UCCL Supervisor or Project Engineer
bea566d8-f526-5470-ae85-c72eebc230f8 | note | Third Party (state) - R - Worley Project engineer
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 25. Reference info, specifications etc
13a4c8e2-a91e-51cf-a613-a49fe45faa75 | note | Applicable Documents - Relevant sections of Controlled doc’s, Material specs (Epcon, coatings etc)
| checkpoint | 26. Punch listing
24f53638-8087-5c2d-ac4a-fd1e5a52a006 | note | Applicable Documents - Section 10 CTS QC Requirements for Civil Works
fbd665be-96c7-5710-9448-927a4ecda97d | note | Acceptance Criteria - CTS QC Requirements for Civil Works
8070dc64-8646-54ee-92b6-7c4b6d9c3c48 | note | Leading Hand - N/A
4a4939ee-dc9b-55d9-9701-6e22400aaf0e | note | Supervisor - H - UCCL Supervisor or Project Engineer
98cb0434-d170-54ba-bf78-85c7d1aba80c | note | Third Party (state) - R - Worley Project engineer
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 27. Compilation of inspection and test record
84876f64-e269-5f0f-a495-32a3c2a4e1fc | note | Applicable Documents - Signed off ITP & work pack, Section 7 and 8 UCC Producer Compliance Statement. These documents will be compiled to form a complete MDR/QC Pack.
72d4569a-df28-5c24-907c-57a0d072906b | note | Acceptance Criteria - CTS General Civil Construction Specification
55141bd6-ce20-5a73-be48-bd0f5f088251 | note | ○ CTS QC Requirements for Civil Works
1c5022d2-7a8f-5e95-b7c9-3633ca1a5b8f | note | Leading Hand - N/A
5c513771-7295-58eb-9f55-2aa0bd7ba87a | note | Supervisor - H - UCCL Supervisor or Project Engineer
2d3877e2-2792-5854-b13b-91a88b13f083 | note | Third Party (state) - R/H - Worley Project engineer / QC Coordinator
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - Tank Annular Stud Welding |  | Tank Annular Stud Welding | 91892665-c6c6-456d-a656-cf950a0ff9bb
| checkpoint | 1. Issued For Construction Drawings
d87005c1-6a01-508b-b358-4d85fbff0441 | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
50eb5d34-48c9-542c-96c3-78078c192c9e | note | Acceptance Criteria - IFC drawings issued. Clear scope of work.
db87ec1f-4928-5c8b-ae5c-c5c90c84c34b | note | Leading Hand - N/A
b986fc4f-cb28-5f68-9289-f193e3ff93d2 | note | Supervisor - N/A
a527e052-e89c-5089-a1fb-ef0a4d5fc8eb | note | Third Party (state) - P - Worley’s project engineer
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2. Procurement of studs
2a1ba273-b95d-5ca6-bd87-fa05db6061ad | note | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
2a2a0b70-3891-5b86-b0e8-83fe01b14da0 | note | Acceptance Criteria - IFC drawings issued. Clear scope of work. Studs procured as per drawing pack
c788b915-25a2-5092-842b-42606d28c0c1 | note | Leading Hand - N/A
f7f6870e-f73d-57d6-8e08-060f20c2cf11 | note | Supervisor - H - UCCL Supervisor or Project Engineer
05fc3c8f-ce3b-5ba6-b976-e23cf443af6d | note | Third Party (state) - R - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3. Surface preparation by abrasive blasting on tank 04 annular downturn plate for stud welding
0324a556-df1e-5543-bc78-c8187e1c225b | note | Applicable Documents - INVIL methodology to weld studs AWS D1.1
8661df92-e8a5-5024-bdc4-5f2ff63dd595 | note | Acceptance Criteria - The areas to which the studs are to be welded shall be free of scale, rust, moisture, paint, or other injurious material to the extent necessary to obtain satisfactory welds and prevent objectionable fumes.
b835b356-7c24-5b6c-aee0-43ae681833d8 | note | Leading Hand - N/A
b0aee7bc-7a56-5953-b064-0a3e258b8d54 | note | Supervisor - W - UCCL Supervisor or Project Engineer
5e4eeb01-cd7b-51c4-82bc-307d7dd44327 | note | Third Party (state) - R - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4. Surface preparation by abrasive blasting on tank 06 annular downturn plate for stud welding
6a273c32-d38b-533d-bcf5-2da2b2f1e3ad | note | Applicable Documents - INVIL methodology to weld studs AWS D1.1
fd3d54dc-a52d-5436-afa5-c335782a605b | note | Acceptance Criteria - The areas to which the studs are to be welded shall be free of scale, rust, moisture, paint, or other injurious material to the extent necessary to obtain satisfactory welds and prevent objectionable fumes.
82909699-4309-5f49-8604-f01252a0ecb4 | note | Leading Hand - N/A
8998d2a6-f9eb-5e35-90d3-5e9b74ddd991 | note | Supervisor - W - UCCL Supervisor or Project Engineer
a3b0014e-4fd9-50a8-a1d4-5425221fc62a | note | Third Party (state) - R - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 5. Trial of stud welding at Channel Workshop and weld visual Inspection
6c961c2a-835b-5204-b8d8-3c71a34d7ede | note | Applicable Documents - INVIL methodology to weld studs AWS D1.1
597497a3-8abe-58d5-907a-9a7239db1208 | note | Acceptance Criteria - Studs shall exhibit full 360° flash with no evidence of undercut into the stud base
0016e36f-348f-5225-b0c0-11a336174037 | note | Third Party (state) - H - Welding Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 6. Bent Test on 1st two studs by each welder. In addition to visual examination, the test shall consist of bending the studs after they are allowed to cool down, to an angle of approximately 30° from either striking the studs with a hammer on the unwelded end or placing a pipe or other suitable device over the stud and manually or mechanically bending the stud
d1986c1f-8975-548d-8983-90f38f4662cf | note | Applicable Documents - AWS D1.1
4b9e6ff4-3bd7-56ac-b834-d33359655759 | note | Acceptance Criteria - If on visual examination the test studs do not exhibit 360° flash, or if on testing, failure occurs in the weld zone of either stud, the procedure shall be corrected, and two more studs shall be welded to a separate material or on production member
31e0aa60-b4ce-544b-843f-7f70b72a1d53 | note | Third Party (state) - H - Welding Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 7. Studs Welded to Tank 04 Annular downturn plate
167b111b-3d68-5ef2-bab0-0a03126c0f4f | note | Applicable Documents - Stud manufacturer’s instructions that accompany studs
877c4b6c-1cea-525d-ba65-5c0d53fbcbe0 | note | Acceptance Criteria - Welded as per stud manufacturer’s instructions accompanying studs
26e202eb-3a51-564d-b9ae-1c4242a58d27 | note | Leading Hand - N/A - Leading Hand
d405cdf6-cb8b-5bf4-89b5-4c92ac174ad5 | note | Supervisor - W - UCCL Supervisor or Project Engineer
64fb57d7-c602-56a0-9a8a-434c31057171 | note | Third Party (state) - W - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 8. Studs Welded to Tank 06 Annular downturn plate
21058004-8762-5d11-ab5f-5e3affb27f46 | note | Applicable Documents - Stud manufacturer’s instructions that accompany studs
e4d5717c-c4c4-527f-bab6-6e3b126cf3dd | note | Acceptance Criteria - Welded as per stud manufacturer’s instructions accompanying studs
9adffd3d-6f14-57c9-aec9-11942e152b82 | note | Leading Hand - N/A - Leading Hand
925a9f00-49be-591f-9a3b-87b5587e6569 | note | Supervisor - W - UCCL Supervisor or Project Engineer
8cdec3bc-981c-5b18-ad05-b50acd4b1153 | note | Third Party (state) - W - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 9. Signoff by Channel Welding Inspector
042b9944-818a-595f-8550-bcbd207cb6d6 | note | Applicable Documents - CTS Weld visual report
a238de60-104e-526d-a157-cb43231b4c74 | note | Acceptance Criteria - Welding Inspector inspects welds and is happy that welding has happened in accordance with process developed in workshop methodology
5755d41b-16f6-5e4f-8fea-8e30809c27d3 | note | Third Party (state) - H - Welding Inspector
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP T04 T06 Tank Upgrade T039/C1 - Underground Line Grout Filling |  | Underground Line Grout Filling | 4e78905d-5dd0-4969-a2b1-02d0b4549d94
| checkpoint | 1. Issued For Construction Drawings & Specification
b2e44926-07b0-58e1-89f2-006d52f95da3 | note | Applicable Documents - General Civil Construction Specification EW-020-203 Construction Drawings
efaef4be-030e-5a61-8077-663324f5d223 | note | Acceptance Criteria - Clear scope of work, Grout capacity calculation
102ca54c-c0e8-5045-bade-ae7ee1798105 | note | Leading Hand - N/A
b814a864-6c51-59a3-ace2-8cad836a6f05 | note | Supervisor - W - UCCL Supervisor or Project Engineer
3e0eaf3f-51a6-5c22-8d8e-92b00998a00f | note | Third Party (state) - R - Civil Inspector
| checkpoint | 2. Flushing of redundant underground pipe line with water
595ebecd-1993-53f7-afa2-5e71b41e308a | note | Applicable Documents - General Civil Construction Specification EW-020-203
a4a2e9d3-42db-5906-b67c-9ce128d4a332 | note | Acceptance Criteria - Redundant underground pipes cleaned out and free of obstruction
59d58ebe-4527-57b8-80c7-6e925304cb3e | note | Leading Hand - P - Leading Hand
2dd3e5fb-b999-51d3-99af-635586ab5488 | note | Supervisor - H - UCCL Supervisor or Project Engineer
2821afba-1544-5f2d-896b-839363dff9c7 | note | Third Party (state) - H - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3. Install filling fittings and breather pipe and or conduit at highest end. Grout fill redundant underground pipeline
829a9290-f984-521e-9ad6-f1593984e632 | note | Applicable Documents - General Civil Construction Specification EW-020-203 Atlas Concrete Grout Specification
4c86c7ec-b6c8-570b-985e-362a8e5747cc | note | Acceptance Criteria - Filling fittings shall be pressure rated ≥ max. pump pressure. Grout to be minimum 17.5MPa. Concrete Delivery Dockets, Pipework pre-washed with water, Grout filling witnessed by CTS
b0fe4c33-9040-56ac-a34a-8c1d99fac84f | note | Leading Hand - P - Leading Hand
526c317f-a72f-5af4-bbe4-7c01a70ab5b9 | note | Supervisor - H - UCCL Supervisor or Project Engineer
95983f92-f674-599a-b420-cb742d7ec0b6 | note | Third Party (state) - H - Civil Inspector
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4. Record / As-built drawing
31369de4-b396-581e-b017-74c06028634f | note | Applicable Documents - General Civil Construction Specification EW-020-203 Atlas Concrete Grout Specification
d19633cb-3030-5429-8b43-2aece42218f7 | note | Acceptance Criteria - Grouted redundant pipes shall be recorded on as-built drawing and given to CTS drawing Office with a drawing office request (DOR) for the site drawing to be updated
ab6d21db-dbd7-57a8-a389-360ca351070d | note | Leading Hand - N/A
23d932f3-14bf-55b4-8a64-5732e9cc4f47 | note | Supervisor - P - UCCL Supervisor or Project Engineer
484d6d19-8595-5e6d-9471-9f3dcd2338c9 | note | Third Party (state) - H - Worley CE/PE
| signoff | AUTHORITY HOLDPOINT
| checklist | Lot Signoff |  | Lot Signoff | 10596494-0490-4674-aaf3-bbdc9053e9e5
| checkpoint | Lot Information complete
93e726b9-d478-5167-accc-3e0fb1f87d6d | date | Date
e7c3eb0d-43ce-5dae-80e4-0b5342589508 | textbox | Lot Type
c43abea1-a8aa-5220-bff9-41ee7d8e707f | textbox | Start Chainage
5c23eae7-76ac-5da1-a69f-7669c32bf51d | textbox | End Chainage
| signoff | AUTHORITY HOLDPOINT
| checklist | Photos |  | Photos | c556f1cf-13aa-4718-a838-a31d9944a2fb
| checkpoint-no-value | Add photos/files here
3ce42dcb-bb35-50e3-b3b8-0a55fb55dac4 | textbox | Lot/Area
| checklist | TEST - ITP 001 - Subgrade Preparation |  | ITP 001 - Subgrade Preparation | 5363ab8d-811c-488c-8dff-ccd9af08f74e
| section | Lot Information
| checkpoint | Lot Information complete
05120bb5-d4bf-521d-807f-7023d43b58e2 | date | Lot Opened On
21481dbe-2f3f-5d85-9d29-39f1574069a3 | date | Date of Works
00473c34-2933-561c-8314-d8797418a2ad | textbox | Lot Type
2b6ca99e-2ec3-5dd6-b5ae-fe7d13de0b07 | textbox | Start Chainage
50a2a081-d1b9-5935-b1c9-ed6dcc22d6ba | textbox | End Chainage
| section | Procurement
| checkpoint | Physically located all utility locations
0daff645-d77f-5e5f-8ae5-f411aed6172a | note | Detail of Activity - Permit to work around services (Gas, Power, Fibre, etc.)
790dc180-5645-5084-a8c4-a22bf2c89834 | note | Minimum Test Frequency - as required per section of works
2c5f1451-8f23-59a0-9c63-785caedc4715 | note | Inspection/Test Method - Document Review
8ff9b370-8869-5522-9ab8-3c28a604406b | note | Acceptance Criteria - All services physically located
1e6d17e5-46ae-5c6d-a840-465ef7281693 | note | Verifying Documentation - Permit attached or permit number noted
3d409afa-978a-5c67-9287-77e2e9480ef6 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 100.2 - Contract Document Signed
d0298961-4e45-5241-ab49-845e45af843c | note | Detail of Activity - Ensure Contract is signed
9559d1b5-6aac-5990-8287-e5b27f6f45b5 | note | Minimum Test Frequency - at the Contract kickoff meeting
947d960e-9ddc-53d9-8fee-4ce45ecbdcc7 | note | Inspection/Test Method - Document Issue
537f443b-dd10-5eeb-b374-11aeef8be586 | note | Acceptance Criteria - N/A
4d7fd03c-5476-538b-be98-52a9bb8ab4b2 | note | Verifying Documentation - Issued with a NTC
a27f370a-4985-5a59-bdcd-c60f8213b18b | note | Responsibility - Downer / BBO's Rep.
| checkpoint | 100.3 - For Construction Drawings Issued
d22e0be1-6309-519e-bcc9-9bbb230b4401 | note | Detail of Activity - Ensure "For Construction" drawings are issued
b650208e-5868-5afa-816c-c8913530ce35 | note | Ensure Contract is signed
8c18305e-4208-5e18-95be-819718766c8b | note | Minimum Test Frequency - at the Contract kickoff meeting
321dab2c-f953-556d-b8d2-3a0b4305fede | note | Inspection/Test Method - Document Issue
8a14e99c-6410-5c82-b1a8-d19727f66166 | note | Acceptance Criteria - N/A
25298f71-bd79-55f9-8a30-c433517fd933 | note | Verifying Documentation - Issued with a NTC
e9f3a47b-a013-5984-8433-46ae84d2f9fc | note | Responsibility - Downer/BBO's Rep.
| signoff | AUTHORITY HOLDPOINT
| section | Construction
| checkpoint | 100.4 - Traffic Management Plan
210e46cb-cdfa-5f93-be1c-1e2fd143393f | note | Detail of Activity - Ensure TMP is approved and check that the requirements are fully understood by the STMS
4ce22e44-7555-5522-9cb1-ff1d40e40dc7 | note | Minimum Test Frequency - every morning and/or when the TMP changes
3e84efe5-c91c-5a52-ba4b-2c23c1e4f1e3 | note | Inspection/Test Method - Document and Physical works review
33ce09a2-c19e-5bc5-819c-ad56b7e1bc25 | note | Acceptance Criteria - COPTTM
278143c5-eb28-5532-ab2e-718d946d706e | note | Verifying Documentation - TMP from contractor
df50b5c4-5f65-5d56-8486-dbce00fe3e3b | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 100.5 - Design
0617a8d1-51f1-5796-a611-435081b2b57f | note | Detail of Activity - Ensure that Design is approved and Drawings are the latest version
eb9005d0-be3a-518b-a6e2-03ca080e4ff9 | note | Minimum Test Frequency - Prior to commencement
f3e53d47-b28b-5b3e-ae75-ded800153bbe | note | Inspection/Test Method - TNZ M/20; TNZ M/7; TNZ M/24
8f366595-4886-52f0-b53f-df93c6afac5a | note | Acceptance Criteria - Is a copy of approved consent(s) available on site
faf13066-3a58-524b-a8c5-43f92c1b9700 | note | Verifying Documentation - Check Drawing register
166a8de3-7214-54a2-86a9-f7a3ddf4eb7e | note | Responsibility - Contractor
| checkpoint | 100.6 - Approved Consents
2f603023-5ab2-5723-82cb-f9bf7a6687af | note | Detail of Activity - Is a copy of approved consent(s) available on site
ae372bcc-bb1f-5c46-94ed-0a233d343311 | note | Minimum Test Frequency - Prior to commencement
24364bae-3324-5d55-813e-b06b4b650b25 | note | Prior to commencement
ba7759a3-89e5-5112-91e0-877a6cd46a76 | note | Inspection/Test Method - Visual Inspection
cefa0a2d-6b52-5271-ad8c-756fb1afcddd | note | Acceptance Criteria -
8b075374-2d38-59d9-a074-c116e019d5b7 | note | Verifying Documentation - This ITP
7cc1053a-3069-5fec-8843-04dd2e2ab24c | note | Responsibility - BBO's Rep.
| checkpoint | 100.7 - Pre-start meeting
e6ec85c6-7b20-59f9-bdea-e479f3f5e675 | note | Detail of Activity - Pre-start meeting to confirm work strategy and safety measures
e40ab7bd-33a7-5bc9-93e1-18954150789b | note | Minimum Test Frequency - Before commencing work each day
c0b8cf65-dcdd-55e7-9d15-c4caea5a2197 | note | Inspection/Test Method - N/A
9641704d-dffb-54ce-92a8-575b25013732 | note | Acceptance Criteria - 100% attendance
3bc84022-89c8-5b7e-bc59-81b437b0460d | note | Verifying Documentation - Pre-start sign on register / site diary
e92f511e-ba3c-5f9b-a00b-56bc06545e63 | note | Responsibility - BBO
| checkpoint | 100.8 - Contractor's methodology
019ade75-5865-55d2-afa3-3d3013593698 | note | Detail of Activity - Site inspection
06eef761-6df4-5ad8-9c39-df1f74f824f7 | note | Minimum Test Frequency - Prior to commencement
3ce1571e-81ab-5587-b623-50775ec16861 | note | Inspection/Test Method - Document review
f19428ef-6587-53f1-ab6e-16bddd43d482 | note | Acceptance Criteria - Methodology conforms with all relevant specifications
2260e019-8ae1-51aa-9f6b-0bde354b35a3 | note | Verifying Documentation - Methodology submitted via NTE
19c5002e-9438-5229-a19d-cbc4ba50d9bb | note | Responsibility - BBO's Rep.
| section | Post Work
| checkpoint | 100.9 - Laydown area / stockpile sites
cfcb6ca8-deab-5f6d-a9e5-7f004ea4a9cc | note | Detail of Activity - Site inspection
dad93464-1605-5ea6-9a76-ca3e6ed70d37 | note | Minimum Test Frequency - Prior to commencement
0775bd7b-7ee7-5cb3-ae03-6ff9002c241b | note | Inspection/Test Method - Visual Inspection
0ac9edfb-0cfd-54d3-bec1-44430bc11d01 | note | Acceptance Criteria - Approved by NZTA
7455835d-ee0a-5c1c-94e6-1e5ce2ba5114 | note | Verifying Documentation - Request for approval (RFA) via NTE
2d9a3402-767f-5a21-af6c-1e1e4583fdad | note | Responsibility - BBO's Rep.
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 101.1 - Weather
052808d9-18b7-58a7-ab9a-eb6137fd0c06 | note | Detail of Activity - Assessment of forecast
9ca2e115-efaa-5280-9d60-0a60c8c3eb6c | note | Minimum Test Frequency - Daily prior to and during works
9b0657ee-b009-5bb0-a572-be0a7b760002 | note | Inspection/Test Method - Check local and national weather forcast services
c7af84f2-c3b5-5d35-be93-977004935b67 | note | Acceptance Criteria - No imminent rain or adverse weather conditions. Consideration of wind and project location/environment
1b15eed5-445a-5a67-8dab-4d5972011f82 | note | Verifying Documentation - Contractor's site diary
2b74f64c-d587-5e4b-a956-581b76f9c1dd | note | Responsibility - Contractor
| checkpoint | 101.2 - Environmental Protection
d1ff1df5-6bf7-5556-a880-eb4748cda0f3 | note | Detail of Activity - Site evaluation
475446ea-ba66-5a4e-8ef0-03b15a5631ea | note | Minimum Test Frequency - Prior to commencement
f31cf18d-1e93-56c1-b93f-c88909627801 | note | Inspection/Test Method - Inspection
c89cd882-712a-51a6-acd9-f9bd2420e281 | note | Acceptance Criteria - Supervisor assessment of conformance
e202d083-2f84-5050-a59c-4795f620bc5d | note | Verifying Documentation - Contractor's site diary
f630990b-8c36-5ea0-87ab-7e5c4e8a0e6e | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 101.3 - Precondition Survey
3aa69012-5ec8-53fa-9a2d-084df0778df7 | note | Detail of Activity - Examine extent of the site
b7025122-0e1a-58f8-bb31-f7124823168e | note | Minimum Test Frequency - Prior to commencement
f8e08d1a-7614-56e6-bff0-261e6d3141be | note | Inspection/Test Method - Inspection
6ef3e200-1e73-50d9-bc27-a71f0d11fced | note | Acceptance Criteria - Supervisor assessment of conformance
a0341198-cd71-541b-b8b7-830e52fd1350 | note | Verifying Documentation - Contractor's site diary
5064aab6-5d22-5e1f-a5a2-3155534f8a64 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| section | Lot Verification
| checkpoint | Lot Verification complete
cc89755a-4626-5f8b-9668-e9840365e4e5 | textbox | Lot Verified By:
9b1ea8cc-996a-5048-96a5-3958ae96409d | dropdown | Lot Status | Outstanding, Closed
daeefbd4-5d50-5673-9c97-3378ed8def62 | date | Lot Closed Date:
73842cfa-a2b6-5922-ac94-a25562fd3a97 | button | Submitted to Client | Yes, No, N/A
1fed631f-22b4-5631-ac5b-ac8ab893122e | textbox | Reviewed by Client
0d5d2de0-d06b-5ec0-91eb-399ed842b441 | textbox | Submission Comments:
| checklist | TEST - ITP 002 - Capping Layer |  | ITP 002 - Capping Layer | 0baf8a97-f864-420f-bebc-3bf9ba4a7c93
| section | Lot Information
| checkpoint | Lot Information complete
ebcbaaac-056a-5129-b26f-c8e1c47c3a54 | date | Lot Opened On
1a5126b0-9a30-52ab-a62e-f5220f33c9ee | date | Date of Works
37a3eaac-9459-5094-8545-253d6e8f119c | textbox | Lot Type
9e704441-9ffa-5882-879a-ed7e3f5375e7 | textbox | Start Chainage
72893085-2488-5449-bc3e-85674cd171ff | textbox | End Chainage
| section | Procurement
| checkpoint | Physically located all utility locations
6864abb3-9df0-5f84-8fff-277f3573ae2d | note | Detail of Activity - Permit to work around services (Gas, Power, Fibre, etc.)
f96506b3-ab10-5739-8b82-60e3a5cfe483 | note | Minimum Test Frequency - as required per section of works
1a576b75-5b06-5fae-a49b-24a50f59771a | note | Inspection/Test Method - Document Review
b26bedb5-e360-5ff5-9f54-62b28affd2bd | note | Acceptance Criteria - All services physically located
6ecad2c3-8e2d-57e6-ba43-91aca82b5348 | note | Verifying Documentation - Permit attached or permit number noted
22518f1d-32ca-5f0e-bca8-1e94ae566e69 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 100.2 - Contract Document Signed
8ef9deaa-91b6-5e50-8883-431ce7f92f3e | note | Detail of Activity - Ensure Contract is signed
80ecb48a-6c96-5999-a7a7-cf44036bc0cb | note | Minimum Test Frequency - at the Contract kickoff meeting
edcb6a82-54a5-5d6f-99ac-be6fdaa7a369 | note | Inspection/Test Method - Document Issue
78798a09-7b46-5c50-8e77-b1baba650ec7 | note | Acceptance Criteria - N/A
c24d467a-57f9-50f4-99ca-4a0d854fbe3c | note | Verifying Documentation - Issued with a NTC
c4d58cd1-177a-5371-acc5-89c9c9eba13b | note | Responsibility - Downer / BBO's Rep.
| checkpoint | 100.3 - For Construction Drawings Issued
a3831201-4855-5d4e-b568-cb7e7aa6fa62 | note | Detail of Activity - Ensure "For Construction" drawings are issued
8f6be392-4d68-5533-b98b-68105e180846 | note | Ensure Contract is signed
b16016d8-e64c-5a0c-a208-5b6407a1b383 | note | Minimum Test Frequency - at the Contract kickoff meeting
76cdc54e-877b-5f86-8b51-7a4f2f618169 | note | Inspection/Test Method - Document Issue
eb8ac336-7c40-57b6-8169-ee0e29dfdc51 | note | Acceptance Criteria - N/A
0724fb78-69bb-5215-ae26-224920b18fcf | note | Verifying Documentation - Issued with a NTC
c98573c5-9bb5-5d61-9c36-2bf747c23b97 | note | Responsibility - Downer/BBO's Rep.
| signoff | AUTHORITY HOLDPOINT
| section | Construction
| checkpoint | 100.4 - Traffic Management Plan
84b0c8f4-09da-559f-a544-6d9aa677edd1 | note | Detail of Activity - Ensure TMP is approved and check that the requirements are fully understood by the STMS
a58b12ca-93f8-5fca-830f-475cc8ea50de | note | Minimum Test Frequency - every morning and/or when the TMP changes
bfbfa7ea-e5f1-5846-a5b9-d3439f8e2da9 | note | Inspection/Test Method - Document and Physical works review
0d3ab922-999b-53b6-96b1-2293de6a2a95 | note | Acceptance Criteria - COPTTM
e84146f6-e813-5590-8158-42646c90d8ce | note | Verifying Documentation - TMP from contractor
60121b19-a2b9-5fc7-b1c5-4b28b0be31b0 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 100.5 - Design
4805c05e-058d-5ec2-9f65-71dff8a5d3e3 | note | Detail of Activity - Ensure that Design is approved and Drawings are the latest version
9c647a57-f512-52da-b051-59acd87a1ebb | note | Minimum Test Frequency - Prior to commencement
2927b4ed-7b1e-51db-88f5-17b1f7c4a928 | note | Inspection/Test Method - TNZ M/20; TNZ M/7; TNZ M/24
a168b25f-e3de-5f8c-a2f6-c629e2d02471 | note | Acceptance Criteria - Is a copy of approved consent(s) available on site
f957a63d-d785-53dd-967e-7e73543455f3 | note | Verifying Documentation - Check Drawing register
1d1b10e9-bb37-52e5-a6cd-1ea9a11b05a4 | note | Responsibility - Contractor
| checkpoint | 100.6 - Approved Consents
c1cca32e-ab0d-5fa6-9203-92235ba039e9 | note | Detail of Activity - Is a copy of approved consent(s) available on site
4c6fbe48-6447-5455-92d0-bcbabe8787d0 | note | Minimum Test Frequency - Prior to commencement
8094a0f5-8173-5f5e-912a-d1eb6c1eb6ba | note | Prior to commencement
5ed48067-2ad2-57db-9c31-8da04baefe46 | note | Inspection/Test Method - Visual Inspection
9525406d-0172-599a-9c1e-dcdc9600354f | note | Acceptance Criteria -
47f3b81a-8379-566a-8f8e-59b9be60ac82 | note | Verifying Documentation - This ITP
ac17e8f2-8c41-5c5f-85cf-b7ccef556caa | note | Responsibility - BBO's Rep.
| checkpoint | 100.7 - Pre-start meeting
ace4ff17-0643-5535-80ac-cd324f7c19d1 | note | Detail of Activity - Pre-start meeting to confirm work strategy and safety measures
b612c74c-7450-54bb-a169-959fb3615c1d | note | Minimum Test Frequency - Before commencing work each day
0b4eea31-d4de-5b54-ae3e-2c0a28083e97 | note | Inspection/Test Method - N/A
a58cc459-f633-563c-b23b-3ec6230a5cbf | note | Acceptance Criteria - 100% attendance
8c8c30d2-f3ea-5786-8655-bb0a1e758511 | note | Verifying Documentation - Pre-start sign on register / site diary
ecc389b8-2a78-52b0-b92c-1f4d1bdc4208 | note | Responsibility - BBO
| checkpoint | 100.8 - Contractor's methodology
9f91cb1e-a77d-585d-863c-bdbce0f15bd5 | note | Detail of Activity - Site inspection
f5cc98ba-cd74-5a48-b917-28516ff35db6 | note | Minimum Test Frequency - Prior to commencement
a7278459-d6a7-57fa-bd65-c21b51001134 | note | Inspection/Test Method - Document review
3c0d404a-cea6-54ef-aa10-7d835c404372 | note | Acceptance Criteria - Methodology conforms with all relevant specifications
f7a78c1c-ed9d-5f0a-b15f-7cb4405a8d6a | note | Verifying Documentation - Methodology submitted via NTE
fa47d607-4c76-5ed3-9841-0cf83472637d | note | Responsibility - BBO's Rep.
| section | Post Work
| checkpoint | 100.9 - Laydown area / stockpile sites
13bf4188-5a93-5ef5-bcd4-73f66b3b42a3 | note | Detail of Activity - Site inspection
e4dfa1d4-312f-5535-a482-d3b6277b1571 | note | Minimum Test Frequency - Prior to commencement
3e668999-5d00-5f71-aab1-a8a4225fcf2f | note | Inspection/Test Method - Visual Inspection
354347c7-33eb-51b6-9743-2fb66c5e1b44 | note | Acceptance Criteria - Approved by NZTA
5edf3e24-5235-5c79-b967-2e902d927062 | note | Verifying Documentation - Request for approval (RFA) via NTE
1d68918e-3c4f-599f-9439-3ac7b627e746 | note | Responsibility - BBO's Rep.
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 101.1 - Weather
be400cd3-252d-553f-9eaf-7c6fd44a73b1 | note | Detail of Activity - Assessment of forecast
dcc211c8-2dc1-5f0f-8dbe-2b3792e233fe | note | Minimum Test Frequency - Daily prior to and during works
79bb2a07-313f-5dae-971e-d98f18b0a506 | note | Inspection/Test Method - Check local and national weather forcast services
10731880-499f-51c2-9700-72dbdf2350b4 | note | Acceptance Criteria - No imminent rain or adverse weather conditions. Consideration of wind and project location/environment
040da5ef-033c-5850-9f86-1d11d6dc9d4d | note | Verifying Documentation - Contractor's site diary
c1a4688a-3e0c-52ed-85fa-ba5bfe3780bb | note | Responsibility - Contractor
| checkpoint | 101.2 - Environmental Protection
6373a627-af35-5fa0-9d92-9d170241e5ce | note | Detail of Activity - Site evaluation
3d87c19b-7294-5177-b6d9-d5091c1d2d6a | note | Minimum Test Frequency - Prior to commencement
68aa1a74-7384-5c9c-bf47-3f2840f6c2fa | note | Inspection/Test Method - Inspection
1622f9d5-52f3-5d48-98f7-6da1f4d606b3 | note | Acceptance Criteria - Supervisor assessment of conformance
c8ee7dca-8060-502b-9c85-eb4fdbbdf818 | note | Verifying Documentation - Contractor's site diary
b7d2586e-4e75-5364-9e6e-faad24205065 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 101.3 - Precondition Survey
d7a05c90-7831-56de-98ff-fa073d87d141 | note | Detail of Activity - Examine extent of the site
215530e9-f1ea-560a-8834-f33dbd8f3d00 | note | Minimum Test Frequency - Prior to commencement
f4447c99-baf8-59bd-b861-3089814e614f | note | Inspection/Test Method - Inspection
38325e46-d99a-5556-9f82-66cdb48a953b | note | Acceptance Criteria - Supervisor assessment of conformance
34cb80b0-b912-5bea-a08e-1f20160184ed | note | Verifying Documentation - Contractor's site diary
23ba5dc9-55bc-54ea-b589-49f9d46bcd75 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| section | Lot Verification
| checkpoint | Lot Verification complete
af075329-0c12-5eb8-83e3-d4944ea37ff6 | textbox | Lot Verified By:
9d80efe1-5e0a-5b6b-8ee1-7dae584e450c | dropdown | Lot Status | Outstanding, Closed
a27fcb93-b1b7-5626-a291-362efe471529 | date | Lot Closed Date:
18eb12e7-f2b6-57b1-b18c-f59a11b9ea78 | button | Submitted to Client | Yes, No, N/A
40624a80-929c-50fa-9c09-197e1899d8b3 | textbox | Reviewed by Client
fc062a2d-e346-518f-9f86-b2e3b8027a7a | textbox | Submission Comments:
| checklist | TEST - ITP 003 - Subbase Layer |  | ITP 003 - Subbase Layer | 30a2d497-448a-4aee-b7df-6ce4ad1aa4ce
| section | Lot Information
| checkpoint | Lot Information complete
408e2de0-d76a-5654-9009-99565a9ada02 | date | Lot Opened On
666660ee-17f3-546e-bdb2-d7cc7f22d333 | date | Date of Works
046f2834-7640-566a-bb5c-2c03d69be0f5 | textbox | Lot Type
786e34a6-943e-5260-aa51-b48ac9607f02 | textbox | Start Chainage
77c58c4a-3292-5b9b-8649-d8d6826ffd7e | textbox | End Chainage
| section | Procurement
| checkpoint | Physically located all utility locations
a8ae8054-4f60-56f4-97a4-88c4ef6b36e5 | note | Detail of Activity - Permit to work around services (Gas, Power, Fibre, etc.)
5eeba223-7907-5cde-b793-a1c47898ec32 | note | Minimum Test Frequency - as required per section of works
5585a794-9266-54d6-b142-d0211e28eae5 | note | Inspection/Test Method - Document Review
a429cc36-1b2d-5ef7-99b0-d8d21447b9e5 | note | Acceptance Criteria - All services physically located
346977ff-d8d8-59d5-8302-8afabeb7ba62 | note | Verifying Documentation - Permit attached or permit number noted
b3000fb5-331e-5422-9672-454c40880074 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 100.2 - Contract Document Signed
88b65d94-da50-5c73-b711-3f4343c497cc | note | Detail of Activity - Ensure Contract is signed
ef266196-1b31-5a8b-b9c1-5df424264a4e | note | Minimum Test Frequency - at the Contract kickoff meeting
de1a60ee-a4c0-54de-9228-39a1b58bbb00 | note | Inspection/Test Method - Document Issue
1ed99eee-83e2-570d-87ec-f4a06fe2913f | note | Acceptance Criteria - N/A
43c37d3c-ffa6-5501-baf7-16e975943fd8 | note | Verifying Documentation - Issued with a NTC
0bd32e80-a110-5aa1-8441-f6daa545802b | note | Responsibility - Downer / BBO's Rep.
| checkpoint | 100.3 - For Construction Drawings Issued
a727d340-b25c-58bb-8973-a63e492e8da6 | note | Detail of Activity - Ensure "For Construction" drawings are issued
b7b3626c-dbd8-56e6-8647-5ed678084e2d | note | Ensure Contract is signed
3dc8e932-25a4-5a5f-96ac-1a15d592e776 | note | Minimum Test Frequency - at the Contract kickoff meeting
19dbad00-7d5a-5ad2-9bba-68a7a9266896 | note | Inspection/Test Method - Document Issue
68560b8d-7d7a-5937-a5c8-330c4e30d22b | note | Acceptance Criteria - N/A
4e68f7fe-2757-5533-ba4a-d1a0dcb1e06e | note | Verifying Documentation - Issued with a NTC
35162dc3-5e24-59dd-b385-b84e31f6fb4c | note | Responsibility - Downer/BBO's Rep.
| signoff | AUTHORITY HOLDPOINT
| section | Construction
| checkpoint | 100.4 - Traffic Management Plan
c5272bf1-7036-5552-b848-b0d14c03a1f7 | note | Detail of Activity - Ensure TMP is approved and check that the requirements are fully understood by the STMS
18437fe7-411c-52ae-a2b0-6dd0171fc278 | note | Minimum Test Frequency - every morning and/or when the TMP changes
a57353df-4e77-5d79-b87b-6cef5efe27c9 | note | Inspection/Test Method - Document and Physical works review
8113a43d-2289-5cb6-9d36-78d5ef5582b7 | note | Acceptance Criteria - COPTTM
08a80483-6820-56fe-93e7-58fbfd956000 | note | Verifying Documentation - TMP from contractor
c252e7dd-96d8-5cd5-a901-cef297dcbcfe | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 100.5 - Design
7f8c824e-9471-53dc-9c94-70d42d1d8d49 | note | Detail of Activity - Ensure that Design is approved and Drawings are the latest version
f6f88d38-0ae5-564c-ba91-01f02bebdf88 | note | Minimum Test Frequency - Prior to commencement
adcf8940-9a8a-57f4-9e3a-8de6ca51a884 | note | Inspection/Test Method - TNZ M/20; TNZ M/7; TNZ M/24
f7e4f64e-384f-598e-aff6-4a11f1e08612 | note | Acceptance Criteria - Is a copy of approved consent(s) available on site
b6392706-c9e4-5d1b-a35c-66dc8490c572 | note | Verifying Documentation - Check Drawing register
ff8c3e2f-2595-5e23-b539-dee94aca832f | note | Responsibility - Contractor
| checkpoint | 100.6 - Approved Consents
893ab715-dbeb-5391-b93a-f52de0364d2f | note | Detail of Activity - Is a copy of approved consent(s) available on site
96b705c7-af0f-55f4-9cc3-b1a3eadca622 | note | Minimum Test Frequency - Prior to commencement
3ce7721f-214c-5fa1-89b5-3cee7ed9e902 | note | Prior to commencement
8bb2dede-b652-520c-ae63-4ba595e9e09f | note | Inspection/Test Method - Visual Inspection
082310a9-9b26-5e87-b604-e9330ee85513 | note | Acceptance Criteria -
b37a98b9-9bb4-5946-8c90-666daa27d3c5 | note | Verifying Documentation - This ITP
0755237c-ef39-509f-91e7-05aba2a9cb15 | note | Responsibility - BBO's Rep.
| checkpoint | 100.7 - Pre-start meeting
f4d60d8a-712b-52e2-8a6c-a4bf3675bb09 | note | Detail of Activity - Pre-start meeting to confirm work strategy and safety measures
337e8f7b-b6bd-54f1-9e20-51c809e64ae7 | note | Minimum Test Frequency - Before commencing work each day
c96d407e-501c-54d3-af1e-b92f1b87aa14 | note | Inspection/Test Method - N/A
33387768-9757-5401-bc9c-6eb0e6ab63b8 | note | Acceptance Criteria - 100% attendance
d8fa4a21-611a-5569-8ea0-c09465569665 | note | Verifying Documentation - Pre-start sign on register / site diary
b9577ea6-e02a-598a-b2f0-7cf6d12c036b | note | Responsibility - BBO
| checkpoint | 100.8 - Contractor's methodology
62ce3b0d-bf72-5c96-a9f5-a6401b5131e9 | note | Detail of Activity - Site inspection
babc3379-1bcc-50a0-a224-4b11c3584293 | note | Minimum Test Frequency - Prior to commencement
9cb718bc-3428-5223-9ba0-e29c2d719be2 | note | Inspection/Test Method - Document review
380f9e3e-70d7-54cb-b817-035642aa98b6 | note | Acceptance Criteria - Methodology conforms with all relevant specifications
4dd46eb2-54b4-5753-af17-5418069013c1 | note | Verifying Documentation - Methodology submitted via NTE
fb44b67a-fbff-5b0b-83bc-e99993f79ff1 | note | Responsibility - BBO's Rep.
| section | Post Work
| checkpoint | 100.9 - Laydown area / stockpile sites
486e1e9e-a636-5c17-a5c8-ef0b3d5b3972 | note | Detail of Activity - Site inspection
fc6727cd-04c6-5f33-a63b-8cf3c0e1f52f | note | Minimum Test Frequency - Prior to commencement
c7ffa64e-713a-5c60-82b2-af7ecdad455c | note | Inspection/Test Method - Visual Inspection
1cab6316-a2ec-5fef-a2b2-9fd91343d388 | note | Acceptance Criteria - Approved by NZTA
c3994e4f-f3c4-5764-852b-23305d173e89 | note | Verifying Documentation - Request for approval (RFA) via NTE
874d2848-0020-598f-81e5-5b38597da69f | note | Responsibility - BBO's Rep.
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 101.1 - Weather
529587b4-1fee-55fd-847f-c964ede4cc46 | note | Detail of Activity - Assessment of forecast
0ac712ef-7ef1-5852-8878-0565394c8ca2 | note | Minimum Test Frequency - Daily prior to and during works
4e7612d2-e57f-59b0-8579-ee4b53d2a2e8 | note | Inspection/Test Method - Check local and national weather forcast services
500fc0db-a587-597d-9557-ed7c7b646ae0 | note | Acceptance Criteria - No imminent rain or adverse weather conditions. Consideration of wind and project location/environment
31d44841-95bf-5d94-9fdb-2cc21287d267 | note | Verifying Documentation - Contractor's site diary
74085e74-b59f-5319-9503-f14ac1043c79 | note | Responsibility - Contractor
| checkpoint | 101.2 - Environmental Protection
62ab42f5-d3ae-5448-b1c0-42cb5a387468 | note | Detail of Activity - Site evaluation
00f5c6e6-a48f-501e-af81-321668e70531 | note | Minimum Test Frequency - Prior to commencement
5349127e-dbce-5fe0-b20c-cba7f527c02a | note | Inspection/Test Method - Inspection
95db073b-1fd6-5b52-98ac-e4d272794975 | note | Acceptance Criteria - Supervisor assessment of conformance
5b6676f7-a145-59b7-aa2c-ba2be776d9e0 | note | Verifying Documentation - Contractor's site diary
598bb5b7-c4c4-54c9-85e9-56163e9db38e | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 101.3 - Precondition Survey
858ddd6a-10ee-5b6e-a6b9-3233eac4e048 | note | Detail of Activity - Examine extent of the site
e28589f6-27c4-50bc-bf28-e1e4610aed5c | note | Minimum Test Frequency - Prior to commencement
e62a4e2a-1879-537a-a007-b5857dd35deb | note | Inspection/Test Method - Inspection
4d9129bb-2359-5fc5-b959-6ff93206ef93 | note | Acceptance Criteria - Supervisor assessment of conformance
5e69f24e-1a90-5773-8a69-6959308d3674 | note | Verifying Documentation - Contractor's site diary
e17b059c-f8df-556b-9ff5-be93036ae551 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| section | Lot Verification
| checkpoint | Lot Verification complete
edc41a54-d35b-5e15-825d-334828b938a4 | textbox | Lot Verified By:
21e16131-ddc5-5518-8220-5d7b30a90dc4 | dropdown | Lot Status | Outstanding, Closed
4590a2c7-c196-5f94-9d5a-797d37fcf7b7 | date | Lot Closed Date:
1db4fea4-71dc-5640-a059-e03e355ce52a | button | Submitted to Client | Yes, No, N/A
e4b961fd-4069-5717-8125-a5bf8c58edeb | textbox | Reviewed by Client
90f7342b-c845-556a-b8c9-84a45707c53e | textbox | Submission Comments: