## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Braze Bench Test |  |  |  |  | Yes | Braze Bench Test | 0cd042cd-e30d-472a-b84e-0a8e194e4855
checkpoint-status |  |  | checkpoint | Test Sheet Completed
text | 5e4616aa-0c29-5f19-82a2-5ce78d5dbea0 |  | textbox | BUILDING:
text | 0e897536-e607-5686-b789-4e1b58ffa96e |  | textbox | AREA / SYSTEM:
text | df95aa36-94e3-5bc4-a346-22934e8cc8e8 |  | textbox | DRAWING No.
text | f972cebc-babd-595f-b32a-8a588f5e3913 |  | textbox | NAME OF WORKER:
text | e0120d12-5f76-5289-a2d2-7e8ca84621c5 |  | textbox | ASSIGNED BRAZE ID.
text | f9c5ff50-2f5d-54a6-9c47-e449ff4c35c8 |  | textbox | JOINT TYPE INSPECTED:
text | d64a39ef-344b-5527-a40a-83eb16d03e95 |  | textbox | INSPECTING SUPERVISOR
checkpoint-status |  |  | checkpoint | Tube is cut by suitable means, ends are deburred & cleaned of any filings, and surfaces prepared with light grade emery paper.
checkpoint-status |  |  | checkpoint | Joint fit has correct clearance and expanded end of tube (if applicable) is to correct length for pipe size - as per specified requirements
checkpoint-status |  |  | checkpoint | Heat from Oxy Acetylene torch is being applied uniformly to the fitting, and torch flame is slightly reducing/carburising.
checkpoint-status |  |  | checkpoint | Silfos used is 15% and is being applied so that through capillary action is achieved around the entire joint.
checkpoint-status |  |  | checkpoint | Shoulder build-up of Sipfos is just present around the entire circumference of the brazed joint, and completed joint is left to air cool.
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | ed1ee9c2-cac1-5d51-80c7-e9c9f9bb7570 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | b8171401-0656-5295-9479-c1f27cf738c7 |  | textbox | Consultant Name
checklist-flat |  |  | checklist | CHW & HHP Pressure Test |  |  |  |  | Yes | CHW & HHP Pressure Test | 1979b2e7-2ae2-4a55-b258-1d73dccf2e9d
checkpoint-status |  |  | checkpoint | Pressure Test Details collected
text | 4158e152-8ca9-50d3-83e5-93605818b1a3 |  | textbox | Location :
text | 4b8bff97-3a74-5520-b914-5283bcb1ee72 |  | textbox | Floor :
text | 610f8229-b9e6-5835-990a-ecac12392823 |  | textbox | Grid :
text | f924fc86-80e5-50c0-86d8-01d2dccab0cb |  | textbox | Area :
text | 7c2322fc-ceda-5ae0-98fa-5978bd0aebd0 |  | textbox | Contact :
text | 10521cd0-3817-5602-aaff-4a1350a43074 |  | textbox | System :
text | 653f1966-05b1-5fa4-bc67-a0d7708bb435 |  | textbox | Drawing Number - REV :
checkpoint-status |  |  | checkpoint | Data
text | a9e6e800-ac86-5a7d-9069-2e22aef7e9c8 |  | textbox | Operating Pressure kPa
text | cbe352c8-836c-5b7e-9020-6f0779b9bfda |  | textbox | Test Pressure
text | d5ddf2ca-a53d-5c54-bccc-240d694aade8 |  | textbox | Drop in Pressure Allowable
text | cfb25518-c42d-5ba6-bae5-1899b55289c7 |  | textbox | Time Duration of Test hrs/mins
checkpoint-status |  |  | checkpoint | Test
text | 1c4acae3-3ac6-592c-97b3-d64fb19b435c |  | textbox | Initial System Pressure
text | 658b364b-1011-5d77-bf62-f232623c8238 |  | textbox | Date
text | 869d305e-5130-561a-9817-562862729fee |  | textbox | Time
text | f22566b2-0afd-57a3-8660-a82ab88d5468 |  | textbox | Final Systems Pressure
text | 07cf3c88-b2b7-55fb-9dd8-53160c04c9f8 |  | textbox | Date
text | 7529f9a9-3460-535e-b435-e7bf97195f5e |  | textbox | Time
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | f7b10bd6-acff-5bad-aa8f-621ed38ce246 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 9f4f3a26-953a-527d-bc63-e2a331e2f0ee |  | textbox | Consultant Name
checklist-sectioned |  |  | checklist | E4M - Mechanical Board |  |  |  |  | Yes | E4M - Mechanical Board | 1b74e8cf-2fea-4148-b827-955fa66f898f
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Switch Board Mounted in correct position and level
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | Switch Board terminations complete
checkpoint-status |  |  | checkpoint | Board Tested
checkpoint-status |  |  | checkpoint | COC's Complete
checklist-sectioned |  |  | checklist | External Duct Work Insulation |  |  |  |  | Yes | External Duct Work Insulation | 1ef84011-4a81-4886-b170-eaac4c3adf3a
checkpoint-group |  |  | section | External Duct Work Insulation
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Ductwrap materials - Multitel 18kg Density foiled 1-side 25mm thick
checkpoint-status |  |  | checkpoint | Cover entire surface with insulation including all flanges,stiffeners and support angles.
checkpoint-status |  |  | checkpoint | Provide 50mm over lapping at all joints.
checkpoint-status |  |  | checkpoint | Tape all joints with 75mm width (72mm on the Market) Aluminium foiled tape.
checkpoint-status |  |  | checkpoint | Fixing for all Duct size 375mm to 750mm steel weld pins on centreline at 400mm spacing bottom surface only.
checkpoint-status |  |  | checkpoint | Fixing for all Duct size 750mm and greater steel weld pins at 400mm spacing maximum.
checkpoint-status |  |  | checkpoint | Fixing for all Duct riser steel weld pins at 400mm spacing maximum.
checkpoint-status |  |  | checkpoint | Using additional polypropylene fixing Bands 600mm centres.
checkpoint-status |  |  | checkpoint | Provide an overlap of atleast 300mm where insulation changes from the inside of the duct to the outside.
checklist-flat |  |  | checklist | Pressure Test |  |  |  |  | Yes | Pressure Test | 297bd196-e8dc-419a-892a-4b39634a2ec1
checkpoint-status |  |  | checkpoint | Details of pressure test
text | bb4be81a-f5d9-5fb4-9358-e6dbefe1db86 |  | textbox | System Name/No.
text | 4538ff9e-e6f6-54e7-a36f-1db439a9dea6 |  | textbox | Location / Drawing No.
text | 3fbaa547-dd14-549d-a077-6b636ae1bbeb |  | textbox | Test Instrument & Serial Number.
text | bf741398-d297-5d32-919c-b086b213fa87 |  | textbox | Normal Working Pressure |  | kPa
text | 4e6cea05-ce84-58b9-8efb-3fead8a00be7 |  | textbox | Start test ambient temperature |  | Celsius
text | eaf2fdfe-fdf8-5e99-8cb6-395684ebc29c |  | textbox | Start test date |  | dd/mm/yy
text | 3072464c-be62-50f1-a355-92a3b4e136de |  | textbox | Start test time |  | hours:mins
text | 4afb1df1-9cee-585e-a980-d716a8472bae |  | textbox | Start test pressure |  | kPa
text | ed661523-35ed-532b-ace1-75b7ba667ba3 |  | textbox | Finish test ambient temperature |  | dd/mm/yy
text | 2c20de96-9b67-5b6e-a899-2266d137db5c |  | textbox | Finish test date |  | hours:mins
text | 3f58404b-c8c5-5ae3-b28a-8c1d6a80eb1e |  | textbox | Finish test time |  | kPa
text | 9e9a46d9-6584-559e-9cc6-386222161042 |  | textbox | Finish test pressure |  | kPa
text | 79409b98-fb1c-533a-82b2-f917b1bdc452 |  | textbox | Corrected pressure at test completion
label | e7bd0147-7b35-5b08-bbf1-30746137cac4 |  | note | Attach photos of the gauges as required
label | 7710a1ff-d46a-56ac-9524-24ad0d3fd881 |  | note | FORMULA :
label | 5f45fbca-1d8c-50cd-904b-076ab8103aa1 |  | note | Pc = P x (Ts + 273) / (T + 273) kpa
label | 9f7d432b-7867-5f66-8b2c-ba3d19df8d58 |  | note | Pc = P x ( +273 ) / ( + 273) kPa
label | cb6fa340-de98-59b0-8c68-6e5ef9a077eb |  | note | Pc = kPa
label | b770319d-d81e-5c36-b68b-8e4ab04a4bdf |  | note | WHERE:-
label | ac3ec979-383e-541a-8a79-6a06bb713d7d |  | note | P = PRESSURE REQUIRING CORRECTION i.e. PRESSURE ACTUALLY READ AT TEST END
label | 88785fb6-5270-527f-860b-3370df0dafc8 |  | note | Pc = CORRECTED PRESSURE
label | 78b41f5c-3b46-5c12-99e6-cdb3d334b10e |  | note | Ts = AMBIENT TEMPERATURE oC AT START OF TEST
label | 37a1c185-c7c5-55d9-bd9e-16d7c34d69fa |  | note | T = AMBIENT TEMPERATURE oC AT SAME TIME OF READING P.
checklist-sectioned |  |  | checklist | Medical Gas Piping |  |  |  |  | Yes | Medical Gas Piping | 3c41b463-ffa8-413b-bd53-ec4f848070e7
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Piping installation to existing system to be appoved before works can commence
checkpoint-status |  |  | checkpoint | Exsiting pipe system made safe before tie in
checkpoint-status |  |  | checkpoint | Pipework Installed as per drawing
text | 3dce92f6-13c0-5122-9839-c5eb37b02656 |  | textbox | Installation done by
checkpoint-status |  |  | checkpoint | Pipe Brackets installed
checkpoint-status |  |  | checkpoint | Pipe sizing is correct and valving in correct location
checkpoint-status |  |  | checkpoint | Avus Installed
checkpoint-status |  |  | checkpoint | Labelling and Markings & Sleeving and Supports Installed
checkpoint-status |  |  | checkpoint | Visual check of pipeline labelling & markings
checkpoint-status |  |  | checkpoint | Leak Tested & Test sheet uploaded
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
text | 66ed15af-dea0-5ef3-be6a-e042538823f4 |  | textbox | Name - AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 4494164e-eb4e-581d-9fb0-351cc948ffb3 |  | textbox | Name - Witness
checkpoint-status |  |  | checkpoint | Signed off By Consultant
text | ee757413-3dc5-53cd-b63e-04bb96b7619c |  | textbox | Name - Consultant
checkpoint-status |  |  | checkpoint | Photo's of Pressure test
checklist-sectioned |  |  | checklist | CHW Insulation |  |  |  |  | Yes | CHW Insulation | 4705f6e8-fff1-431c-a620-68b431ec5fbe
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Approved material thickness has been used (Thermobreak®).
checkpoint-status |  |  | checkpoint | Insulation is installed as per the manufacturers recommendations, as well as per any additional requirements set out in the project specificaiton
checkpoint-status |  |  | checkpoint | Pipe sections firmly abutted to Insulation Blocks within the pipe supports, and Blocks have been glued
checkpoint-status |  |  | checkpoint | Insulation is glued to the pipe with a 50mm wide band of adhesive (Ados F2®) at both ends of section to form the vapour barrier
checkpoint-status |  |  | checkpoint | Adhesive is applied along all longitudional and circumferential joints
checkpoint-status |  |  | checkpoint | A 50mm wide strip of pressure sensitive tape reinforced aluminium tape is applied to the insulation facing, along and around all joints
checkpoint-status |  |  | checkpoint | Mitre cut elbows have been used on all bends.
checklist-flat |  |  | checklist | HDPE Pipework Installation |  |  |  |  | Yes | HDPE Pipework Installation | 694418f4-77d5-4e4f-9609-4936989f029d
checkpoint-status |  |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status |  |  | checkpoint | All personal using the welding machine to be trained and certificate issued to the client.
checkpoint-status |  |  | checkpoint | Inspect pipework for damage prior to installation.
checkpoint-status |  |  | checkpoint | Threaded rod and Unistrut to be used to support HDPE
checkpoint-status |  |  | checkpoint | pipework, supports to be installed off structural beams where possible.
checkpoint-status |  |  | checkpoint | Spacing of supports to be as per manufactures specifications.
checkpoint-status |  |  | checkpoint | Install valves as per drawing ensuring bolts are the correct length and tightened.
checkpoint-status |  |  | checkpoint | Bolt heads to marked with a cross indicating they have been tightened
checkpoint-status |  |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status |  |  | checkpoint | Confirm Test pressure from Site Manager
checkpoint-status |  |  | checkpoint | Pressure test completed with air and not hydraulic
checkpoint-status |  |  | checkpoint | Pressure testing to be completed progressive lengths of Installed pipework
checkpoint-status |  |  | checkpoint | Complete Pipework Pressure Test Report
checkpoint-status |  |  | checkpoint | As-Builts Completed.
checklist-sectioned |  |  | checklist | HDPE Compressed Air Pipework and Equipment Installation Checklist |  |  |  |  | Yes | HDPE Compressed Air Pipework and Equipment Installation Checklist | 6b28d1de-65d2-4129-b8d5-55690d97285e
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | All material certificates of compliance are provided
checkpoint-status |  |  | checkpoint | All personal using the welding machine to be trained and certificate issued to client
checkpoint-group |  |  | section | Inspection of Pipework Prior to installation
checkpoint-status |  |  | checkpoint | Inspect pipework for damage prior to installation
checkpoint-group |  |  | section | Inspection of Compressed Air Equipment
checkpoint-status |  |  | checkpoint | Inspect condenser Air compressors , Dryers , Receivers , Filters and Pre - Filters prior to installation of damage
checkpoint-group |  |  | section | Install pipework support brackets
checkpoint-status |  |  | checkpoint | Treaded rod and unistruct to be used to support HDPE pipework , supporting to be installed off structural beams where possible
checkpoint-status |  |  | checkpoint | Spacing of supports to be as per manufactures specifications
checkpoint-group |  |  | section | Installation of valves
checkpoint-status |  |  | checkpoint | Install valves as per drawing ensuring bolts are the correct length and tightened.
checkpoint-status |  |  | checkpoint | Bolt heads to marked with a cross indicating they have been tightened
checkpoint-group |  |  | section | Installation of Strainers
checkpoint-status |  |  | checkpoint | Strainers to have an isolating valve either side and have clear access to conduct maintenance.
checkpoint-group |  |  | section | Installation of Test Points
checkpoint-status |  |  | checkpoint | Provide Binder test points directly before and after main plant items
checkpoint-group |  |  | section | Compressor Installation
checkpoint-status |  |  | checkpoint | Install compressor as per manufactures recommendation.
checkpoint-status |  |  | checkpoint | Compressor is installed level.
checkpoint-status |  |  | checkpoint | Ensure there are no obstructions to complete maintenance activities.
checkpoint-group |  |  | section | Dryer Installation
checkpoint-status |  |  | checkpoint | Install Dryer as per manufactures recommendation.
checkpoint-status |  |  | checkpoint | Dryer is installed level
checkpoint-status |  |  | checkpoint | Ensure there are no obstructions to complete maintenance activities.
checkpoint-group |  |  | section | Receiver Installation
checkpoint-status |  |  | checkpoint | Install Receiver as per manufactures recommendation.
checkpoint-status |  |  | checkpoint | Receiver is installed level.
checkpoint-status |  |  | checkpoint | Ensure there are no obstructions to complete maintenance activities.
checkpoint-status |  |  | checkpoint | Access manhole of 600 mm ID on one side
checkpoint-group |  |  | section | Filter and Pre- Filter Installation
checkpoint-status |  |  | checkpoint | Install Filter as per manufactures recommendation.
checkpoint-status |  |  | checkpoint | Ensure there are no obstructions to complete maintenance activities.
checkpoint-status |  |  | checkpoint | Each filter shall be equipped with differential pressure gauges and pressure transducers for filter dirty alarm.
checkpoint-group |  |  | section | Electrofusion Welding
checkpoint-status |  |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-group |  |  | section | Pipework Pressure Test
checkpoint-status |  |  | checkpoint | Confirm Test pressure from Site Manager
checkpoint-status |  |  | checkpoint | Pressure test completed with air and not hydraulic ?
checkpoint-status |  |  | checkpoint | Pressure testing to be completed progressive lengths of Installed pipework
checkpoint-status |  |  | checkpoint | Complete Pipework Pressure Test Report
checkpoint-group |  |  | section | Pipework Identification
checkpoint-status |  |  | checkpoint | All above ground piping shall be labelled with self adhesive labels to indicate contents and flow direction.
checkpoint-status |  |  | checkpoint | Labels shall be applied at 8m maximum spacing and within 1m of each valve.
checkpoint-group |  |  | section | Valve Tag Installation
checkpoint-status |  |  | checkpoint | All valves shall be fitted with a tag that clearly shows the valve number as per the drawings
checkpoint-status |  |  | checkpoint | The tag shall be attached to the body of the valve in a location
checkpoint-group |  |  | section | Fire Penetration Treatment
checkpoint-status |  |  | checkpoint | Pipework installed through a fire wall is to be fire stopped
checkpoint-group |  |  | section | Seismic Certification
checkpoint-status |  |  | checkpoint | Install Seismic Fixings as per drawings supplied from Structural Engineer.
checkpoint-group |  |  | section | As- Builts
checkpoint-status |  |  | checkpoint | As-Builts Completed.
checkpoint-status |  |  | checkpoint | All works completed and reviewed
checklist-sectioned |  |  | checklist | External Duct Work Insulation (Fire Rated) |  |  |  |  | Yes | External Duct Work Insulation (Fire Rated) | 70aed6b9-7666-40b0-a284-cc527d8a09ea
checkpoint-group |  |  | section | External Duct Work Insulation ( Fire Rated )
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Fire rated Ductwrap materials - 38mm thick Fyrewrap Elite 1.5 (FRL 120/120/120)
checkpoint-status |  |  | checkpoint | Install as per Manufacturer's Standards: (Trafalgar-Fyrewrap)
checkpoint-status |  |  | checkpoint | Fyrewrap duct wrap must completely covered the duct and there must not be any exposed sections or gaps.
checkpoint-status |  |  | checkpoint | A 100mm miniimum overlap must be used on all joints. Only the Three specified methods (telescope, checkerboard and butt splice methods.) of overlap may be used when adjoining Fyrewrap duct wraps.
checkpoint-status |  |  | checkpoint | Cut edges must be completely sealed with the specified pressure-sensitive aluminium foiled tape.
checkpoint-status |  |  | checkpoint | ≤600 x600 duct size Steel banding only spacing 40mm from edges over the overlap and one additional between overlaps.
checkpoint-status |  |  | checkpoint | ≤1200 x1200 duct size Steel banding and pins bottoms only spacing 40mm from edges over the overlap and one additional between overlaps. Pre-welded Pins grid 200mm centres.
checkpoint-status |  |  | checkpoint | ≥1200 x1200 duct size pins only all sides of duct pre-welded Pins grid 200mm centres.
checkpoint-status |  |  | checkpoint | Wall penetrations up to 1600mm duct size 75mm x 75mm x1.6mm steel angle 100mm width x 60mm thick maxilite board.
checkpoint-status |  |  | checkpoint | Length of second layer from the fire barrier FRL 60/60/60
checkpoint-status |  |  | checkpoint | Duct size 600mm x 600mm or less -second layer 1350mm
checkpoint-status |  |  | checkpoint | Duct size 600mm x 1200mm or less -second layer 1600mm
checkpoint-status |  |  | checkpoint | Duct size 600mm x 600mm -second layer 1900mm
checkpoint-status |  |  | checkpoint | Duct size 200mm x 2400mm -second layer 2500mm
checkpoint-status |  |  | checkpoint | Duct size 2400mm x 3600mm -second layer 2700mm
checkpoint-status |  |  | checkpoint | Used only Trafalgar Access Panels -must be fitting directly over the existing duct access panels fixed with rivets and fyreflex fire rated sealant, with a second local layer of Fyrewrap.
checklist-sectioned |  |  | checklist | Mechanical Duct |  |  |  |  | Yes | Mechanical Duct | 74724aaa-5481-40b7-8ca4-e9ee1a5897be
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | Ducting / equipment connections including flexibles, nuts, bolts and washers correct and tight.
checkpoint-status |  |  | checkpoint | U/S of duct heights correct as per Workshop Drawings.
checkpoint-status |  |  | checkpoint | Ducts to be removed relocated / relocated as per drawings
checkpoint-status |  |  | checkpoint | Duct Hangers (is spacing correct, installed level etc)
checkpoint-status |  |  | checkpoint | Duct jointing (Joints sealed, cleats fitted etc)
checkpoint-status |  |  | checkpoint | Fire Dampers installed in open position c/w access panel.
checkpoint-status |  |  | checkpoint | Sound attenuators installed
checkpoint-status |  |  | checkpoint | Transfer ducts installed
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | Motorized dampers orientation to be installed correct way for sealing purpose
checkpoint-status |  |  | checkpoint | Access Panels to be installed as per drawing
checkpoint-status |  |  | checkpoint | Spade Joint ( Pandemic Mode ) to be installed as per drawing indicated
checkpoint-status |  |  | checkpoint | All volume control dampers set fully open.
checkpoint-status |  |  | checkpoint | Butterfly and outlet dampers installed as per drawing and in open position.
checkpoint-status |  |  | checkpoint | Filter box installed
checkpoint-status |  |  | checkpoint | Seismic bracing installed as per Drawing
text | b57ee844-95e0-51f4-8a2b-3103cc813d80 |  | textbox | Drawing Referance number
checkpoint-status |  |  | checkpoint | Pressure testing (If Required )
boolean | 139f7787-08d7-5b64-8f53-3d79a2e382a3 |  | tickbox | Leak test Documents uploaded
checkpoint-group |  |  | section | Fit off QA
checkpoint-status |  |  | checkpoint | Flexible ducting installed c/w supports.
checkpoint-status |  |  | checkpoint | Correct Equipment / Correct Grills / Diffuser Installed
checkpoint-status |  |  | checkpoint | Grills as per drawings relocated or removed
checkpoint-status |  |  | checkpoint | Grills to be blanked as per drawing for Pandemic mode
checkpoint-status |  |  | checkpoint | Filters installed
checklist-sectioned |  |  | checklist | Fans |  |  |  |  | Yes | Fans | 868cb4c6-7f67-4943-b5b9-0ad23d65f703
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Mountings / springs installed
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | U/S of Fan heights correct as per Workshop Drawings.
checkpoint-status |  |  | checkpoint | Position of fan Installed correctly ontop of Roof Structure upstands
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | Builder - Waterproof and Seal to be installed
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | Fire Damper Installation Test |  |  |  |  | Yes | Fire Damper Installation Test | 91ef7df4-080b-4c98-a446-dc45f01d3fd0
checkpoint-status |  |  | checkpoint | Fire Damper Ready for Testing
text | 640694a1-4248-5323-824b-20f7d0b9d946 |  | textbox | Fire Damper Reference
text | 1ed33654-6c31-54bb-b700-874ce62a120c |  | textbox | Size - W x H (mm)
text | 0af8cf9d-b2b7-5950-9d33-63f484ddb4e2 |  | textbox | Wall / slab Thickness (mm)
boolean | fb355819-d2c8-5cd3-8a39-1738cd0bc8a3 |  | tickbox | Access Air On
boolean | 3743f902-400e-552d-96a1-aca4eb1c1c8f |  | tickbox | Access Air Off
text | 812a0a8b-ed98-5402-8310-381b30a62bb6 |  | textbox | Model No.
text | 8c97d947-2fd4-58f6-bc84-53ddb9490f77 |  | textbox | Wall FRL
text | 9f0fdf0b-66a0-55d7-8ce8-d9353261c2a0 |  | textbox | Fire Damper FRL
checkpoint-status |  |  | checkpoint | F/D label in accordance with 1682.1 is fitted.
checkpoint-status |  |  | checkpoint | F/D construction and installation is in accordance with the certified and tested method
checkpoint-status |  |  | checkpoint | F/D orientation is installed as per the label
checkpoint-status |  |  | checkpoint | F/D is fully open and the fusable link is installed
checkpoint-status |  |  | checkpoint | F/D is installed with respect to the direction of air flow marked on the label
checkpoint-status |  |  | checkpoint | F/D wall clearances are achieved (Reference 1682.2)
checkpoint-status |  |  | checkpoint | F/D operation (closure) is not impeded
checkpoint-status |  |  | checkpoint | F/D assumes a fully closed position in fire mode
checklist-sectioned |  |  | checklist | Fan Coil Units |  |  |  |  | Yes | Fan Coil Units | b5d122a7-0f94-4955-9f39-862fe6061b90
checkpoint-group |  |  | section | First Fix
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | u/s of Unit at correct height
checkpoint-status |  |  | checkpoint | Mounting and Springs Installed
checkpoint-status |  |  | checkpoint | Correct Hanger Spacing
checkpoint-status |  |  | checkpoint | Unit Plenum Boxes to be installed
checkpoint-status |  |  | checkpoint | Filters installed
checkpoint-status |  |  | checkpoint | Siesmic Bracing Installed
checklist-flat |  |  | checklist | Fan Coil Units E4M |  |  |  |  | Yes | Fan Coil Units E4M | c14e8264-78f5-4a6f-bad6-4450a846f48a
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated correcly as per wiring diagram
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Motorized control valves wired up and connected
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-sectioned |  |  | checklist | AHU's |  |  |  |  | Yes | AHU's | c3008699-1c08-4289-b359-576b34c5c269
checkpoint-group |  |  | section | Unit First Fix QA
checkpoint-status |  |  | checkpoint | Check if plinth site is correct
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | Setting out point correct
checkpoint-status |  |  | checkpoint | Anti Vibration pads to be installed
checkpoint-status |  |  | checkpoint | Condensate Piping installed
checkpoint-status |  |  | checkpoint | Tundish installed by others and connected up
checkpoint-status |  |  | checkpoint | Insulation Complete for Piping and Condensate lines
checkpoint-status |  |  | checkpoint | Siesmic Bracing Installed
checkpoint-group |  |  | section | Unit Second Fix QA
checkpoint-status |  |  | checkpoint | Filters Installed
checkpoint-status |  |  | checkpoint | Commissioning Complete
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-sectioned |  |  | checklist | CWH & HHP Piping |  |  |  |  | Yes | CWH & HHP Piping | c5c9ea5e-4382-4ab3-8f97-d193fb8ec30b
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Pipework installed as per Drawing
text | c093f36f-2684-5f7f-9ae1-d6be3d1d7f6d |  | textbox | Installation done by
checkpoint-status |  |  | checkpoint | Pipe sizing is correct and valving in correct location
checkpoint-status |  |  | checkpoint | Insulation blocks installed where required
checkpoint-status |  |  | checkpoint | Correct hanger spacing
checkpoint-status |  |  | checkpoint | Isolating and Control valve installed correctly
checkpoint-status |  |  | checkpoint | Hose piping installed
checkpoint-status |  |  | checkpoint | Air vents installed at all high points
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | Pressure Tested CWH & HHW pipe
checkpoint-status |  |  | checkpoint | P - trap installed
checkpoint-status |  |  | checkpoint | Driptray installed
checkpoint-status |  |  | checkpoint | Condensate Drains installed
checkpoint-status |  |  | checkpoint | Tundish provided by others
checkpoint-status |  |  | checkpoint | Correct Fall to tundish , and water flow tested
checklist-sectioned |  |  | checklist | Fire Dampers |  |  |  |  | Yes | Fire Dampers | c75a42f3-b274-4457-ae64-6465caca8c93
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Correct FD Installed
checkpoint-status |  |  | checkpoint | Access Panel installed
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | Drop Tested
checkpoint-status |  |  | checkpoint | Track is Clear
checkpoint-status |  |  | checkpoint | Builder to Fire Sealed
checklist-flat |  |  | checklist | Seismic Certification |  |  |  |  | Yes | Seismic Certification | cd8dc5d9-1da2-4ef2-baf8-193610d67900
checkpoint-status |  |  | checkpoint | Install Seismic brackets as per drawings supplied from Structural Engineer.
checklist-sectioned |  |  | checklist | Condensate Insulation |  |  |  |  | Yes | Condensate Insulation | d5ca4bdd-0d4e-4c89-823b-24dfbe7e84ad
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Approved materials have been used (e.g. Elastomeric closed cell insulation), min 9m thick
checkpoint-status |  |  | checkpoint | Entire surface of pipe is covered from the indoor units' condensate trap, for a distance of 2m down the line
checkpoint-status |  |  | checkpoint | Adhesive is applied to any longitudional and circumferential joints, as well as to the ends of the insulaiton to the pipe
checkpoint-status |  |  | checkpoint | Finish circumferential joints by wrapping with 50mm wide pressure-sensitive pre-adhered PVC tape.
checklist-sectioned |  |  | checklist | External Acoustic Insulation (FCU's) |  |  |  |  | Yes | External Acoustic Insulation (FCU's) | db52cde2-63e8-4382-8897-37dfdcb1a27b
checkpoint-group |  |  | section | External Duct Work Insulation
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Acoustic wrap materials - 50mm Polyester sheet cover with 5kg wave bar
checkpoint-status |  |  | checkpoint | Cover all surface of the FCU units with insulation excluding the Vents and pipe outlet area.
checkpoint-status |  |  | checkpoint | fixing using self adhesive pins and polypropylene Bands with with buckles .
checkpoint-status |  |  | checkpoint | Tape all joints with 50mm width reinforced Aluminium foiled tape.
checklist-flat |  |  | checklist | Internal Duct Work Insulation |  |  |  |  | Yes | Internal Duct Work Insulation | dd74e48c-c567-4052-94d5-c9e1a2127183
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Duct materials - Fibreglass
checkpoint-status |  |  | checkpoint | Fixed with Adhesive weld pins and speed clips located not more than 75mm from the edges of the ducts and spaced not more than 300mm centres.
checkpoint-status |  |  | checkpoint | Longitudinal corner joints fixed with:
checkpoint-status |  |  | checkpoint | duct dimensions less than 300mm -25mmx25mm angles
checkpoint-status |  |  | checkpoint | duct dimensions 300mm and greater -50mmx50mm angles
checkpoint-status |  |  | checkpoint | Joints taped between adjacent of insulation with a 75mm wide strip of reinforced aluminium foil laminate tape.
checkpoint-status |  |  | checkpoint | Tape joints protected with 75mm wide sheet metal cover strip, pop riveted to the corner angles.
checklist-flat |  |  | checklist | Electrofusion Welding |  |  |  |  | Yes | Electrofusion Welding | e7832575-1238-481e-b224-ab45fb83a4de
checkpoint-status |  |  | checkpoint | Welding Details entered
text | bf76d5a7-250e-5835-bfd0-d7589fbb10f3 |  | textbox | Fusion Machine used - SR No 402 - 1348 Caldertech EF welder
checkpoint-status |  |  | checkpoint | Pipe surface free from scratches, deeper than 10% of the wall thickness ?
checkpoint-status |  |  | checkpoint | Pipe scraped and marked ?
checkpoint-status |  |  | checkpoint | Pipe surface cleaned with Isophrophel alcohol?
checkpoint-status |  |  | checkpoint | Barcode scanned by machine?
checkpoint-status |  |  | checkpoint | Record cooling time achieved?
checkpoint-status |  |  | checkpoint | EF Coupler Completed by and recorded
text | b96ca1d3-aadc-5c5d-841e-f0094df5b063 |  | textbox | Record EF Coupler Used ( Size )
text | a433fed8-d0d8-50f7-b080-1bbb97bc8da6 |  | textbox | Type info
checkpoint-status |  |  | checkpoint | Details of E.F Coupler Operator
text | 40a8777e-1e2c-5f91-9ae3-7e50f9ec932c |  | textbox | Type Persons name
checkpoint-status |  |  | checkpoint | Post weld checks completed
checklist-flat |  |  | checklist | Fire Damper Installation Test |  |  |  |  | Yes | Fire Damper Installation Test | e93fcd82-b3f3-41ea-9551-4ad529f7ac40
checkpoint-status |  |  | checkpoint | Fire Damper Ready for Testing
text | 5c556669-cc48-5720-85b3-5821263418d1 |  | textbox | Fire Damper Reference
text | 492500df-5d00-54c8-b106-3cd4f6305470 |  | textbox | Size - W x H (mm)
text | ea055fdd-2841-53a1-a5b3-5642daec324b |  | textbox | Wall / slab Thickness (mm)
boolean | 489f1ca6-3792-52cc-949e-67eb9550560b |  | tickbox | Access Air On
boolean | f1a5d2c7-0375-5282-9c62-50f5805ef9e6 |  | tickbox | Access Air Off
text | c9694555-d23a-5232-a0dd-9d0ff46bd2e0 |  | textbox | Model No.
text | bdd01892-7e85-5bc8-adad-96a8fb50eab0 |  | textbox | Wall FRL
text | 2516eae4-b86e-582d-9e8a-ecc1127be1ef |  | textbox | Fire Damper FRL
checkpoint-status |  |  | checkpoint | F/D label in accordance with 1682.1 is fitted.
checkpoint-status |  |  | checkpoint | F/D construction and installation is in accordance with the certified and tested method
checkpoint-status |  |  | checkpoint | F/D orientation is installed as per the label
checkpoint-status |  |  | checkpoint | F/D is fully open and the fusable link is installed
checkpoint-status |  |  | checkpoint | F/D is installed with respect to the direction of air flow marked on the label
checkpoint-status |  |  | checkpoint | F/D wall clearances are acheieved (Reference 1682.2)
checkpoint-status |  |  | checkpoint | F/D operation (closure) is not impeded
checkpoint-status |  |  | checkpoint | F/D assumes a fully closed position in fire mode