## CRL- QA Documentation
CRL
Section | Quality Management Plan
Section | Drawings
AE Smith Construction Drawing
X
Y
Z
Consultant
X
Y
Z
Seismic
X
Y
Z
Section | Producer Statement Design
Building / Area
PS 1
PS 3
PS 4
Section | BMS
Building / Area
X
Y
Z
Section | Electrical
Building / Area
COC's
X
Y
Z
Section | Specifications Document
HTM_02-01_Part A
Section | General
X
Y
Z
Section | Photos
X
Y
Z

## Check Sheet( ITR's)
CRL- All Stations
Check Sheet | CRL-ITR-001 - Mechanical Duct
| Section | First Fix QA
Checkpoint
Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
U/S of duct heights correct as per Workshop Drawings.
Duct Hangers (is spacing correct, installed level , rods trimmed back etc)
Duct jointing (Joints sealed, cleats fitted etc)
Orientation of dampers and equipment to be installed correct way
Access Panels to be installed as per drawing
| Section | Second Fix QA
Checkpoint
All volume control dampers set fully open.
|  |  | Seismic bracing installed as per Drawing | Section | Drawing Referance number
Flexibles installed and supported correctly
| Section | Fit Off QA
Checkpoint
Correct Equipment / Correct Grills / Diffuser Installed
Restrained correctly
Flexible connection fixed correctly to grill box
Check Sheet | CRL-ITR-002 - Fire Dampers
| Section | First Fix QA
|  | Checkpoint | Penetration formed correctly
Correct FD Installed & correct orientation
| Section | Second Fix QA
Checkpoint
Access Panel installed
|  |  | Drop Tested |  |  | ( Sudeshan please use previous job sheet that is in your libary)
Track is Clear
All angles correctly fixed
Label to be installed
Check Sheet | CRL-ITR-003 - Mechanical Board ( MSSB )
Checkpoint
Correct Equipment / plant installed
Switch Board Mounted in correct position and level
Switch Board terminations complete
Board Tested
COC's Complete
Label to be installed
Check Sheet | CRL-ITR-004 - Fans
Checkpoint
Correct Equipment / plant installed
Correct mountings / springs installed
U/S of Fan heights correct as per Workshop Drawings.
|  |  | Seismic Bracing Installed | Section | Drawing Referance number
Label to be installed
| Section | E4M QA
Checkpoint
Electrical Isolators installed in correct location
Units Terminated
Units Tested and Running
Check Sheet | CRL-ITR-005 - Fan Coil Units
| Section | Unit First Fix QA
|  | Checkpoint | Correct Unit Installed
u/s of Unit at correct height
Correct mountings / Springs Installed
Unit Second Fix QA
|  | Checkpoint | Unit Plenum Boxes to be installed
Filters installed & clearence checked
|  |  | Seismic Bracing Installed | Section | Drawing Referance number
P - trap installed if required
Driptray installed if required
Condensate Drains installed
Correct Fall to tundish , and water flow tested
Label to be installed
| Section | E4M QA
Checkpoint
Electrical Isolators installed in correct location
Units Terminated
Units Tested and Running
Check Sheet | CRL-ITR-006 - Chilled Water Pipe Systems
Checkpoint
|  |  | Pipework installed as per Drawing | Section | Installation done by
Valve arrangement installed as per schematic
Insulation blocks installed where required
Correct hanger spacing
Drains installed at low points
Air vents installed at all high points
The pipe OD and groove dimensions are within tolerance range as per victaulic specification
The correct coupling has been used for the correct joint i.e flexible or rigid
Visual indicators verified - Positive overlap - Joint Square
Steel is primed and weld painted after works are completed (PA10)
|  |  | Pipework Seismic to be installed | Section | Drawing Referance number
Check Sheet | CRL-ITR-007 - Hydro Pressure Test
|  | Checkpoint | Pressure Test |  |  | ( Sudeshan please use previous job sheet that is in your library and add to this section)
Check Sheet | CRL-ITR-008 - AHU Installation
Checkpoint
Check plinth size and location
Correct Unit Installed
Condensate Piping installed
Unit correctly anchored
|  |  |  | Section | Drawing Referance number
| Section | Unit Second Fix QA
|  | Checkpoint | Filters Installed
Label to be installed
| Section | E4M QA
|  | Checkpoint | Electrical Isolators installed in correct location
Units Terminated
Units Tested and Running
Check Sheet | CRL-ITR-009 - Chillers Installation
Checkpoint
Check if plinth site is correct
Correct Unit Installed
Setting out point correct
|  |  | Corrrect Mounting Springs installed | Section | Drawing Referance number
Label to be installed
Check Sheet | CRL-ITR-010 -Crack Unit Installation
Checkpoint
Correct Unit Model
Check for Damage
Verify Floor is Level
|  |  | Confirm Fixings as per detail (Seismic) | Section | Drawing Referance number
Crack Second Fix QA
Potable Water connected ( by others )
Filters Installed – Check Clearances
Door Clearance checked
Drains Installed – Run to Tundish by Others
Shipping mounts removed
Label to be installed
Check Sheet | CRL-ITR-011 - Pump Installation
Checkpoint
Check if plinth site is correct
Correct Unit Installed
Setting out point correct
|  |  | Corrrect Mounting Springs installed | Section | Drawing Referance number
Label to be installed
Check Sheet | CRL-ITR-012 - Braze Bench Test
Checkpoint
Test Sheet ( Sudeshan please use previous job sheet that is in your library and add to this section)
Med Lab Results
Checkpoint
Document of Results
Check Sheet | CRL-ITR-013 - Radiant Heaters
Checkpoint
Correct Equipment / plant installed
U/S of Equipemnt heights correct as per Workshop Drawings.
| Section | E4M QA
|  | Checkpoint | Electrical Isolators installed in correct location
Units Terminated
Units Tested and Running
Check Sheet | CRL-ITR-014 - Duct / Equipment Cleaning
Checkpoint
Duct cleaned in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
Check Sheet | CRL-ITR-015 - Cowls
|  | Checkpoint | Outside Air Roof Cowl Installed
Builder - Waterproof and Seal to be installed
Check Sheet | CRL-ITR-016 - DX Units
|  | Checkpoint | Correct Unit Installed
Out door Unit Installed
u/s of Unit at correct height
Refrigeration Pipework installed as per drawings
|  |  |  | Section | Installation done by
|  |  |  | Section | Pipework Installed from DX unit box to Outdoor unit
Schematic markupsdrawings
Condensate Piping installed
Pressure Tested
|  |  |  | Section | Signed off By AE Smith
[7 empty] | Name of person | Date
|  |  |  | Section | Photo's of Pressure test
[7 empty] | Start of Pressure test |  | Time / Date
[7 empty] | Pressure test after recored Duration |  | Time / Date
Triple Evacuation procedure to be done.Final below 500 Microns
Refrigeration ( Scale ) charge unit completed - According to Calculation for Pipe Size & Length
Insulation Complete for Piping and Condensate lines
|  |  | Siesmic Bracing Installed | Section | Drawing Referance number
| Section | Unit Second Fix QA
|  | Checkpoint | Filters Installed
| Section | E4M QA
|  | Checkpoint | Electrical Isolators installed in correct location
Units Terminated
Units Tested and Running
Check Sheet | CRL-ITR-017 - CHW Insulation
Checkpoint
Insulation is installed as per the manufacturers recommendations, as well as per any additional requirements set out in the project specificaiton
Pipe sections firmly abutted to Insulation Blocks within the pipe supports, and Blocks have been glued
Insulation is glued and taped correctly
Confirm insulation is free of damages
Check Sheet | CRL-ITR-018 - Condensate Insulation
Checkpoint
Approved materials have been used (e.g. Elastomeric closed cell insulation), min 9m thick
Condensate pipework insulated correctly
Confirm insulation is free of damages
Check Sheet | CRL-ITR-019 - External Duct Work Insulation
Checkpoint
Insulate ducting as per drawing and specifications
Provide 50mm over lapping at all joints.
Confirm pins are installed and spacing is correct
Confirm bands at 600mm centres.
Confirm all overlaps and joints are complete
Confirm insulation is free of damages
Check Sheet | CRL-ITR-020 - Fire Rated Duct Insulation
Checkpoint
Insulate ducting as per drawing and specifications
Ensure all wraps are complete and no gaps ensure
Confirm all joints installed correctly with suitable overlaps
Pins and banding correctly applied
Maxilite board to wall complete and sealed.
Confirm second layer length has been installed as per specification from wall.
Access Panels installed correctly.Confirm fixings , sealant and alignment with internal panel.
Confirm insulation is free of damages
Check Sheet | CRL-ITR-021- Metal Cladding
Checkpoint
Clad pipework as per drawing
Approved materials have been used
Pipework cladding installation complete and tidy.Check straps ,sealant and removable sections
Penetraitons are sealed for gauges, instruments, and drain vents (silicone)
Confirm cladding is free of damages