## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | Mechanical Duct | [5 empty] | CRL-ITR-001 - Mechanical Duct
section | First Fix QA
checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint | U/S of duct heights correct as per Workshop Drawings.
checkpoint | Duct Hangers (is spacing correct, installed level , rods trimmed back etc)
checkpoint | Duct jointing (Joints sealed, cleats fitted etc)
checkpoint | Orientation of dampers and equipment to be installed correct way
checkpoint | Access Panels to be installed as per drawing
section | Second Fix QA
checkpoint | All volume control dampers set fully open.
checkpoint | Seismic bracing installed as per Drawing
textbox | Drawing Reference Number
checkpoint | Flexibles installed and supported correctly
section | Fit Off QA
checkpoint | Correct Equipment / Correct Grills / Diffuser Installed
checkpoint | Restrained correctly
checkpoint | Flexible connection fixed correctly to grill box
checklist | Fire Dampers | [5 empty] | CRL-ITR-002 - Fire Dampers
section | First Fix QA
checkpoint | Penetration formed correctly
checkpoint | Correct FD Installed & correct orientation
section | Second Fix QA
checkpoint | Access Panel installed
checkpoint | Drop Tested
checkpoint | Track is Clear
checkpoint | All angles correctly fixed
checkpoint | Label to be installed
checklist-flat | Mechanical Board (MSSB) | [5 empty] | CRL-ITR-003 - Mechanical Board (MSSB)
checkpoint | Correct Equipment / plant installed
checkpoint | Switch Board Mounted in correct position and level
checkpoint | Switch Board terminations complete
checkpoint | Board Tested
checkpoint | COC's Complete
checkpoint | Label to be installed
checklist | Fans | [5 empty] | CRL-ITR-004 - Fans
section | Fans
checkpoint | Correct Equipment / plant installed
checkpoint | Correct mountings / springs installed
checkpoint | U/S of Fan heights correct as per Workshop Drawings.
checkpoint | Seismic Bracing Installed
textbox | Drawing Reference Number
checkpoint | Label to be installed
section | E4M QA
checkpoint | Electrical Isolators installed in correct location
checkpoint | Units Terminated
checkpoint | Units Tested and Running
checklist | Fan Coil Units | [5 empty] | CRL-ITR-005 - Fan Coil Units
section | Unit First Fix QA
checkpoint | Correct Unit Installed
checkpoint | u/s of Unit at correct height
checkpoint | Correct mountings / Springs Installed
section | Unit Second Fix QA
checkpoint | Unit Plenum Boxes to be installed
checkpoint | Filters installed & clearence checked
checkpoint | Seismic Bracing Installed
textbox | Drawing Reference Number
checkpoint | P - trap installed if required
checkpoint | Driptray installed if required
checkpoint | Condensate Drains installed
checkpoint | Correct Fall to tundish , and water flow tested
checkpoint | Label to be installed
section | E4M QA
checkpoint | Electrical Isolators installed in correct location
checkpoint | Units Terminated
checkpoint | Units Tested and Running
checklist-flat | Chilled Water Pipe Systems | [5 empty] | CRL-ITR-006 - Chilled Water Pipe Systems
checkpoint | Pipework installed as per Drawing
textbox | Installation done by
checkpoint | Valve arrangement installed as per schematic
checkpoint | Insulation blocks installed where required
checkpoint | Correct hanger spacing
checkpoint | Drains installed at low points
textbox | Air vents installed at all high points
checkpoint | The pipe OD and groove dimensions are within tolerance range as per victaulic specification
checkpoint | The correct coupling has been used for the correct joint i.e flexible or rigid
checkpoint | Visual indicators verified - Positive overlap - Joint Square
checkpoint | Steel is primed and weld painted after works are completed (PA10)
checkpoint | Pipework Seismic to be installed
textbox | Drawing Reference Number
checklist-flat | Hydro Pressure Test | [5 empty] | CRL-ITR-007 - Hydro Pressure Test
checkpoint | Details of pressure test
textbox | System Name/No.
textbox | Location / Drawing No.
textbox | Test Instrument & Serial Number.
textbox | Normal Working Pressure
textbox | Start test ambient temperature
textbox | Start test date
textbox | Start test time
textbox | Start test pressure
textbox | Finish test ambient temperature
textbox | Finish test date
textbox | Finish test time
textbox | Finish test pressure
textbox | Corrected pressure at test completion
note | Attach photos of the gauges as required
note | FORMULA:
note | Pc = P x (Ts + 273) / (T + 273) kpa
note | Pc = P x (+273 ) / (+ 273) kPa
note | Pc = kPa
note | WHERE:-
note | P = PRESSURE REQUIRING CORRECTION i.e. PRESSURE ACTUALLY READ AT TEST END
note | Pc = CORRECTED PRESSURE
note | Ts = AMBIENT TEMPERATURE oC AT START OF TEST
note | T = AMBIENT TEMPERATURE oC AT SAME TIME OF READING P.
checklist | AHU Installation | [5 empty] | CRL-ITR-008 - AHU Installation
section | AHU's
checkpoint | Check plinth size and location
checkpoint | Correct Unit Installed
checkpoint | Condensate Piping installed
checkpoint | Unit correctly anchored
textbox | Drawing Reference Number
section | Unit Second Fix QA
checkpoint | Filters Installed
checkpoint | Label to be installed
section | E4M QA
checkpoint | Electrical Isolators installed in correct location
checkpoint | Units Terminated
checkpoint | Units Tested and Running
checklist-flat | Chillers Installation | [5 empty] | CRL-ITR-009 - Chillers Installation
checkpoint | Check if plinth site is correct
checkpoint | Correct Unit Installed
checkpoint | Setting out point correct
checkpoint | Corrrect Mounting Springs installed
textbox | Drawing Reference Number
checkpoint | Label to be installed
checklist | Crack Unit Installation | [5 empty] | CRL-ITR-010 - Crack Unit Installation
section | Crack Unit
checkpoint | Correct Unit Model
checkpoint | Check for Damage
checkpoint | Verify Floor is Level
checkpoint | Confirm Fixings as per detail (Seismic)
textbox | Drawing Reference Number
section | Crack Second Fix QA
checkpoint | Potable Water connected (by others)
checkpoint | Filters Installed – Check Clearances
checkpoint | Door Clearance checked
checkpoint | Drains Installed – Run to Tundish by Others
checkpoint | Shipping mounts removed
checkpoint | Label to be installed
checklist-flat | Pump Installation | [5 empty] | CRL-ITR-011 - Pump Installation
checkpoint | Check if plinth site is correct
checkpoint | Correct Unit Installed
checkpoint | Setting out point correct
checkpoint | Corrrect Mounting Springs installed
textbox | Drawing Reference Number
checkpoint | Label to be installed
checklist | Braze Bench Test | [5 empty] | CRL-ITR-012 - Braze Bench Test
section | Test Sheet
checkpoint | Test Sheet Completed
textbox | BUILDING:
textbox | AREA / SYSTEM:
textbox | DRAWING No.
textbox | NAME OF WORKER:
textbox | ASSIGNED BRAZE ID.
textbox | JOINT TYPE INSPECTED:
textbox | INSPECTING SUPERVISOR
checkpoint | Tube is cut by suitable means, ends are deburred & cleaned of any filings, and surfaces prepared with light grade emery paper.
checkpoint | Joint fit has correct clearance and expanded end of tube (if applicable) is to correct length for pipe size - as per NDY specified requirements
checkpoint | Heat from Oxy Acetylene torch is being applied uniformly to the fitting, and torch flame is slightly reducing/carburising.
checkpoint | Silfos used is 15% and is being applied so that through capillary action is achieved around the entire joint.
checkpoint | Shoulder build-up of Sipfos is just present around the entire circumference of the brazed joint, and completed joint is left to air cool.
checkpoint | Sign Off Complete
checkpoint | Signed off By AE Smith
checkpoint | Signed off By Witness
textbox | Witness Name
checkpoint | Signed off by Consultant
textbox | Consultant Name
section | Med Lab Results
checkpoint | Document of Results
checklist | Radiant Heaters | [5 empty] | CRL-ITR-013 - Radiant Heaters
section | Radiant Heaters
checkpoint | Correct Equipment / plant installed
checkpoint | U/S of Equipemnt heights correct as per Workshop Drawings.
section | E4M QA
checkpoint | Electrical Isolators installed in correct location
checkpoint | Units Terminated
checkpoint | Units Tested and Running
checklist-flat | Duct / Equipment Cleaning | [5 empty] | CRL-ITR-014 - Duct / Equipment Cleaning
checkpoint | Duct cleaned in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
checklist-flat | Cowls | [5 empty] | CRL-ITR-015 - Cowls
checkpoint | Outside Air Roof Cowl Installed
checkpoint | Builder - Waterproof and Seal to be installed
checklist | DX Units | [5 empty] | CRL-ITR-016 - DX Units
section | DX Units
checkpoint | Correct Unit Installed
checkpoint | Out door Unit Installed
checkpoint | u/s of Unit at correct height
checkpoint | Refrigeration Pipework installed as per drawings
textbox | Installation done by
checkpoint | Pipework Installed from DX unit box to Outdoor unit
label | Schematic markups drawings
checkpoint | Condensate Piping installed
checkpoint | Pressure Tested
checkpoint | Signed off By AE Smith
textbox | Name of person
textbox | Date
checkpoint | Photo's of Pressure test
textbox | Start of Pressure test
textbox | Time / Date
textbox | Pressure test after recored Duration
textbox | Time / Date
checkpoint | Triple Evacuation procedure to be done.Final below 500 Microns
checkpoint | Refrigeration (Scale) charge unit completed - According to Calculation for Pipe Size & Length
checkpoint | Insulation Complete for Piping and Condensate lines
checkpoint | Seismic Bracing Installed
textbox | Drawing Reference Number
section | Unit Second Fix QA
checkpoint | Filters Installed
section | E4M QA
checkpoint | Electrical Isolators installed in correct location
checkpoint | Units Terminated
checkpoint | Units Tested and Running
checklist-flat | CHW Insulation | [5 empty] | CRL-ITR-017 - CHW Insulation
checkpoint | Insulation is installed as per the manufacturers recommendations, as well as per any additional requirements set out in the project specification
checkpoint | Pipe sections firmly abutted to Insulation Blocks within the pipe supports, and Blocks have been glued
checkpoint | Insulation is glued and taped correctly
checkpoint | Confirm insulation is free of damages
checklist-flat | Condensate Insulation | [5 empty] | CRL-ITR-018 - Condensate Insulation
checkpoint | Approved materials have been used (e.g. Elastomeric closed cell insulation), min 9m thick
checkpoint | Condensate pipework insulated correctly
checkpoint | Confirm insulation is free of damages
checklist-flat | External Duct Work Insulation | [5 empty] | CRL-ITR-019 - External Duct Work Insulation
checkpoint | Insulate ducting as per drawing and specifications
checkpoint | Provide 50mm over lapping at all joints.
checkpoint | Confirm pins are installed and spacing is correct
checkpoint | Confirm bands at 600mm centres.
checkpoint | Confirm all overlaps and joints are complete
checkpoint | Confirm insulation is free of damages
checklist-flat | Fire Rated Duct Insulation | [5 empty] | CRL-ITR-020 - Fire Rated Duct Insulation
checkpoint | Insulate ducting as per drawing and specifications
checkpoint | Ensure all wraps are complete and no gaps ensure
checkpoint | Confirm all joints installed correctly with suitable overlaps
checkpoint | Pins and banding correctly applied
checkpoint | Maxilite board to wall complete and sealed.
checkpoint | Confirm second layer length has been installed as per specification from wall.
checkpoint | Access Panels installed correctly. Confirm fixings, sealant and alignment with internal panel.
checkpoint | Confirm insulation is free of damages
checklist-flat | Metal Cladding | [5 empty] | CRL-ITR-021 - Metal Cladding
checkpoint | Clad pipework as per drawing
checkpoint | Approved materials have been used
checkpoint | Pipework cladding installation complete and tidy. Check straps, sealant and removable sections
checkpoint | Penetraitons are sealed for gauges, instruments, and drain vents (silicone)
checkpoint | Confirm cladding is free of damages