## res_ITC 12 - R11 and R16 Stormw
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-flat | AXXX - West Dapto - ITC 007 (ITP007) - Utilities (Excl. Water, Streetlights and Traffic Signals) | [5 empty] | AXXX - West Dapto - ITC 007 (ITP007) - Utilities (Excl. Water, Streetlights and Traffic Signals)
checkpoint | 1 - Preparation Works
label | REQUIREMENTS / REFERENCE: Project Safety Plan, Project Environment Plan
label | ACCEPTANCE CRITERIA:
label | • All site personnel inducted, required SWMS completed and signed, Safety Plan approved
label | • ERSED controls installed on site, air quality visually monitored for dust etc due to construction activities, Environment Plan approved
label | • Contact DBYD and complete excavation permit, extent of works set out with survey pegs
text | INSPECTION:
checkpoint | 2 - Design Documentation
label | REQUIREMENTS / REFERENCE: WCC 1391 Cl 2
label | ACCEPTANCE CRITERIA:
label | • HOLD POINT:
label | • Prepare documentation based on the concept drawings, including conduit alignment and chainages, obstructions, number and types of conduits, any pits and lid details
label | • Prepare a design report including choice of cable route, reasoning behind pit locations, site specific environmental requirements, reasoning for any variations to the concept design
text | INSPECTION:
text | HOLD POINT NUMBER:
holdpoint | HOLD POINT
checkpoint | 3 - Authority Approval of Design
label | REQUIREMENTS / REFERENCE: WCC 1391 Cl 2.2
label | ACCEPTANCE CRITERIA:
label | • HOLD POINT:
label | • Provide evidence of the service distributor’s design approval
text | INSPECTION:
text | HOLD POINT NUMBER:
holdpoint | HOLD POINT
checkpoint | 4 - Utility Construction Materials
label | REQUIREMENTS / REFERENCE: WCC 1391 Cl 3
label | ACCEPTANCE CRITERIA:
label | • HOLD POINT:
label | • All materials are as per WCC requirements and project drawings, and have been approved for use in the works
text | INSPECTION:
text | HOLD POINT NUMBER:
holdpoint | HOLD POINT
checkpoint | 5 - Set Out of Works
label | REQUIREMENTS / REFERENCE: WCC 1391 Cl 4.1
label | ACCEPTANCE CRITERIA:
label | • HOLD POINT:
label | • Set out the location, lengths and levels of the cable network and pits, as documented at least 1 day prior to commencing excavation
text | INSPECTION:
text | HOLD POINT NUMBER:
holdpoint | HOLD POINT
checkpoint | 6 - Installation of Utility Assets
label | REQUIREMENTS / REFERENCE: WCC Cl 4.2, 4.3
label | ACCEPTANCE CRITERIA:
label | • Lay conduits in straight lines parallel or normal to the carriageway, avoid unnecessary bends. Install and provide required cover as per drawings
label | • Set pits flush with finished level of the surrounding area, shape surrounding area
label | • Provide bedding and connect conduits into pit as per drawings
label | • Locate pits as per design documentation and WCC 1391 Cl 4.3
text | INSPECTION:
checkpoint | 7 - Backfill Materials and Backfill
label | REQUIREMENTS / REFERENCE:
label | • WCC 0223
label | • WCC 1391 Cl 4.4
label | ACCEPTANCE CRITERIA:
label | • Use fill materials suitable for project earthworks
label | • Do not commence backfill until conduit system as been inspected, record survey data prior to backfill
label | • Compact backfill material as per drawings and conduct density and moisture testing
label | • Re-use existing surface materials where possible
text | INSPECTION:
label | COMMENTS / ATTACHMENTS: Compaction Test Report
checkpoint | 8 - Testing of Installed Conduits
label | REQUIREMENTS / REFERENCE: WCC 1391 Cl 4.5
label | ACCEPTANCE CRITERIA:
label | • WITNESS POINT:
label | • Use a test mandrel through each conduit, test completed conduits for ovality at least 14 days after compaction of completed backfill. Provide results to the Client. Immediate replace any damaged sections of conduit
text | INSPECTION:
text | WITNESS POINT NUMBER:
holdpoint | WITNESS POINT
checkpoint | 9 - Marking of Kerbs
label | REQUIREMENTS / REFERENCE: WCC 1391
label | ACCEPTANCE CRITERIA:
label | • WITNESS POINT:
label | • Mark the face of kerbs, showing the route of conduits (if required)
text | INSPECTION:
text | WITNESS POINT NUMBER:
holdpoint | WITNESS POINT
checkpoint | 10 - Final Inspection (Completion)
label | REQUIREMENTS / REFERENCE: WCC 1391
label | ACCEPTANCE CRITERIA:
label | • HOLD POINT:
label | • Complete a final inspection with the Client, confirming:
label | • Correct number of conduits installed
label | • Draw wire in each conduit
label | • Pits are free of debris and ingress of water
label | • Pit lids fit securely
label | • Labels on pit lids
text | INSPECTION:
text | HOLD POINT NUMBER:
holdpoint | HOLD POINT
checkpoint | 11 - WAE Drawings
label | REQUIREMENTS / REFERENCE: WCC 1391
label | ACCEPTANCE CRITERIA:
label | • Provide Works As Executed (WAE) Drawings, showing locations of all conduits and pits for each installed utility service
text | INSPECTION:
checkpoint | QA ENGINEER / SPE / PE SIGN OFF
text | Name:
text | Date:
label | Signature